- l

| SL NO. | BIDDER’S QUERRY | BHEL’S REPLY |
| --- | --- | --- |
| 1. | - No cable tunnel or cable spreader room details / drawings are available in the tender document We. are unable to calculate the Digital LHS cable quantity. Please provide us the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
| 2. | - No details of Transformer Caveran are available in the tender document. We request you to kindly provide us the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
| 3. | GIS floor / GIB floor drawings or details are not available in the tender document. Please provide us the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
| 4. | - PENSTOCK Butterfly Valve area details / drawings are not available in the tender document. Please provide us the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
| 5. | In your technical specification it has been mentioned that the Main Fire Alarm Panel must be redundant type. As per approved make list no manufacturer manufactures redundant Fire Alarm Panel. Please confirm the requirement. | Bidder to follow NIT requirements. |
| 6. | Please confirm whether the Main Fire Alarm Panel will be connected to client’s network through MODBUS gateway or potential free contact. | Main Fire Alarm Panel should have provision for both MODBUS connectivity and minimum five number of potential free contact for interfacing with DCS. |
| 7. | - Please confirm whether all the office room battery room etc. shall be covered by Aspiration type Detectors or normal spot type detectors. | The subject areas will be protected through both aspiration type detectors and smoke detectors. |
| 8. | Please confirm the required number of tripping. | Only one (01) no of potential free contact is required for tripping purpose. |
| 9. | - Please confirm the no. of potential free contact for interfacing purpose. | Minimum 10 nos. potential free contacts are required. Exact requirement shall be decided during detail engineering. |
| 10. | As per the scope matrix Sl no. 10 please confirm whether machine hall floor is required to be covered by FDA or not, please confirm. | Yes, FDA system is required for all the areas as per NIT including the machine hall floor |
| 11. | - As per the scope matrix Sl no. 11 please confirm whether GIS hall floor is required to be covered by FDA or not, please confirm. | Yes, FDA system is required for all the areas as per NIT including the GIS hall floor |
| 12. | Please confirm the Siren capacity (diametric range) | Siren shall be suitable for minimum of 3 km diametric range. |
| 13. | Please confirm whether only Hooter or Hooter cum Strobe is required. | Hooters shall be provided. |
| 14. | Please provide us the full details of the required Control & power cable. | Bidders are requested to follow the NIT for Minimum specification of any equipment. All equipment shall be designed considering the NIT requirements, good engineering practices and National / International code, subject to approval of BHEL during order execution stage. |
| 15. | Plot Plan Drawing in Auto Cad if available is required for locating the concerned areas and actual length and dimensions. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
| 16. | - Schematic arrangement drawing NH/DEM/MGD/FF/01 is not available in the tender document. Please provide us the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
| 17. | Single line diagram of cooling water drawing NH/DEM/MGD/CW/01 is not available in the tender document. Please provide us the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
| 18. | - Overall plan layout drawing of Transformer Caveran and OGA and rating of Transformer is required. Please provide us the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
| 19. | MIV oil pumping unit drawing, Governor Oil Pump unit drawing are not available. Please provide the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
| 20. | - Detail Cable Trays arrangement of Turbine Floor, Generator Floor, Machine Floor is not available in the tender. Please provide the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
| 21. | In the tender document ventilation tunnel, cable tunnel, detail cable tray arrangement and elevation are not mentioned. Please confirm the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
| 22. | - Cable tunnel details between transformer hall and Pothead Yard area is not available. Please provide us the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
| 23. | Location and OGA drawing of 2 nos. Auxilary Transformer (33KV/11KV), Location of DG Room, location Panel Room of Pothead Yard area are not available with the tender document. Please provide the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
| 24. | - Please confirm the location and OGA drawing of 3 nos. ICT transformers. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.. |
| 25. | Clause of No: 26.5.5 Fire Fighting system all embedded and exposed water pipes size of 25 NB and above shall be made of Carbon Steel of minimum Schedule 40 and Clause No: 5.7.3 piping and fittings (page no 5-6) piping shall be of heavy duty class carbon steel confirming to ASTM A53/ ASTM A106 or equivalent IS as per employers approval confirming to the requirement. Please confirm the piping specification. | MOC list of various items is attached herewith the pre bid replies. All equipment shall be designed considering the NIT requirements, good engineering practices and National / International code, subject to approval of BHEL during order execution stage. |
| 26. | - Please confirm the Tank Location. | Typical drawings are attached along with the pre bid clarification. Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
| 27. | In the Clause no: 26.5.8.2 (water sprinkler and spray system) Each Deluge system shall consists of an electrically monitored isolation valve again clause no: 10.7.3 page no: 31 of 38 states that the deluge valve system shall consists of Wet trim deluge valve, manual isolation gate valve at inlet and outlet of the Deluge Valve. Please confirm the type of isolation valve which is required in the spray system. | The deluge valve system shall consist of Wet Trim Deluge valve , Manual Isolation gate valve at Inlet and outlet of the deluge valve , Y type strainer at the Inlet of the Deluge valve , Deluge valve local Control Panel ( DVLCP). No bypass line has been envisaged for Deluge valve |
| 28. | - Please confirm the type of all 25 NB and above carbon steel pipe confirming to ASTM A 106 Gr. B or ASTM A 106 Gr. B Galvanized. | MOC list of some of the items is attached herewith the pre bid replies. All equipment shall be designed considering the NIT requirements, good engineering practices and National / International code, subject to approval of BHEL during order execution stage. |
| 29. | Please provide us the welding specification of all fire water pipe (25 NB and above). | Bidder to submit the Welding specification for purchaser’s review during order execution stage. The welding shall be carried out as per this approved welding procedure, without any additional commercial implications to purchaser. |