| Sl | Discussion Point | Resolution |
| --- | --- | --- |
|  | Plot Plan of the Plant. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
|  | Indicative P&ID of the system (Drawing no. NH/DEM/MGD/FF/01 Detailed scheme of interconnection of sumps, dry pits etc.-- clause 21.2 "Specific parameters and Layout conditions" of section 21 "Cooling Water System", Single line diagram of CW system Drg no. NH/DEM/MGD/CW/01 | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
|  | Indicative layout drawings of Aux Buildings and Transformer Yard Area. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
|  | Please note that there is no TAC approval as such. Local fire authorities are taken in India. In Oil & Gas sector, the client has their own OISD approvals. Please suggest in such case who will be approving authority and who will be approving our engineering and installation for FPS system? | TAC approval shall be included in bidder’s scope. |
|  | Please provide drawing showing BHEL, MCC. | MCC for the FDPS is included in bidder’s scope. The location of the same shall be finalized during order execution stage. |
|  | Location of cooling water header with tap off point for Fire water pumps? | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
|  | As per clause 10.0 of Technical specifications, the system has been designed by BHEL as per NFPA/TAC guidelines whereas as per scope of NIT Design is also part of scope. Please clarify. If the design is already done by BHEL, Please provide us the details for residual engineering. | Design of complete FDPS is included in bidder’s scope as per cl no 1.0 of BHEL’s specification |
|  | Pipes for Hydrant system, HVWS/MVWS are generally in IS 1239/3589 ERW medium or heavy grade depending upon design pressure/working pressure. As per clause 5.7.3 of GTS for Pipe, fitting, Valves and Heat exchanger, it seems BHEL wants to use A 106/A53 Seamless pipes. Please clarify. | BHEL’s specification requirements shall be followed. |
|  | Specifications of “Control & Monitoring system/ Scada” has been enclosed as Volume ii ( c) part 3 & 4, sr. no. 11 of the chapter of tender. Please clarify whether these specs. are related to our scope. | Control & Monitoring of FDPS is included in bidder’s scope. |
|  | The piping work for hydrants/HVWS/MVWS headers need to be taken on pipe rack/supports provided by BHEL or we have to provide separate supports/racks etc. | Routing of the Piping shall be finalized during order execution stage. |
|  | We envisage that no civil work is in our scope except for hole making in walls etc. and grouting. | Only Petty civil works like making opening in the walls & making it good after erection is included in bidder’s scope |
|  | Cross-sectional drawing of cable tray with length. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
|  | Spec – Part No. As per your consideration of MSD & ASD for control room office, electrical utility area, but it is not clear to us to provide which detection at below false ceiling / above false ceiling. | Specification requirements to be followed |
|  | Location of Booster Pump House | Booster Pump House shall be located at EL 1083.0 M near the 400 KV Pothead Yard |