## Pre-Bid Queries
BHEL replies #6 to Pre bid queries
Sl No. | Clause No:- | Description as per specification |  | Resolution Point
Technical
1 | Technical Specification | MIV Floor Drawings are required -
1a. | Technical Specification | For Cable Tray detail at MIV Floor – no of cable rack, no of tray, size of tray required for finalise the quantity Digital LHS Cable and no of sprinkler requirement. | Please provide us the detail drawing/dimension for the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
1b. | Technical Specification | MIV Oil Pumping Units size required for calculating sprinkler quantity | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
1c. | Technical Specification | Governor Oil Pumping size required for calculating sprinkler quantity | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
2 | Technical Specification | Power House at El. 1017.00 M (Turbine Floor, A‐D bay)
2a. | Technical Specification | Cable Trays detail required for finalise the quantity Digital LHS Cable and no of sprinkler requirement | Please provide us the detail drawing/dimension for the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
3. | Technical Specification | Power House at El. 1021.50 M (Generator Floor)
3a. | Technical Specification | Cable Trays drawing required for finalise the MSD and Digital LHS Cable qty. | Please provide us the detail drawing/dimension for the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
3b. | Technical Specification | Generators qty. & sizes are also required. | Please provide. | Bidder to referBHEL specification for details.
4. | Technical Specification | Power House at El. 1028.40 M (Machine Floor)
4a. | Technical Specification | Cable Trays - no of cable rack, no of tray, size of tray required for finalise the quantity Digital LHS Cable and no of sprinkler requirement. | Please provide us the detail drawing/dimension for the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
5. | Technical Specification | Power House Aux Block at El. 1017.00 M (Mechanical Services Floor)
5a. | Technical Specification | Mechanical Workshop size required for finalise of MSD | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
5b. | Technical Specification | Stores Size required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
5c. | Technical Specification | Air compressor, lubricating oil tank & other equipment Size required. | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
6. | Technical Specification | Power House Aux Block at El. 1021.500 M (Electrical utility floor). SATs, Station Auxiliary Board & Other equipment/ area.
6a. | Technical Specification | SATs, Station Auxiliary Board & Other equipment/ area. | Please provide us the detail drawing/dimension for the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
7 | Technical Specification | Power House Aux Block at El. 1026.00 M (Electrical Service floor)
7a. | Technical Specification | Electrical W/S & Lab Size required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
7b. | Technical Specification | Switchgear Area Size required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
8. | Technical Specification | Power House Aux Block at El. 1030.50 M
8a. | Technical Specification | Control room, Server Room, Resource Centre Room etc. Size required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
9 | Technical Specification | GIS CUM TRANSFORMER CAVERN GIS Drawing required
9a. | Technical Specification | GIS Drawing required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
9b. | Technical Specification | 12 nos. GSU Transformers - Drawings required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
9c. | Technical Specification | 1 no. Bus Reactor - Drawing required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
10. | Technical Specification | GIB Area (El. 1036.40 M)
10a. | Technical Specification | Cable Trays - no of cable rack, no of tray, size of tray required for finalise the quantity Digital LHS Cable and no of sprinkler requirement. | Please provide us the detail drawing/dimension for the same. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
11 | Technical Specification | GIS Area ( El. 1040.50 M) ) - drawing required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
12 | Technical Specification | BUS DUCT GALLERY - drawing required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
13 | Technical Specification | CONNECTING CABLE TUNNEL - no of cable rack, no of tray, size of tray required for finalise the quantity Digital LHS Cable and no of sprinkler requirement. | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
14 | Technical Specification | Ventilation Tunnel - drawing required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
15 | Technical Specification | MAIN ACCESS TUNNEL - drawing required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
16 | Technical Specification | Cable Tunnel (Between transformer hall to pothead) - drawing required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
17 | Technical Specification | POTHEAD YARD AREA – - drawing required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
17a. | Technical Specification | 3 Numbers of ICT (Transformer). - drawing required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
17b. | Technical Specification | 2 Numbers of Aux Transformer (33 KV/11 KV) – - drawing required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
17c. | Technical Specification | DG Room Area - - drawing required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
17d. | Technical Specification | Panel Room - drawing required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
17e. | Technical Specification | Bulk Oil Storage Tank - drawing required | Please provide.
17f. | Technical Specification | Penstock Buttery Valve - drawing required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
17g. | Technical Specification | 132 KV Pothead Yard - drawing required | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
17h. | Technical Specification | Booster Pump House - drawing required | Please provide. | Layout of Booster Pump House is included in Bidder's scope.
18. | Technical Specification | FIRE RATED PENETRATION SEALS, FIRE BARRIERS, FIRE DAMPERS - drawing & detail scope of work is required. | Please provide. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
6.2 Note 4 | Document No PY 51263 Rev 00 | Since Valve House is located at a distance from the Main Power House, it is not feasible to connect the Plant Fire Alarm System to the Fire detectors in the Valve House. Accordingly a standalone Fire Alarm Panel shall be provided in the Valve House. The MSD & MCPs in valve house shall be connected to this dedicated Fire Alarm Panel. 220 V Power supply for this Panel shall be provided by others. Three signals (valve house under fire, valve house Panel Healthy & valve house Panel under fault) shall be repeated in the SCADA through Potential free contact. For this the Potential free contacts shall be connected to SCADA system in the valve house and further cabling from valve house to SCADA Panel in the Main Power House Building shall not be in Bidder’s scope. | Please confirm | Confirmed.
6.2.1 | Document No PY 51263 Rev 00 | Fire sealing/barrier material (Mortar Seal Type) of Two hours rating shall be provided for all entry and exit openings (of wall/ floor) for cables. |  | Confirmed.
|  | Fire Dampers of HVAC ducts is beyond the purview of this document. However facility for tripping of all fire dampers in the event of fire shall be provided. | We will provide only potetial free contact near to the fire alarm panel. Cabling From contact to respective panel will no be in our scope. Also the no of potential free contact will be decided during detail engineering | Confirmed.
7.2 t. | Document No PY 51263 Rev 00 | Insulation with cladding and painting | Please provide the detail specification | Not included in Bidder's scope. Point deleted.
7.2 u. | Document No PY 51263 Rev 00 | Hooking up of all services with battery limit Interfaces. | Scope not clear | Not included in Bidder's scope. Point deleted.
10.6 | Document No PY 51263 Rev 00 | Fluid Velocity in the main header shall normally not exceed 3.0 m/s. However in localised section/branch pipes velocity shall be limited to 5m/s as permitted per FP manual (TAC) | As per Cl. No. 26.1.3.2 of Volume IIIB (PTS):-Package-1 by NHPC the fire header and piping shall be looped and of sufficient size to supply the flow requirements at any point in the loop considering the most direct path to be out of service. Fluid velocity in the main header shall normally not exceed 3.0 m/s. Pipe sizes shall also be designed to accommodate any future expansion/ water demands. Please confirm | Fluid Velocity in the main header shall normally not exceed 3.0 m/s. However in localised section/branch pipes velocity shall be limited to 5m/s as permitted per FP manual (TAC)
10.7.2 | Document No PY 51263 Rev 00 | The Following Equipment shall be provided with HVWS system as per cl no 26.1.1 of Contract Specification:
|  | 1. 12 Number of GSU transformers located at El 1028.40 ( Transformer Hall ) of the GIS cum transformer cavern building 2. 1 nos. Bus Reactor located at El 1028.40 (Transformer Hall ) of the GIS cum transformer cavern building 3. Four (4) No’s of Governor Oil Pumping Units located at EL 1017.00 located in Power House Building. 4. 4 nos. of Main Inlet Valve (MIV) Oil Pumping Unit located at EL 1017.00 in Power House Building. 5. 3 nos. for ICT (including spare) Location at EL 1078.00 at ICT cum GIS Building at Potyard Head 6. 2 nos. for Auxiliary Power Transformer (33 kV / 11 kV) placed in DG area | As per Cl. No. 26.1.1 of Volume IIIB (PTS):-Package-1 by NHPC ii) Thirteen (13) nos. deluge system for fire protection of each GSU transformer (including spare GSU transformer), iii) Three (3) nos. deluge system for fire protection of each Bus Reactor iv) Four (4) nos. of deluge system for fire protection of governor oil pumping units, v) Four (4) nos. of deluge system for fire protection of main inlet valve oil pumping units, vi) Deluge system for fire protection of XLPE cables including power & control cables / trays in the cable tunnels and cable gallery, as per approved drawings, vii) Four (4) nos. deluge system for fire protection of each ICT (including spare), viii) Two (2) nos. deluge system for fire protection of each Auxiliary Power Transformer (33 kV / 11 kV) placed in DG area, Hence as per NHPC specification 30 nos area to be protected by hvws system where as in BHEL spec 27 nos to be protected by hvws system - Please Confirm | 1. 12 Number of GSU transformers located at El 1028.40(Transformer Hall) of the GIS cum transformer cavern building. 2. 1 nos. Bus Reactor located at El 1028.40(Transformer Hall) of the GIS cum transformer cavern building . 3. Four (4) No's of Governor Oil Pumping Units located at El 1017.00 located in Power House Building. 4. 4 nos. of Main Inlet Valve(MIV) Oil Pumping Unit located at El 1017.00 in Power House Building. 5. 3 nos. of ICT(including spare) location at El 1078.00 at ICT cum GIS Building at Potyard Head. 6. 2 nos. of Auxiliary Power Transformer(33 kv/ 11kv) placed in DG area.
GENERAL
|  | The schematic arrangement has been detailed in drawing no. NH/DEM/MGD/FF/01. | Please provide the drawing | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
|  | Single line diagram of cooling water system has been shown in drawing no. NH/DEM/MGD/CW/01 | Please provide the drawing | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that , they shall not be eligible for any additional commercial implications on account of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage.
|  | Make List | Please provide the specific make list pertains to customer approved vendor list for fire protection system | Bidder to follow the details in NIT.