| Sl | Discussion Point | Resolution |
| --- | --- | --- |
|  | We will provide the Fire Protection System as per BHEL Specification. NHPC specification has been considered for information purpose only. | Bidder proposal is not acceptable. Complete specification requirement shall be followed. |
|  | Since the project is located in Bhutan, we request you to exclude erection, testing and commissioning from bidder's scope. Design, engineering and supply will be in bidders' scope. Manpower for supervision of site erection will be provided by bidder. This is in line with BHEL's standard practice for Fire Protection System package. | Bidder proposal is not acceptable Bidder to follow specification requirements. |
|  | We request BHEL to provide the drawings. Following drawings are not attached with the tender specification; a. Overall Plot Plan b. GAD of transformers and reactors to be provided with HVW Spray System. c. Cable tray arrangement in cable tunnel and GIB cellar flooor to be provided with MVW Spray System. d. Composite P&ID / Schematic drawing for filling arrangement, hydrant system, HVW Spray System and MVW spray system. e. Schematinc Drawing for Fire Detection and Alarm System. f. Typical DV assembly drawing for HVW Sytem. g. Typical DV assembly drawing for MVW Sytem. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders, Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage. |
|  | We request BHEL to provide the quantities for fire extinguishers for bidding purpose. Final quantities will be supplied as per the design and engineering after award of contract. | Bidder to estimate the quantities as per specification and applicable standards. |
|  | We request BHEL to provide the size and nos of entry and exit openings for cables. Without these details, requirement of fire sealing/ barrier material cannot be ascertained. | Typical drawings have been furnished along with NIT and /or BHEL’s replies to Pre-bid queries raised by bidders for estimation of size and nos of entry and exit openings for cables . Final drawings shall be furnished during order execution stage. Bidder to note that they shall not be eligible for any additional commercial implications because of furnishing of new input drawing and /or revised drawings etc by BHEL during order execution stage |
|  | We request BHEL/ NHPC to accept following additional vendors; Fire Fighting System integrator- Thermosystems. Pumps - Flowmore. Fire Alarm Panel- Schrack. Heat / smoke Detectors- Schrack. Optical/ Beam Detector- Schrack | Bidders who are meeting qualification criteria are eligible for bidding. Bidders to abide by the vendor list provided in the specification. Any additional vendors if required shall be approved after award of order as per standard procedures. |
|  | We request BHEL to provide Technical Data Sheets for various items not attached with the tender specification. | Please refer Sl. No. 9 below |
|  | Petty civil works like making opening in the walls & making it good after erection is included in bidder’s scope |  |
|  | Material of Construction (MOC) Of Major Equipment Shall Be as Per Table-1 Below |  |
|  | PQC Requirement: In addition to the PQC requirement furnished in the NIT, the following shall be met by bidder: Bidder shall be a ISO Certified company |  |
|  | All Input drawings shall be governed by per clause no 18.6 of BHEL’s specification. |  |
|  | Bidders is advised to quote strictly as per BHEL’s specification requirements. In case bidder excludes some components of scope of supply or some features of specification requirements, the bidder will be required to include the same in the scope during offer evaluation stage /contract execution stage without any additional commercial and price implications on account of the same. Bidder to note that they won’t be entitled for any price impact on account of withdrawal of deviation taken from BHEL spec during technical scrutiny stage. |  |

TABLE-1

The major items of FPS system and their MOC is listed in the table below: -

| SL. NO. | ITEM | MOC |
| --- | --- | --- |
|  | Tank filling Pumps (Electric Motor Driven) | - Impeller : High grade duplex stainless steel ( AISI 329 or better) - Casing : Cast steel ( ASTM A 216 WCB or better) - Shaft, sleeve and key: stainless steel( AISI 410 or better) |
|  | Fire Water Pipes | A106 Gr-B |
|  | Fire Water Pipes (Over ground pipes normally empty but periodically charge with water & foam system applications) | A106 Gr-B Galvanized to IS:1239, Part- 1, Galvanized as per IS: 4736 |
|  | Valve |  |
| 4A | Valves DN 50 NB and below | Body : SS (ASTM A276 Type 316 / A182 Gr F 316) Spindle shaft & Pin : SS (AISI 410) Disc / Ball / Wedge : SS (ASTM A 351 Gr CF8) Gland seal / Seat : PTFE Seat / Body lining : PTFE |
| 4B | Valves Above DN 50 NB | Body : ASTM A216 WCB Spindle shaft & Pin : SS (AISI 410) Disc / Ball / Wedge : SS (ASTM A 351 Gr CF8) Gland seal / Seat : PTFE Seat / Body lining : PTFE |
|  | HVWS Nozzle | S.S 304 |
|  | MVWS Nozzle | S.S 304 |
|  | Hydrant Valve | S.S 304 |
|  | Basket/Y Strainer | Body is ASTM A 106(R-04) and internal is S.S (AISI 316), 30 mesh |
|  | Branch Pipe | S.S 304 |
|  | Air Release Valve | Gun Metal as per IS 318 |
|  | Deluge Valve | Carbon steel |
|  | Flanges | Up to 150 NB: 105. Note: Mitered/Fabricated bends flanges shall be provided for sizes 200 NB and above. |
|  | Fittings | a) Up to 32 NB: 105. b) 32 NB & Above : ASTM 234(R-04) Note: - All fittings and flanges for galvanized pipes shall be galvanized as per IS 4736. - Mitered/Fabricated bends shall be provided for sizes 200 NB and above. |
|  | Hose Pipe | Reinforced Rubber Lined Fire Hose as per IS 636, Type – A |
|  | Bolts, Screws and Nuts | As per IS 1363 (Part I and II) |

| M/s Thermosystems | PE&SD |
| --- | --- |