TECHNICAL SPECIFICATION FOR 12KV, 1250A OFF LOAD ISOLATOR PANEL

- MANUFACTURERS NAME                       :

- MANUFACTURERS DESIGNATION        : OFF LOAD ISOLATOR

- TYPE OF SWITCH                                       : AIR

- TYPE OF REFERENCE                                : TKL3/12KV/1250A

- CONSTRUCTION                                         : FIXED TYPE

- NO. OF POLES                                              : THREE

- METHODE OF OPERATION                       : QUICK MAKE AND QUICK BREAK

- METHODE OF CLOSING                             : MANUALLY OPERATED

- METHODE OF OPENING                             : MANUALLY OPERATED

- OPERATING MECHANISM                         : HANDLE MOUNTED ON FRONT

- RATED VOLTAGE(NORMAL/MAX)          :  11KV/12KV

- RATED FREQUENCY                                   : 50HZ + 6%

- RATED CURRENT                                         : 1250AMPS

- RATED DUTY                                                 : CONTINUOUS

15.1 SHORT TIME WITHSTAND CURRENT    : 40KA/1SEC

15.2 PEAK WITHSTAND CURRENT                  : 100KA PEAK

16. TEPERATUE RISE ABOVE 45 C                   : 45 C

AMBIENT AT RATED CURRENT

17. CLEARENCE(MIN):

17.1 PHASE TO EARTH                                        : 130MM

17.2 PHASE TO PHASE                                         : 150MM

17.3 FIXED CONTACT TO BLADE IN OPEN     : 160MM

POSITION

18. RATED INSULATION LEVEL:

18.1 STANDARD IMPULSE WITHSTAND

VOLTAGE POSITIVE AND NEGATIVE POLARITY

A) ACROSS THE ISOLATING DISTANCE          : 85KV PEAK

B) TO EARTH & BETWEEN POLES                     : 75KV PEAK

19. ONE MINUTE POWER FREQUENCY

WITH STAND VOLTAGE

A) ACROSS THE ISOLATING DISTANCE           : 35KV RMS

B) TO EARTH & BETWEEN POLES                      : 28KV RMS

20. TORQUE REQURED TO OPERATE THE        : 18Kg-m

SWITCH

21. MAIN CONTACTS:

21.1 TYPE OF CONTACTS                                       : SNAP ACTION

22. AUX.CONTACTS: MAIN

22.1 SPARE CONTACTS (MINIMUM)

A) NORMALLY OPEN                                           : 4 NOS

B) NORMALLY CLOSED                                      : 4NOS

22.2 AUX.CONTACT RATING

A) CONTINUOUS (MAKE)                                   : 10 AMPS

B) BREAK (INDUCTIVE)                                      : 5AMPS

23. NO. OF MECHANICAL OPERATION SWITCH     : 1000 NOS

CAN WITHSTAND WITHOUT DETERIORATION

OF CONTACTS

24. TYPE OF INETRLOCK-MECHANICAL                  : BETWEEN OFF LOAD ISOLATOR AND DOOR

25. REFERENCE STANDARD                                        : IS 9921