SPECIFICATIONS FOR 11KV, 2500A DOUBLE BREAK ISOLATOR WITH EARTH SWITCH

PROJECT: 70 PUMPS, BHEL, RC PURAM, HYDERABAD.

DESCRIPTION: SUPPLY OF 11KV, 2500A, 50Hz DOUBLE BREAK OUTDOOR ISOLATOR WITH EARTH SWITCH COMPLETE WITH ALL ACCESSORIES.

TECHNICAL SPECIFICATIONS FOR 11KV, 2500A ISOLATOR WITH EARTH SWITCH.

- SCOPE:

The specification provides for the design, engineering, manufacture, inspection and testing before dispatch, supply and delivery and assembly at destination of 11KV, 2500A, 3 phase Isolator with earth switch with all accessories for outdoor use.

- STANDARDS:

The rating as well as performance and testing of the isolator shall conform to the latest revisions and amendments of the following standards.

Sl.No    STANDARD                                                      TITLE

1        IS: 9921          Specification for Alternating Current Disconnectors (Isolators)

and Earth switches for voltage above 1000V.

2        IEC: 129          Alternating Current Isolators and Earthing switches.

3        IS: 2147           Degree of protection provided by enclosure for low voltage

switchgear and control gear.

4        IS: 4691          Degree of protection provided by enclosure for rotating

electrical machinery.

5        IS: 12063       Classification of degree of protection provided by enclosures of

electrical equipment.

6        IS: 2629          Recommended practice for hot galvanizing of iron.

7        IS: 4759          Hot dip zinc coatings on structural steel and allied products.

8        IS: 2633          Method for testing uniformity of coating of zinc.

9        IS: 6735          Farmers-spring lock washers for screws with cylindrical heads.

10       IS: 2016         Plain washers.

11       IEC-71           Electrical clearances.

12       IS: 1573         Electroplated coating of zinc on iron and steel.

- SERVICE CONDITIONS:

Equipment to be supplied against this specification shall be suitable for satisfactory continuous operation under the following tropical conditions.

i) Location:                                       70PUMPS, BHEL, RC PURAM, Hyderabad.

ii) Max.ambient air temp (deg.C):                   50

iii) Min.ambient air temp (deg.C):                   7.5

iv) Average daily ambient air temp (deg.C):    35

v) Relative humidity (%):                                 74

vi) Average annual rainfall (mm):                    925

vii) Max.altitude above Mean Sea Level (mt): 1000

viii) Isoceraunic level (days/year):                    50

ix) Seismic level (Horizontal acceleration):      0.10g

Note: Moderate hot and humid tropical climate conducive to rust and fungus growth.

RATINGS:

| a | Nominal System Voltage | 11KV |
| --- | --- | --- |
| b | Rated Voltage | 12KV |
| c | Rated impulse withstand voltage | 85KV/75KV(peak) |
| d | Rated frequency | 50Hz |
| e | Rated current (for isolator only) | 2500A |
| f | Rated short time withstand current | 40KA(rms) for 3 sec |
| g | Rated peak withstand current | 63KA(rms) |
| h | Insulator - Type of Insulator - Name of Manufacturer - Rated voltage for Insulator - Min.Creepage distance - Standards applicable | Post Type BHEL/JSI/ALLIED 33KV 320mm IS: 2544, IS: 5356, IEC: 168, IEC: 273 |

- LIMITS OF TEMPERATURE RISE:

The limits of temperature rise shall be given in IS: 9921 (part-II) 1982

- TESTS:

The following tests shall be carried out as per IS: 9921/1985 on complete isolators and their operating devices.

- MARKING:

Isolators and their operating devices shall be provided with the name plates in accordance with IS: 9921/1982. The name plate shall be adequate weather and corrosion proof.

Note: The double break isolator is likely to erect on structural support of 4.7mt height. So the supplier shall give suitable down pipe for operation along with control gear etc.