## Sheet1
BHARAT HEAVY ELECTRICALS LIMITED, JHANSI
SPECIFICATION CUM COMPLIANCE CERTIFICATE OF 11KV VCB PANEL
NOTE :
1 | VENDOR must submit complete information against clause No. 5 ( Qualifying condition). The offer meeting this clause would only be processed.
2 | The " offered" Column and where applicable, the " Deviations" Column of this format shall be filled in by the Vender and submitted along with the offer.Technical details also submitted with the offer. Inadequate / incomplete, ambiguous, or unsustainable information against any of the clauses of the specification / requirements shall be treated as non - compliance.
3 | The offer and all documents enclosed with offer should be in English language only.
SCOPE :
DESIGN, MANUFACTURING, TESTING, PACKING, SUPPLY, ERECTION AND COMMISSIONING OF 11 KV VCB PANEL
S.NO. | DESCRIPTION FOR BHEL REQUIREMENT |  |  |  | OFFERED | DEVIATIONS
1 | This specification governs the quality requirements of design, manufacturing, testing, packing at supplier works, delivery, erection and commissioning of 11KV, 630 Amp. VCB panel. |  |  |  | VENDER TO CONFIRM
1.1 | STANDARD APPLICABLE
| SWITCHGEAR : | IS:13118-1991/ IS:3427-1969 |  |  | VENDER TO CONFIRM
| CT | : IS:2705 -1992 |  |  | VENDER TO CONFIRM
| PT | IS:3156 -1992 |  |  | VENDER TO CONFIRM
| STATUTORY | : MEETS INDIAN ELECTRICITY RULES |  |  | VENDER TO CONFIRM
1.2 | Quantity | 2 Set |  |  | VENDER TO CONFIRM
1.3 | Location | 1 set for 33/11 KV sub-station and 1 set for Loco testing sub-station |  |  | VENDER TO CONFIRM
2 | REQUIREMENT
2.1 | 11KV, 630 Amp., 25KA Indoor Type multiple VCB panel with 1 No. incomer and 2 Nos. outgoing. Panel shall be complete with air insulated 3 phase bus bar, earth bars, small wiring, terminal board, fuses, foundation bolt and sundries. |  |  |  | VENDER TO CONFIRM
| Description |  | Incomer | Out going | OFFERED | DEVIATIONS
3 | 11KV, 630 Amp. Horizontal drawout type Vacuum circuit breaker. |  | 1 No. | 2 Nos. | VENDER TO CONFIRM
3.1 | Vacuum circuit breaker comprising of following:
i | Motor/ Manual spring charging mechanism |  |  |  | VENDER TO CONFIRM
ii | Closing & Tripping Coil SUITABLE FOR 30/110V DC |  |  |  | VENDER TO CONFIRM
iii | 8 No +8 NC Auxiliary Switch |  |  |  | VENDER TO CONFIRM
iv | Mechanical ON/OFF Indication |  |  |  | VENDER TO CONFIRM
v | Mechanical Spring charge/Discharge indication |  |  |  | VENDER TO CONFIRM
vi | Braker Position Indicator |  |  |  | VENDER TO CONFIRM
vii | Mechanical Operation Indicator |  |  |  | VENDER TO CONFIRM
viii | Automatic Safety Shutters |  |  |  | VENDER TO CONFIRM
ix | Secondary self-aligned plug in contacts |  |  |  | VENDER TO CONFIRM
x | Anti-Pumping feature |  |  |  | VENDER TO CONFIRM
3.2 | 11 kV Epoxy Resin Cast current Transfromer/5-5A |  | 3 Nos | 6 Nos | VENDER TO CONFIRM
i | Core-I: Cl.0.5 with 15VA burden for Metering |  |  |  | VENDER TO CONFIRM
ii | Core-II: Cl. 5P10 with 15 VA burden for Proction |  |  |  | VENDER TO CONFIRM
3.3 | 11 Kv Epoxy Resin Cast Potential Transfrome |  | 1 No. | NIL | VENDER TO CONFIRM
i | Ratio :11 kV/v3/110V/v3,3 Phase, Drawout Type. |  |  |  | VENDER TO CONFIRM
ii | Core-I: Cl. 1.0 with 100 VA burden for Metering |  |  |  | VENDER TO CONFIRM
3.4 | Meter: Size :96 x 96 |  |  |  | VENDER TO CONFIRM
i | Analog Ammeter with selector switch/5A |  | 1 No. | 2 Nos. | VENDER TO CONFIRM
ii | Analog Voltmeter with selector switch |  | 1 No. | 2 Nos. | VENDER TO CONFIRM
iii | Multifunction meter. Class 0.5 |  | 1 No. |  | VENDER TO CONFIRM
iv | KWH Meter digital type |  | 1 No. | 2 Nos. | VENDER TO CONFIRM
3.6 | Relays: |  |  |  | VENDER TO CONFIRM
i | Numerical Non-Directional IDMT 3O/C+1 E/F Relay |  | 1 No. | 2 Nos. | VENDER TO CONFIRM
ii | Master Trip Relay |  | 1 No. | 2 Nos. | VENDER TO CONFIRM
iii | Aux. Relay |  | NIL | 4 Nos | VENDER TO CONFIRM
3.7 | Indicating Lamps/Push Buttons: |  |  |  | VENDER TO CONFIRM
i | R,Y,B Indication Lamp |  | 3 Nos | 6 Nos | VENDER TO CONFIRM
ii | Braker ON/OFF Indicating Lamps |  | 2 Nos | 4 Nos | VENDER TO CONFIRM
iii | Spring charging indication Lamps |  | 1 No. | 2Nos | VENDER TO CONFIRM
iv | Trip indication Lamps |  | 1 No. | 2 Nos. | VENDER TO CONFIRM
v | Trip Circuit Healthy Indication |  | 1 No. | 2 Nos. | VENDER TO CONFIRM
3.8 | Miscellaneous Items: |  |  |  | VENDER TO CONFIRM
i | Trip/ Neutral/ Close Switch |  | 1 No. | 2 Nos. | VENDER TO CONFIRM
ii | Trip Circuit Healthy Push Buttom |  | 1 No. | 2 Nos. | VENDER TO CONFIRM
iii | MCB for AC and DC Supply |  | 2 Nos | 4 Nos | VENDER TO CONFIRM
iv | 4 Window Annunciator With Hooter |  | 1 No. | 2 Nos. | VENDER TO CONFIRM
v | Panel space heater with thermostat |  | 1 No. | 2 Nos. | VENDER TO CONFIRM
vi | Bus Bar Aluminium |  | 1 Set | 2 Set | VENDER TO CONFIRM
vii | Panel illumination with switch |  | 1 No. | 2 Nos. | VENDER TO CONFIRM
viii | 5 Amp 3 pin socket |  | 1 No. | 2 Nos. | VENDER TO CONFIRM
ix | Control fuses, ferules & wiring |  | 1 Set | 2 Set | VENDER TO CONFIRM
x | M.S Cubical with powder coating |  | 1 Set | 2 Set | VENDER TO CONFIRM
3.9 | Accessaries
i | spring charging handle |  | 1 No. | 2 No. | VENDER TO CONFIRM
ii | interlocking/racking & slow charging handle |  | 1 No. | 2 Nos. | VENDER TO CONFIRM
4 | GENERAL
4.1 | All the drawing including outline general arrangement shall be submitted to us in Triplicate for approval before commencement of work. |  |  |  | VENDER TO SUBMIT
4.2 | 3 sets of operation/maintenance manual shall be supplied. |  |  |  | VENDER TO CONFIRM
4.3 | At least 15 day advance information should be given to enable us to depute our representative for inspection / testing. Dispatch shall be affected only after inspection |  |  |  | VENDER TO CONFIRM
4.4 | Aluminum anodized name plate for outgoing circuit shall be screwed in front and back of the panel. |  |  |  | VENDER TO CONFIRM
4.5 | The equipment shall be guaranteed in respect of material construction and operation against any manufacturing and design defect for a period of 24 months after supply. |  |  |  | VENDER TO CONFIRM
4.6 | Offer shall be sent with complete literature and necessary details. |  |  |  | VENDER TO SUBMIT
5 | QUALIFYING CONDITION
5.1 | Only those venders, who are in the line of panel manufacturing or authorized agents of panel manufacturer, shall quote. The following information’s are to be submitted with the offer. This is required from venders for qualifications of their offers. |  |  |  | VENDER TO SUBMIT
a | Name of the panel manufacturer and company profile |  |  |  | VENDER TO SUBMIT
b | Details of manufacturing facilities available at manufacturer works |  |  |  | VENDER TO SUBMIT
c | Details of test facilities available at manufacturer works. |  |  |  | VENDER TO SUBMIT
6 | BHEL reserves the right to verify information submitted by vender. In case the information is found to be false/ incorrect, the offer shall be rejected |  |  |  | VENDER TO SUBMIT
S.J.Chakraborty |  |  | Inder mathur |  | Sujeet Srivastava
Sr. DGM (WE&S) |  |  | Manager (WE&S) |  | Sr. Engineer (WE&S)