## INDENTED MATERIALS (hidden)
2018-07-05
SL.NO | MATERIAL CODE | DISCRIPTION | QTY | UNIT PRICE | TOTAL PRICE | PR NO
1 | EL1901IBM22 | LOCAL REMOTE SWITCH | 2 |  |  | 12301088
2 | SWTCD220N25 | BREAKER CONTROL SWITCH TNC 25A 220V DC | 3
3 | SWASA415N10 | AMMETER SELECTOR SWITCH 10A 415V AC | 1
4 | ELLPGCLMS063 | TRIP SELECTOR SWITCH | 7
5 | ELBLRMIS01 | DOOR HANDEL | 2
6 | ELBLRMIS02 | ON/OFF SWITCH FOR SFU MODEL | 1
9 | ELBLRMIS05 | CONTROL BUS COPPER 320mm LENGTH | 24 | 410
10 | ELBLRMIS06 | CONTROL BUS COPPER 120mm LENGTH | 55 | 210
11 | ELBLRMIS07 | CONTROL BUS ALUMINIUM 120mm length | 16 | 100
12 | ELBLRMIS08 | CONTROL BUS COPPER 750mm LENGTH | 9 | 560
13 | ELBLRMIS09 | CONTROL BUS COPPER 600mm LENGTH | 5 | 500
14 | ELBLRMIS10 | CONTROL BUS ALUMINIUM 600mm length | 2 | 340
15 | ELBLRMIS11 | ALUMINIUM FISH PLATE 435mm | 42 | 260
16 | ELBLRMIS12 | RUBBER BELLOW | 4 | 6500
ADD ITEM 6/7/2018
17 | ELBLRMIS13 | Copper control Bus Bar 480 | 8 | 620
18 | ELBLRMIS14 | Copper control Bus Bar 185 | 95 | 410
19 | ELBLRMIS15 | Alluminium Space Heater Bus Bar 185 | 8 | 140
|  | Copper control Bus Bar 750 | 4 | 560
20 | ELBLRMIS16 | Copper control Bus Bar 135 | 33 | 230
21 | ELBLRMIS17 | Alluminium Space Heater Bus Bar 135 | 6 | 140
22 | ELBLRMIS18 | Copper control Bus Bar 500 | 12 | 500
23 | ELBLRMIS19 | Copper control Bus Bar 235 | 12 | 410
24 | ELBLRMIS20 | Copper control Bus Bar 135 | 12 | 230
25 | ELBLRMIS21 | Alluminium Space Heater Bus Bar 235 | 2 | 340
| ELBLRMIS22 | Alluminium Space Heater Bus Bar 135 | 2 | 140
|  | TRIP Selection Switches | 6
26 | HBFFAEAGNBA1BNA1XE | Numerical Relay of ABB make REM615 model | 1 | 125000
27 | HBFFAEAGNBA1BNA1XE | Numerical Relay of ABB make REM615 model | 1 | 125000

## ADD ITEMS (hidden)
Short Supplied / replacement Items for LT MCC panels supplied for CHP & AHP of Unit#3, 1X700MW, Bellary Site
Sl.No. | Description of the Item | Length (mm) | Quantity (Nos.) | Materials received as on 24.06.2017 | MCC Panel | Remarks
1 | Copper control Bus Bar | 480 | 8 | 8 | ASAW PH MCC ( Ash Handling)
2 | Copper control Bus Bar | 185 | 95 | 95
3 | Alluminium Space Heater Bus Bar | 185 | 8 | 8
4 | Copper control Bus Bar | 750 | 4 | 4 | MCC-8 WT-5 MCC
5 | Copper control Bus Bar | 135 | 33 | 33
6 | Alluminium Space Heater Bus Bar | 135 | 6 | 6
7 | Copper control Bus Bar | 500 | 12 | 12 | MCC-8 WT-4 MCC
8 | Copper control Bus Bar | 235 | 12 | 12
9 | Copper control Bus Bar | 135 | 12 | 12
10 | Alluminium Space Heater Bus Bar | 235 | 2 | 2
11 | Alluminium Space Heater Bus Bar | 135 | 2 | 2
12 | Door Locks |  | 333 | 700 | MCC-10 | EPD has sent 700 nos. Locks to replace the damaged ones. But, Customer is asking for complete replacement as the old locks are of very low quality
|  |  | 452 |  | ASAW PH MCC
|  |  | 320 |  | MCC-8 WT-4 MCC
|  |  | 275 |  | MCC-8 WT-5 MCC
|  |  | 811 |  | MCC-9
|  |  | 304 |  | SILO MCC
13 | Missing DOL modules & Control transformers. These modules have been noticed missing while unpacking the panels. Still, the MCC-9 PANELS have not been erected. List of the modules missing from MCC-9 will be intimated once the panel erection works start. |  | 2 |  | ASAW PH MCC ( Ash Handling) | Module No.19FE- 110VAC CONTROL TRANSFORMER MODULE. MODULE NO.23FC-2.5KW SPARE DOL MODULE
|  |  | 2 |  | MCC-8 WT-4 MCC | Module No.5FD- 1.1 KW ACTUATOR-1 MODULE. MODULE NO.5FC-3.7KW FLAP GATE III-1 MODULE
14 | TRIP Selection Switches |  | 6 |  | 1 each for MCC-8(WT-4), MCC-8 WT-5, MCC-9, MCC-10, ASAW MCC & SILO MCC | Additonal switch needs to be installed as Synch circuit of Bus coupler is not working properly.
Rectification / repair of Items for LT MCC panels supplied for CHP & AHP of Unit#3, 1X700MW, Bellary Site
Sl.No. | Description of Item | Description of the Issue |  | Action required | Status As on Date
1 | Numerical Relay of ABB make REM615 model | The display screen of the One no. ABB make relay of REM615 model is found faulty. The display screen is not readable as the brightness is very high and we are not able to adjust the brightness from the key pad (with the help of ESC and DOWN Keys). But, the function of the relay is OK, as it is generating all the outputs perfectly. Sl.No. of the Relay is 1VYV91125007 & Order Code:HBFFAEAGNBA1BNA1XE. |  | Repair / Replacement of Relay.
2 | Numerical Relay of ABB make REM615 model | 4 Nos. Relays of REM615 model (Order Code: HBFFAEAGNBA1BNA1XD), supplied for the motor feeders of WT-5 MCC panels have been tested with secondary injection kit and relays are operating satisfactorily by generating all the outputs correctly. But, in the Fault records, it is not displaying the Fault name (like PHIPTOC or EFHPTOC etc.,) and also not displaying the operating time of the fault. Remaining details like fault time stamp, current & voltage values at that instant are being shown correctly.

## BOQ
BILL OF QUANTITY
SL.NO | MATERIAL CODE | DISCRIPTION | MAKE | TYPE | MODEL & SPEC | QTY | UNIT
1 | EL1901IBM22 | LOCAL REMOTE SWITCH | KAYCEE | 32A, 2WAY, 4 POLE WITH OFF, 220VDC |  | 2 | EA
2 | SWTCD220N25 | BREAKER CONTROL SWITCH TNC 25A 220V DC | KAYCEE | BREAKER CONTROL SWITCH TNC 25A 220V DC |  | 3 | EA
3 | SWASA415N10 | AMMETER SELECTOR SWITCH 10A 415V AC | KAYCEE | 6A ASS |  | 1 | EA
4 | ELLPGCLMS063 | TRIP SELECTOR SWITCH | KAYCEE | 16A, 3WAY, 12 POLE, WITH OUT OFF, 220V DC |  | 7 | EA
5 | ELBLRMIS01 | DOOR HANDLE FOR PANELS | C&S | As per photo attached |  | 2 | NUM
6 | ELBLRMIS02 | ON/OFF SWITCH FOR SFU MODLE | C&S | As per photo attached |  | 1 | NUM
7 | ELBLRMIS05 | CONTROL BUS COPPER 320mm LENGTH | COPPER ELECTRICAL GRADE | 6x6sq.mm of 320mm length, WITH TWO HOLES | AS PER IS 613- 1984 | 24 | NUM
8 | ELBLRMIS06 | CONTROL BUS COPPER 120mm LENGTH | COPPER ELECTRICAL GRADE | 6x6sq.mm of 120mm length, WITH TWO HOLES | AS PER IS 613- 1985 | 55 | NUM
9 | ELBLRMIS07 | CONTROL BUS ALUMINIUM 120mm length | COPPER ELECTRICAL GRADE | 6x6sq.mm of 120mm length, WITH TWO HOLES | AS PER IS 5082 | 16 | NUM
10 | ELBLRMIS08 | CONTROL BUS COPPER 750mm LENGTH | COPPER ELECTRICAL GRADE | 10x5sq.mm of 750mm length, WITH TWO HOLES | AS PER IS 613- 1984 | 9 | NUM
11 | ELBLRMIS09 | CONTROL BUS COPPER 600mm LENGTH | COPPER ELECTRICAL GRADE | 6x6sq.mm of 600mm length, WITH TWO HOLES | AS PER IS 613- 1984 | 5 | NUM
12 | ELBLRMIS10 | CONTROL BUS ALUMINIUM 600mm length | ALLUMINIUM ELECTRICAL GRADE | 10x5sq.mm of 600mm length, WITH TWO HOLES | AS PER IS 5082 | 2 | NUM
13 | ELBLRMIS11 | ALUMINIUM FISH PLATE 435mm | ALLUMINIUM ELECTRICAL GRADE | 150x10sq.mm of 435 mm length, WITH TWO HOLES | AS PER IS 5082 | 42 | NUM
14 | ELBLRMIS12 | RUBBER BELLOW | AS PER DRG. ATTACHED |  |  | 4 | NUM
15 | ELBLRMIS13 | Copper control Bus Bar 480 | COPPER ELECTRICAL GRADE | 6x6sq.mm of 480mm length, WITH TWO HOLES | AS PER IS 613- 1984 | 8 | NUM
16 | ELBLRMIS14 | Copper control Bus Bar 185 | COPPER ELECTRICAL GRADE | 6x6sq.mm of 185mm length, WITH TWO HOLES | AS PER IS 613- 1984 | 95 | NUM
17 | ELBLRMIS15 | Alluminium Space Heater Bus Bar 185 | COPPER ELECTRICAL GRADE | 10x5sq.mm of 185mm length, WITH TWO HOLES | AS PER IS 5082 | 8 | EA
18 | ELBLRMIS16 | Copper control Bus Bar 135 | COPPER ELECTRICAL GRADE | 6x6sq.mm of 135mm length, WITH TWO HOLES | AS PER IS 613- 1984 | 33 | NUM
19 | ELBLRMIS17 | Alluminium Space Heater Bus Bar 135 | ALLUMINIUM ELECTRICAL GRADE | 10x5sq.mm of 135mm length, WITH TWO HOLES | AS PER IS 5082 | 6 | NUM
20 | ELBLRMIS18 | Copper control Bus Bar 500 | COPPER ELECTRICAL GRADE | 6x6sq.mm of 500mm length, WITH TWO HOLES | AS PER IS 613- 1984 | 12 | NUM
21 | ELBLRMIS19 | Copper control Bus Bar 235 | COPPER ELECTRICAL GRADE | 6x6sq.mm of 235mm length, WITH TWO HOLES | AS PER IS 613- 1984 | 12 | NUM
22 | ELBLRMIS20 | Copper control Bus Bar 135 | COPPER ELECTRICAL GRADE | 6x6sq.mm of 135mm length, WITH TWO HOLES | AS PER IS 613- 1984 | 12 | NUM
23 | ELBLRMIS21 | Alluminium Space Heater Bus Bar 235 | ALLUMINIUM ELECTRICAL GRADE | 10x5sq.mm of 235mm length, WITH TWO HOLES | AS PER IS 5082 | 2 | NUM
24 | ELBLRMIS22 | Alluminium Space Heater Bus Bar 135 | ALLUMINIUM ELECTRICAL GRADE | 10x5sq.mm of 135mm length, WITH TWO HOLES | AS PER IS 5082 | 2 | NUM
25 | HBFFAEAGNBA1BNA1XE | Numerical Relay of ABB make REM615 model | ABB | REF | HBFFAEAGNBA1BNA1XE | 2 | EA
26 | ELBLRMIS23 | HARDWARE FOR BELLARY SITE AS PER BELOW LIST |  |  |  | 1 | LOT