## AHP Scope Matrix
ANNEXURE-3-ELECTRICAL, CONTROL AND INSTRUMENTATION SCOPE MATRIX FOR | [5 empty] | 1X800 MW HPGCL YAMUNA NAGAR | Rev: 00 Dated: 12-06-2025
SL. NO. | SCOPE DETAILS | INPUT DETAILS | ENGINEERING / DESIGN | SUPPLY | RECEIPT, UNLOADING, STORAGE, ERECTION, TESTING, COMMISSIONING | REMARKS
1 | Complete Electrical and C&I System except for BHEL free issue equipment's as below 1) 11KV Switchboard 2) 6.6KV Switchboard 3) 6.6KV HT Motor 4) DCS 5) VMS Note: 1.All AC/DC/UPS/Aux Power supply required for BHEL free issue equipment's shall be in bidders scope. 2.O&M of BHEL Free issue equipment's shall be in bidders scope. | EPC Bidder | EPC Bidder | EPC Bidder | EPC Bidder | Location of BHEL free issue equipments shall be decided based on final layout engineering by successful bidder and space shall be considered by bidder in switchgear building/control Room with all facilities. All other required civil facilities like anchor/kerb angles/insert plates/support structures/base frames/channels etc. shall be considered by bidder . Supply and E&C of all HT/LT power, control, signal, and communication cables, Cable trays, supports, earthing, electronic earthing material for BHEL free issue items shall be in Bidder's scope Unloading and storage of BHEL free issue items shall be in the scope of BHEL. BHEL region shall issue these items to EPC bidder. Local loading/unloading /transportation of these materials from BHEL storage to bidders storage/facilities shall be in bidders scope. Bidder shall provide min. 2 Nos. uncabled feeders each of 250A, 100A, 63A, 32A, 16A rating (1 No in in I/C-1 and 1 No in I/C-2) in all 415V PMCC boards supplied by Bidder for BHEL use. Load of 100KVA for each MCC shall be considered for these loads while transformer sizing. Data Concentrator system or Relay Network for BHEL free issue equipment as applicable up to Central Control room (TG building) shall in bidders scope . This battery limit is also applicable for LT switchgear. Bidder shall provide the Illumination, Earthing, Lightning protection for all areas where Civil & structural is in bidder scope. Wherever integration of bidder supplied items with BHEL supplied system is involved, necessary integration shall be done by the bidder. Security of all equipment’s including BHEL free supply till handing over to end customer is in scope of bidder. Obtaining Statutory clearance is in Bidders scope including BHEL free issue equipment's.
2 | 1. MCC buildings/control rooms/ any other electrical building required as per scope of this pacakge 2. Cable trestle/rack required as below in is bidders scope. a. For all bidders facilities . b. For BHEL free supply items located in BHEL buildings & bidder buildings c.Any interconnection required for bidder equipment from BHEL buildings | EPC bidder | EPC bidder | EPC bidder | EPC bidder | Quantity & location of MCC building marked in plot plan is tentative only . Bidder to decide the Quantity and locations of MCC buildings without disturbing other facilities of BHEL . Connection between oil retention pit( Bidders scope of Transformer) to common oil retention pit located in main plant area is in bidders scope. The interconnection between Bidders earthing and Existing/Main earth grid is in Bidder scope. Please refer plot plan Annexure 1 for further details
BHEL FREE ISSUE EQUIPMENTS
3 | 11KV and 6.6KV Switchboard One number each of 11kV and 6.6kV HT switchboards, with the maximum available outgoing feeders as mentioned in Sl No 11 and 12, shall be provided to the bidder as a BHEL free issue equipment for the entire scope of work. | EPC Bidder | BHEL BHOPAL | BHEL BHOPAL | EPC Bidder | Bidder to refer Sl No 10 for 11kV power supply source availability. Bidder shall submit Electrical load list and transformer sizing within 3 months from LOI All Upstream/downstream tripping and interface/signal exchange between Sl No 10, 11, 12 shall be in the bidder’s scope. The bidder shall ensure that the maximum loading at the 11kV level does not exceed the maximum cut-off MVA specified in Sl. No. 10. Bidder shall determine the appropriate rating of the 11/6.6 kV transformer and ensure that the maximum loading at the 11 kV level does not exceed the maximum cut-off MVA specified in Sl. No. 10. Few additional 11KV/6.6KV feeder will be addded in these boards for BHEL requirement and exact quantity will be decided during detailed engineering. Increase in panel length due to this shall be accommodated by bidder by considering additional space without any commercial implication to BHEL. Cable tray/Supports/earthing within the bidders switchgear building is in the scope of bidder. During the engineering of the HT bus duct, interconnection between the bidder-supplied 11/6.6 kV transformer and the BHEL free-issued 6.6 kV switchboard, the bidder shall ensure that relevant inputs are obtained from BHEL for the termination of the HT bus duct at the 6.6 kV switchgear end. The bidder shall also ensure that the forward phase sequence, correct CT parameters are maintained during detalied engineering of 11kV and 6.6KV Switchboard. It is the bidder’s responsibility to avoid any mismatch in this interface, and any modifications required at a later stage shall be within the bidder’s scope without any commercial implication to BHEL
4 | HT Motors for Water and Slurry Pump application Bidder to refer Sl No 13 for BHEL free issue HT motors available to bidder Note : HT motor for any other applications other than Water and Slurry Pump is in bidders scope. | EPC Bidder | BHEL BHOPAL | BHEL BHOPAL | EPC Bidder | Bidder shall provide qty, rating, TS curve, speed, GD2 type of mounting and coupling details as input to BHEL within 4 months from LOI. Temperature measuring system, LPBS for all BHEL free issue HT motors shall be in the bidder’s scope . The supply of consumables and lubrication for BHEL free issue HT motors is included in the bidder’s scope. Before shifting motors from BHEL storage to bidders storage/facilities, the bidder shall conduct motor testing. In case any fault occurs during operation and BHEL recommends repair at the factory premises, the bidder shall decouple/remove the motor and shift it to the BHEL storage. After repair, the bidder shall again unload, erect and test the motor. If any EPC bidder designed equipment requires job motor during inspection of the equipment, then BHEL shall transport directly to manufacturers works. post inspection despatch of motor directly to project site including loading, unloading storage is in bidders scope. Any damage during transit shall be dealt as per BHEL commercial terms and conditions
5 | AHP (DCS) , software development and other equipment related to DCS ( DCS panels, Network panels, LVS, PCs, Printers, furniture desk, Chairs, PC Consoles, Servers, EMS, OWS/OEWS/EWS) | EPC Bidder | BHEL EDN | BHEL EDN | EPC Bidder | Bidder's scope includes the following: 1. Detailed IO list including BHEL free issue items , KKS tagging, P&ID Diagram, set-points, Control Philosophy & write up, block logic diagram & HMI screens (for software development), Functional grouping. 2.Detailed IO list shall be submitted within 6 months of LOI in the format prescribed by BHEL which shall be shared to sucessful bidder . Any addition of IO's at later stage is not acceptable. 3. Bidder shall visit BHEL/Customer during software development, application testing , FAT and ensure the completeness of software for E&C. 4. Any logic modificationduring commissioning stage shall be executed by EPC bidder. 5. 24V DC and UPS system (UPS load and 24V DC load applicable to BHEL free supplied equipments shall be shared to successful bidder during detailed engineering by BHEL-EDN.Bidder to size the rating of UPS and DC system considering the above load plus any load required for bidder supplied equipments.) 6.Complete PLC system, for HCSD System, Classifier, Baggifier, DBA and any other PLC operated equipment's, including its HMI, UPS, PC, printers, battery, battery charger etc.
6 | Vibration Monitoring/Analysis System (VMS/VMAS ) | EPC Bidder | BHEL EDN | BHEL EDN/EPC Bidder | EPC Bidder | Bidder to provide sensor and key phasor mounting arrangement for bidder supplied equipment's as per contractual requirement. Sensors, Prefab Sensor cables from sensor up to Field mounted local JB near Motor and VMS panel shall be supplied as free issue to Bidder. Balance items required for completeness of the system are in the scope of Bidder.
7 | Roof Top Solar System | BHEL-SBD/RUDRAPUR | EPC Bidder | EPC Bidder | EPC Bidder | For estimation, the Bidder may take 50 KWp of the total capacity of the Solar Plant Defined for this Project as a whole. Further before placement of the order, Bidder to ensure that the items thus procured shall be of the same make as installed in the main Plant area supplied by BHEL.
BHEL Supply items which are to be located in Bidder's scope of buildings in addition to BHEL Free supply Items
8 | CCVM System | BHEL EDN / EPC BIDDER | BHEL EDN | BHEL EDN | BHEL PS REGION | Location of these equipment's shall be decided based on final layout engineering by successful bidder and space shall be considered by bidder in switchgear building, control room, any other buildings. All other required civil facilities like anchor/kerb angles/insert plates/support structures/base frames/channels etc. shall be considered by bidder as required during Detailed ENGG. All AC/DC/UPS/Aux Power supply required for above equipment's shall be arranged by bidder.
9 | PA System | BHEL PEM / EPC BIDDER | BHEL PEM | BHEL PEM | BHEL PS REGION
Available feeder and motor list to bidder. Below mentioned number is maximum available offered as free supply to bidder, Any additional requirement shall be supplied by bidder as per bidder design requirement without any commercial implication to BHEL.
10 | List of uncabled 11KV source feeders available to bidder. a) Only 2 No of 11KV uncabled Feeder shall be provided by BHEL to bidder for AHP application at two locations as mentioned below: Location-1 & 2 : Both un-cabled 11kV feeders are available at 3.5 Meter MV Switchgear room of Power house building. |  |  |  |  | a) 11KV Tie feeder for 11 kV AHP switchboard at Sl No 3 - Maximum MVA available is 10 MVA. | Battery limit for Cable rack, cable trays, supports for 11KV Tie feeder from Main plan TG building (3.5m MV Swgr Room Power House) to 11kV AHP switchboard is as below : Adequate nos. of cable trays and tray support from Main Power House MV Swgr room to C-row pipe cum cable rack upto Column number-1 shall be provided by BHEL for bidder's scope of 11kV Cables for feeding the 11kV AHP Switchboard. During contract stage, Vendor will provide the number of cable trays required along with their loading details as input to BHEL . Beyond this point, only space shall be provided for vendor in BHEL cable trestle upto the nearest planned BHEL cable trestle near 11kV AHP siwtchboard. Supply & installation of Cable Trays and support in BHEL's cable trestle shall be in Bidder's scope. During contract stage, Vendor will provide the number of cable trays required along with their loading details as input to BHEL for reserving the space in BHEL Cable trestle/ cable rack for bidder's cables. Further, Cable rack along with cable trays & support shall be provided by Vendor for connecting the 11kV AHP Switchgear room with the nearest BHEL cable trestle. Complete cable supply, laying & termination at both ends (i.e. from 3.5m MV Swgr Room in Power House to 11kV AHP Switchboard) is in bidder's scope.
11 | List of 11KV O/G feeders available to bidder. Location of switchboard : To be decided by Bidder |  |  |  |  | a) 11KV Transformer Feeder (11/6.6kV )- up to 16MVA b) 11KV Transformer Feeder (11/0433kV)- up to 2500KVA | a) 2 Nos b) 6 Nos
12 | List of 6.6KV O/G feeders available to bidder. Location of switchboard : To be decided by Bidder |  |  |  |  | a) 6.6KV Motor feeder b) 6.6KV Transformer Feeder VFD application | a) 22 Nos b) 0 Nos
13 | BHEL free issue HT motors available to bidder |  |  |  |  | 6.6KV Motor | 16 Nos
Battery limit for hopper level integration of AHP sytem
14 | ESP Hopper Level | BHEL-RANIPET | BHEL-RANIPET | BHEL-RANIPET | BHEL-RANIPET | ESP hopper High & Low level switches and wiring up to ESP MCC are excluded from bidder scope. However, Cable & Cabling from ESP MCC to AHP DCS is in the scope of bidder. IO's for the above shall be considered by bidder in IO list and all the associated cabling.
15 | APH/ECO/DUCT/SCR Hopper Level | BHEL-TRICHY | BHEL-TRICHY | BHEL-TRICHY | BHEL-TRICHY | Level switches for Economizer / APH hoppers/Duct Hopper are excluded from bidder scope. However, Cable & Cabling from Level Switches/ Junction Boxis in the scope of bidder. IO's for the above shall be considered by bidder in IO list and all the associated cabling.
Name of BHEL UNIT for coordination with successful bidder of various system during Engineering
Sl No | System |  |  |  |  | BHEL-Unit
A | Plot Plan with Switchgear location, cable routing, earthing, illumination |  |  |  |  | BHEL-ISG/BHEL PEM
B | Electrical and C&I system other than below listed |  |  |  |  | BHEL-ISG
1 | Design and integration of 6.6KV and 11KV system along with upstream breaker interface |  |  |  |  | BHEL-PEM/ BHEL-BHOPAL
2 | DCS, VMS, UPS, 24V DC System |  |  |  |  | BHEL-EDN
3 | CCVM System |  |  |  |  | BHEL-EDN
4 | PA System |  |  |  |  | BHEL-PEM
5 | Roof Top Solar System |  |  |  |  | BHEL-SBD/Rudrapur
6 | HT Motors for Water and Slurry Pump |  |  |  |  | BHEL-BHOPAL
7 | ESP Hopper Level |  |  |  |  | BHEL-RANIPET
8 | APH/ECO/DUCT/SCR Hopper Level |  |  |  |  | BHEL-TRICHY
9 | Fire Fighting and FDA system |  |  |  |  | BHEL-PE&SD

## Sheet1 (hidden)
PESD to inform the no of panels with dimensipns to ber located in CHP area
EDN inputs DCS
what about DG?
bunker level monitoring system
Whether BHEL supplied items to be kept in power sector stores or Bidder stores
BHEL Supplied equipments shall be erected by region or bidder
what about raod scope? What about lighting for the roads
Construction power supply?
Man power ?
CHP MCC located in other than CHP area
Other unit MCC like FGD kept in our area
Solar PV plants covered in civil scope check?
Should we tell the maximum load required because Statuion transformer has been sized?
electrical design softwares