| PSGSG/12-13/02 | SPECIFICATIONS FOR “O RINGS” |  | Drg.No. |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Date | 11.11.14 |  |
|  |  |  | Product | GSM245 |  |
| 1.0 | APPLICATION: EPDM “O rings” as per dimensions given below are required for sealing gas insulated switchgear equipment. |  |  |  |  |
| 2.0 2.1 2.2 | SPECIFICATION: Material : EPDM “O-rings” as per following profile with S.H. of 70 ± 5 have to be supplied: |  |  |  |  |
| ## Page 1/2 | PSGSG/12-13/02.doc |  |  |  | Signature |

Contd..

| PSGSG/12-13/02 | SPECIFICATIONS FOR “O RINGS” | Drg.No. |  |
| --- | --- | --- | --- |
|  |  | Date | 11.11.14 |
|  |  | Product | GSM245 |
| 2.3 2.4 2.5 2.6 2.7 2.8 | List of “O Rings” to be supplied: S.No; Inner Diameter (ID), mm; Outer Diameter (OD),mm; Thickness in (mm); Qty.. 1; 570; 590; 10; 100. 2; 270; 286; 8; 30. 3; 120; 136; 8; 30. 4; 750; 770; 10; 8. 5; 390; 406; 8; 30. 6; 350; 366; 8; 100. 7; 70; 80; 5; 30. The supplier shall submit material composition report and hardness values for the material. The component shall be free from pin holes, cracks and shall be leak proof. Necessary test reports shall be furnished. O-rings shall be part of switchgear equipment which works under the gas pressure difference of 11.0 bar. The supplier shall quote on the basis of per unit of each type of O-ring. The material shall be packed individually in appropriate packing so as to protect o-ring surface and prevent de-shaping of the material during transportation. Test certificates shall be provided along with the delivery of the components. |
| Page 2/2 | PSGSG/12-13/02.doc | Signature |  |

| PSGSG/12-13/02 | SPECIFICATIONS FOR “O RINGS” | Drg.No. |  |
| --- | --- | --- | --- |
|  |  | Date | 24.07.14 |
|  |  | Product | GSM245 |
| 2.9 3.0 | The supplier should have National/International repute with proven record and should have. supplied similar ”O’ rings for GIS/Switchgear applications to GIS manufacturers worldwide. The supplier must submit along with the quotation a few references to whom the supplier has supplied a similar material. In case of doubts in specifications the supplier shall contact BHEL for clarifications. |  |  |
| Page 2/2 | PSGSG/12-13/02.doc | Signature |  |