## EM5
Ind No 79887 Dtd 4/3/08
|  |  |  | PDB 5-EM-F | INDICATING LAMPS
|  |  | TPN-415V AC |  |  |  | DIGITAL AMETER |  | VOLTMETER WITH VSS
S NO | DESCRIPTION | AMPS | SFU RATING | CABLE SIZE FOR | INCOM | OUTGOING | INCOMING | OUTGOING | INCOMING | OUTGOING
|  |  | AMPS | CONNECTIONS
1 | INCOMER > | 400 | SFU | 240MM SQX4 .X2 RUNS ARM | 3NOS. | 3NOS. | YES | NO | YES | YES
OUTGOINGS
1 | P1-1 | 250 | 250 | 3.5X240MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
2 | P1-2 | 100 | 100 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
3 | P1-3 | 250 | 250 | 3.5X240MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
4 | P1-4 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
5 | P1-5 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
6 | P1-6 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
7 | P1-7 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
8 | P1-8 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES

## EM4
Ind No 79887 Dtd 4/3/08
|  |  |  | PDB 4EM-F | INDICATING LAMPS
|  |  | TPN-415V AC |  |  |  | DIGITAL AMETER |  | VOLTMETER WITH VSS
S NO | DESCRIPTION | AMPS | SFU RATING | CABLE SIZE FOR | INCOM | OUTGOING | INCOMING | OUTGOING | INCOMING | OUTGOING
|  |  | AMPS | CONNECTIONS
1 | INCOMER > | 800A | ACB-1000A | 240MM SQX4 .X4 RUNS ARM | 3NOS. | 3NOS. | YES | NO | YES | YES
OUTGOINGS
1 | P7-1 | 600 | 600 | 3.5X240MM SQX3 ARM | 3NOS. | NIL | NO | YES | NO | YES
2 | P7-2 | 300 | 300 | 3.5X240MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
3 | P7-3 | 250 | 250 | 3.5X240MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
4 | P7-4 | 400 | 400 | 3.5X240MM SQX2 ARM | 3NOS. | NIL | NO | YES | NO | YES
5 | P7-5 | 100 | 100 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
6 | P7-6 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
7 | P7-7 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
8 | P7-8 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
9 | P7-9 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES

## EM3
Ind No 79887 Dtd 4/3/08
|  |  |  | PDB 3-EM-F | INDICATING LAMPS
|  |  | TPN-415V AC |  |  |  | DIGITAL AMETER |  | VOLTMETER WITH VSS
S NO | DESCRIPTION | AMPS | SFU RATING | CABLE SIZE FOR | INCOM | OUTGOING | INCOMING | OUTGOING | INCOMING | OUTGOING
|  |  | AMPS | CONNECTIONS
1 | INCOMER > | 800A | ACB-1000A | 240MM SQX4 .X4 RUNS ARM | 3NOS. | 3NOS. | YES | NO | YES | YES
OUTGOINGS
1 | P4-1 | 400 | 400 | 3.5X240MM SQX2 ARM | 3NOS. | NIL | NO | YES | NO | YES
2 | P4-2 | 200 | 200 | 3.5X240MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
3 | P4-3 | 250 | 250 | 3.5X240MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
4 | P4-4 | 200 | 200 | 3.5X240MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
5 | P4-5 | 200 | 200 | 3.5X240MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
6 | P4-6 | 200 | 200 | 3.5X240MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
7 | P4-7 | 400 | 400 | 3.5X240MM SQX2 ARM | 3NOS. | NIL | NO | YES | NO | YES
8 | P4-8 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
9 | P4-9 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
10 | P4-10 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
11 | P4-11 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
12 | P4-12 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
13 | P4-13 | 100 | 100 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES

## EM2
Ind No 79887 Dtd 4/3/08
|  |  |  | PDB 2-EM-F | INDICATING LAMPS
|  |  | TPN-415V AC |  |  |  | DIGITAL AMETER |  | VOLTMETER WITH VSS
S NO | DESCRIPTION | AMPS | SFU RATING | CABLE SIZE FOR | INCOM | OUTGOING | INCOMING | OUTGOING | INCOMING | OUTGOING
|  |  | AMPS | CONNECTIONS
1 | INCOMER > | 800A | ACB-1000A | 240MM SQX4 .X4 RUNS ARM | 3NOS. | 3NOS. | YES | NO | YES | YES
OUTGOINGS
1 | P7-1 | 600 | 600 | 3.5X240MM SQX3 ARM | 3NOS. | NIL | NO | YES | NO | YES
2 | P7-2 | 300 | 300 | 3.5X240MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
3 | P7-3 | 250 | 250 | 3.5X240MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
4 | P7-4 | 400 | 400 | 3.5X240MM SQX2 ARM | 3NOS. | NIL | NO | YES | NO | YES
5 | P7-5 | 100 | 100 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
6 | P7-6 | 100 | 100 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
7 | P7-7 | 100 | 100 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
8 | P7-8 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
9 | P7-9 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
10 | P7-10 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
11 | P7-11 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
12 | P7-12 | 32 | 32 | 3.5X35MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
13 | P7-13 | 250 | 250 | 3.5X240MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES

## Sheet2
|  | ANNEXURE NO. - 1A-C | ind no 79887
ITEM | DESIGNATION | DESCRIPTION | TYPE MAKE | QTY | REMARK
1 | ACB | AIR CKT. BREAKER(ACB), 1000A, 415V AC, 3 POLE, 240 VAC MOTORCONTROL, DRAWOUT WITH CRADLE SH. REL EA1-240V AC, CT'S 800A6NO+6NC AUX. CONTACTS, 24 WAY SIC SERVICE POS. MICROSWITCH, EQUIPPED WITH REL.SR21 SHUTTERASSY.,DOOR INTERLOCKING RACKING INTERLOCK KIT TYPE CN-CS 1000C | CN-CS1000C G E POWER MAKE OR EQUIVALENT OF SIEMENS OR L& T MAKE | 1 | NOT APPLICABLE IN PDB 5
2 | CT1 TO CT3 | C T 800/5 A 5 VA WITH MOUNTING BRACKETS | A.E. | 3
3 | F1 TO F6 | HRC FUSE LINKS 2 A | NS2 GE
4 |  | FUSE BASE 20 A | NSH GE
5 | MCB | MINIATURE CIRCUIT BREAKER 10 A 2 POLE 240 V AC COMBINED RELEASE | SIEMENS OR HAGER
6 | PB | PUSH BUTTON UNSHROUD ACTUATOR GREEN RED | 3SB1200-OAE01 SIEMENS
7 |  | CONTACT BLOCK 1 NO + 1 NC FOR PUSH BUTTON | 3SB1400-OA SIEMENS
8 | V | DIGITAL VOLTMETER, TYPE 3 1/2 DIGITS,OPERATING VOLT. 415V ACRESOLUTION 10V RANGE, AUX. SUPPLY 240V AC, INSCRIPTIONS RY, YB, RB ENGRAVED ON INDICATING PLATE,MODEL VSS 96D IS :1248 | VSS 96 D A.E. MAKE
9 | ACB | DIGITAL AMMETER, TYPE 4 1/2 DIGITS, OPERATING CURRENT 5A, DULY CALIBRATED FOR CTR 800/5,RESOLUTION 10A RANGE, AUX. SUPPLY 240V AC, MODEL ASS 96D IS :1248 | ASS 96 D A.E. MAKE |  | RATINGS AS PER FEEDER DETAILS
10 | R,Y, B | LED PILOT LIGHT, RED,YELLOW , BLUE VOLTAGE SUITABLE FOR 42-240V AC AND 42-220V DC.TYPE 3SB14 01-2WZ3 | 3 SB 1401-2W23 SIEMENS
11 | SFU | SWITCH DISCONNECTOR FUSE UNIT TPN, 400A, OPEN EXECUTION, (INTERIOR) WITHOUT FUSE LINKS WITH DOOR INTERLOCKING, WITH 1 NO + 1NC AUX CONTACTS TYPE FN 400 IS : 13942-3 | FN 100 L&T OR EQUIVALENT SIEMENS |  | RATING MENTIONED IS FOR 400A FEEDER ONLY . FOR OTHER FEEDERS RATING AS PER FEEDER
12 |  | HRC FUSE LINKS AMP RATING AS PER FEEDER | L&T OR EQUIVALENT SIEMENS
13 | CT1 TO CT3 | C T 100/5 A 5 VA WITH MOUNTING BRACKETS | A.E. | 3 | RATING MENTIONED IS FOR 100A FEEDER ONLY . FOR OTHER FEEDERS RATING AS PER FEEDER

## EM1
Ind No 79887 Dtd 4/3/08
|  |  |  | PDB 1-EM-F | INDICATING LAMPS
|  |  | TPN-415V AC |  |  |  | DIGITAL AMETER |  | VOLTMETER WITH VSS
S NO | DESCRIPTION | AMPS | SFU RATING | CABLE SIZE FOR | INCOM | OUTGOING | INCOMING | OUTGOING | INCOMING | OUTGOING
|  |  | AMPS | CONNECTIONS
1 | INCOMER > | 800A | ACB-1000A | 240MM SQX4 .X4 RUNS ARM | 3NOS. | 3NOS. | YES | NO | YES | YES
OUTGOINGS
1 | P6-1 | 400 | 400 | 3.5X240MM SQX2 ARM | 3NOS. | NIL | NO | YES | NO | YES
2 | P6-2 | 300 | 300 | 3.5X240MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
3 | P6-3 | 250 | 250 | 3.5X240MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
4 | P6-4 | 100 | 100 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
5 | P6-5 | 100 | 100 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
6 | P6-6 | 100 | 100 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
7 | P6-7 | 100 | 100 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
8 | P6-8 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
9 | P6-9 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
10 | P6-10 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
11 | P6-11 | 63 | 63 | 3.5X70MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
12 | P6-12 | 32 | 32 | 3.5X35MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
13 | P6-13 | 32 | 32 | 3.5X35MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES
14 | P6-14 | 250 | 250 | 3.5X240MM SQ ARM | 3NOS. | NIL | NO | YES | NO | YES