TECHNICAL AMENDMENT NO. 1

| NAME OF PROJECT | : | CAPTIVE POWER PLANT FOR PARADIP REFINERY LIMITED. |
| --- | --- | --- |
| TECHNICAL SPECIFICATION NO. | : | PE-TS-353-100-N001 (REV.0) – Technical Specification For Special Process Horizontal Pumps. |

The terms, conditions, specifications and stipulations of the Bidding Document shall stand modified to the extent indicated in Column No. 5 below and subject to these modifications; all other terms, conditions, specifications of the Technical Specification for Special Process Horizontal Pumps shall remain unaltered.

| SL. No. | TECHNICAL SPECIFICATION (TECHNICAL VOLUME -IIB) |  | SUBJECT | ADDITIONS / DELETIONS / MODIFICATION |
| --- | --- | --- | --- | --- |
|  | SECTION | CLAUSE NO. |  |  |
| 1 | 2 | 3 | 4 | 5 |
| 1. | D | Sl. No. 2.10 of Datasheet-A for Variant No. 01, 02, 03 & 04 (viz. Horizontal Pumps Group-I) | NPSHA at pump suction flange | Modification: 8.5 MLC instead of 5.659 MLC |
| 2. | D | Sl. No. 2.11 of Datasheet-A for Variant No. 01, 02, 03 & 04 (viz. Horizontal Pumps Group-I) | NPSHR shall be ltd to | Modification: 7.0 MLC instead of 4.359 MLC |
| 3. | D | Sl. No. 2.9 of Datasheet-A for Variant No. 05, 06 & 07 (viz. Horizontal Pumps Group-II) | Available Pressure on Suction side of BFP | Modification: 1 kg/cm2 (a) instead of 4.736 kg/cm2 (a) |
| 4 | D | Sl. No. 2.10 of Datasheet-A for Variant No. 05, 06 & 07 (viz. Horizontal Pumps Group-II) | NPSHA at pump suction flange | Modification: 4.5 MLC instead of 5.423 MLC |
| 5 | D | Sl. No. 2.11 of Datasheet-A for Variant No. 05, 06 & 07 (viz. Horizontal Pumps Group-II) | NPSHR shall be ltd to | Modification: 3.2 MLC instead of 4.123 MLC |