## Scope matrix
ANNEXURE-02 (rev-01) ELECTRICAL and C&I ITEMS SCOPE OF SUPPLY AND WORKS FOR COAL HANDLING PLANT AND FGD FOR 1X660 MW PANKI TPS
Sl.No. | Equipments | Design & Engineering | Supply | Receipt,Unloading/ Storage and Security | Local Transport,Erection ,Testing and Commissioning | Remarks
1 | 11 KV and 3.3 KV HT switchboard | BHEL | BHEL | BHEL | BHEL | Vendor shall furnish HT load list with type of feeder,rating and power requirement. For SCR Machine transformer, BHEL shall arrange 11/3.3 KV HT supply up to the land mounted JB/LOAD BREAK SWITCH (supplied by Vendor) , further power distribution is in the scope of Vendor.
2 | 3.3KV HT Busduct | BHEL | BHEL | BHEL | BHEL
3 | 3.3 KV HT Motors. | BHEL | BHEL | Vendor | Vendor | HT Motor input details (like, sizing calculations along with the interface details like GD² values, T-S Curves, Speed, Coupling type,mounting arrangements Starting method etc.) shall be furnished by the Vendor. Temperature Transmitters mounted in JBs shall be considered for Winding and Bearing temperature measurement of HT Motors (including BHEL supplied Motors) & Crushers and the same shall be in the scope of bidder.
4 | 11/0.433 KV Dry Type Transformers except for SCR Machine | BHEL | BHEL | BHEL | BHEL | Vendor shall furnish LT load list with type of feeder,rating, duty and Power requirement.
5 | 11/0.433 KV or 3.3/0.433 KV Dry Type Transformers for SCR Machine | Vendor | Vendor | Vendor | Vendor
6 | LT Swtichgear except for SCR Machine | BHEL | BHEL | BHEL | BHEL
7 | LT Swtichgear for SCR Machine | Vendor | Vendor | Vendor | Vendor
8 | LT bus ducts | BHEL | BHEL | BHEL | BHEL | Connection from SCR Machine Transformer to SCR MCC is in Vendor's scope .
9 | LT Motors | Vendor | Vendor | Vendor | Vendor | LT Motor sizing calculations along with the type of feeder requirement shall be furnished by the Vendor. Motor shall be suitable for power cable terminations as per cable schedule, Power JB shall be provided by Vendor if required.
10 | Variable Frequency Drive Panels | Vendor | Vendor | Vendor | Vendor | VFD Panels as required for this Package is in scope of Vendor. VFD panels for Apron feeder shall be kept in the WT-Control room.
11 | HT Power Cables | BHEL/Vendor | BHEL | BHEL | BHEL/Vendor | For SCR Machine: 11/3.3 KV HT and C& I cabling up to the land mounted JB/LOAD BREAK SWITCH (supplied by Vendor) is in the scope of BHEL , further HT/LT/C&I Cabling is in the scope of Vendor. All the hardwired signals required for interfacing between SCR machine and DCS shall be wired upto the land mounted Control JB. For WT Machine, SAC, Wagon Shifter and Pusher etc : a) HT/LT/C&I Cabling and Termination between Vendor supplied equipments is in the scope of Vendor. b) HT/LT/C&I cabling from BHEL supplied MCC to Vendor supplied PLC/ drives/equipments is in the scope of Vendor. c) All the interfacing signals required between WT PLC and DCS is in the scope of Vendor. For Balance Area : a) HT/LT/C&I Cabling and Termination between Vendor supplied equipments is in the scope of Vendor. b) HT/LT/C&I Cabling and Termination between MCC/DCS and Vendor supplied equipments is in the scope of BHEL. Vendor shall provide Cable sizing calculations,cable schedule and cable Termination charts (for Vendor scope of cables) for customer approval. BHEL will supply the cable based on the BOQ of Cables furnished by Vendor.
12 | LT Power Cables | BHEL/Vendor | BHEL | BHEL | BHEL/Vendor
13 | Control and Instrumentation Cables | BHEL/Vendor | BHEL | BHEL | BHEL/Vendor
14 | Flexible/Trailing/Festoon/Composite/Co-axial Cables/Un-armoured or any other special cable required for this package including fixing arragement such as festooning, Cable reeling drum and bus bar etc and Termination arrangement including Junction Box etc. | Vendor | Vendor | Vendor | Vendor
15 | All Data cables such as Profibus ,Modbus,Ethernet cable, OFC etc. and Special cables(other than standard screen cables ) ie., cables from sensor to controllers, indicators etc. OR Encoder cables OR HART instrument cables etc., as required . | Vendor | Vendor | Vendor | Vendor | OFC Cables for BHEL supplied DCS and for soft connectivity between BHEL DCS & WT machine PLC is in the scope of BHEL.
16 | Cable trays & supports | BHEL/Vendor | BHEL | BHEL | BHEL/Vendor | For SCR Machine: Cable tray erection and layout preparation for SCR Machine including Trailing cable is in the scope of Vendor. For WT Machine, SAC, Wagon Shifter and Pusher etc : Cable tray erection and layout preparation (including BHEL scope of cabling) of WT Complex,SAC area and Wagaon shifter/pusher area,WT Control room etc. is in the scope of Vendor. For Balance Area : a) Cable tray erection and layout preparation between Control & Power JB/Local Control Panels/PDB etc. and Drives/ Field Instruments etc. is in the scope of Vendor. b) Cable tray erection and layout preparation on moving machine like Travelling Tripper is in the scope of Vendor. c) Cable Tray erection and layout preparation between Switchgear/MCC building to Control & Power JB/Local Control Panels/WT starting point etc. shall be in the scope of BHEL. Vendor shall provide BOQ of Cable tray and Supports.BHEL will supply the Cable trays and Supports based on BOQ furnished by Vendor.
17 | Cabling accessories(Termination kits, Cable Glands , Lugs,Tags and conduits etc.) | BHEL | BHEL | BHEL | BHEL | For Cabling works included in the scope of BHEL.
18 | Cabling accessories(Termination kits, Cable Glands , Lugs,Tags and conduits etc.) | Vendor | Vendor | Vendor | Vendor | For Cabling works included in the scope of bidder.
19 | Earthing and Lightnining protection materials | BHEL/Vendor | BHEL | BHEL | BHEL/Vendor | For SCR Machine: Earthing (Electrical & Electronic) & Lightning material erection and layout preparation for SCR Machine including Trailing cable is in the scope of Vendor. Rail earthing & its connection to nearby BHEL earth-grid/ riser for SCR machine/Shifter/Pusher is in the scope of Vendor. For WT Machine, SAC, Wagon Shifter and Pusher etc : Earthing (Electrical & Electronic) and Lightining material erection and layout preparation of WT Complex,SAC area and Wagaon shifter/pusher area,WT Control room etc. is in the scope of Vendor. For Balance Area : a) Earthing (Electrical & Electronic) material erection and layout preparation between BHEL earth Pit/Mat/Submat/riser etc and Vendor erected Equipment’s/LCP’s/Motors/Field Instruments/ Tray/Conduit is in the scope of Vendor. Vendor shall provide BOQ of earthing and Lightning materials..BHEL will supply the earthing and Lightning materials based on BOQ furnished by Vendor.
20 | Local Push Button Stations and De-interlock switches. (including for BHEL free issue Motors) | Vendor | Vendor | Vendor | Vendor | LPBS Schedule area wise to be submitted by Vendor. Number of NO+NC Contacts shall be considered as per Drive/equipment Control circuit requirement.
21 | Power Junction Box and Control Junction Boxes | Vendor | Vendor | Vendor | Vendor | Motor/Equipments/Panels (LCP, DB's, VFD panels,Starter panels etc) shall be suitable for Power cable terminations as per cable schedule, PJB shall be provided by Vendor if required. Cable between PJB and Motor/Equipments/Panels is in the scope of Vendor.
22 | Land Mounted Power JB/LOAD BREAK SWITCH panel and Control JB for SCR Machine | Vendor | Vendor | Vendor | Vendor
23 | UPS with Batteries, ACDB for BHEL supplied DCS/RIO panels | BHEL | BHEL | BHEL | BHEL
24 | UPS with Batteries , ACDB for Vendor supplied equipment | Vendor | Vendor | Vendor | Vendor | 2 KVA additional load shall be considered in WT-UPS design for BHEL use.Number of outgoing feeders( Working+Standby) for BHEL load shall be informed during DDE. Cabling between BHEL loads and UPS DB is in the scope of BHEL.
25 | 220V DC Battery & Battery charger with DCDB | BHEL | BHEL | BHEL | BHEL
26 | 24V DC Battery & Battery charger with DCDB for BHEL supplied DCS/RIO panels | BHEL | BHEL | BHEL | BHEL
27 | 24V DC Battery & Battery charger with DCDB for Vendor supplied equipment | Vendor | Vendor | Vendor | Vendor
28 | ACDB / DCDB / PDB for this package | Vendor | Vendor | Vendor | Vendor | Vendor shall furnish the Area/JNT/building wise Load list/DB List with power requirement and total power required for considering feeders in MCC.
29 | Vibration monitoring system for HT Motors & Crushers | BHEL | BHEL | BHEL | BHEL | Notch, provision for mounting key phasor and mounting pads for mounting of vibration Detectors on HT Motors/Crushers/Pumps/Compressors/Coupling/Shaft etc. shall be provided by the Vendor for Vibration Monitoring and Analysis System (VMAS supplied by BHEL). The exact provision required on Vendor’s equipment will be provided by BHEL during detailed engineering to successful Vendor and Vendor shall comply with the same. Vendor shall take care of the same in the Vendor submitted drawings as well.
30 | Local Control Panels, Local Power cum Control Panels and Integral Starter Panels as required for this package. | Vendor | Vendor | Vendor | Vendor | 1. Complete scope of Local Control Panels required for this package is in scope of Vendor. 2. The drawings of these Panels shall be approved by customer/consultant in line with the contract specifications. 3. BHEL will only provide 3 Ph, 415V AC power supply for these control panels, further distribution (including providing control transformer for 230V AC, 110V AC/DC,24V AC/DC etc. is in the scope of Vendor. The Load requirement for these panels shall be furnished by the Vendor during DDE for allocating power supply feeders in the MCC. 4. Interposing relays required for remote operation(Strat/Stop etc.) shall be considered in Control Panels.
31 | Hydraulics/power packs required for this package inlcuding associated electrics. | Vendor | Vendor | Vendor | Vendor
32 | Hooters / Sirens as required for this package | Vendor | Vendor | Vendor | Vendor | Hooters Schedule area wise to be submitted by Vendor
33 | Pull chord Switches / Belt-Sway Switches / Zero- Speed Switches/Chute Block Switches/Heavy Duty Limit Switches / Torque Limit Switches/Over Speed/Switches/Instruments/Guages/Transmitters/Sensors/Solenoid Valves/Control Valves/Actuators/Thermo Couples/Proximity Limit Switches etc. and any other required not limited to above shall be considered for Safe & reliable Operation and Monitoring of the system . Redundancy of instruments/field devices shall be provided as per C&I specifications. | Vendor | Vendor | Vendor | Vendor | Safety switch schedule/Instrument schedule to be submitted by the Vendor. Brackets/Structural Steel for mounting field equipments/Instruments is in the scope of Vendor. Zero Speed Switches shall be supplied with Belt Speed Indication.
34 | DCS system ( including CSU and LSU) | BHEL | BHEL | BHEL | BHEL | Control Philosophy,Control logic diagrams, HMI Screens,Drive list, IO List(including interfacing signal list with other packages/ Machines),P&I drawing,Instruments list/schedule, etc including KKS tags for this package is in the scope of Vendor.
35 | PLC with Redundant hot standby processor based control system with Two ( 2) nos. OWS and one (1) no. Operating cum engineering work station (OWES) and Local control Desk backed up by push button, switches, joy sticks etc & Annunciation windows along with A4 sized colored LJP etc., for Stacker reclaimer and Redundant wireless link or industrial grade redundant soft link between CHP DDCMIS & Stacker reclaimer PLC. | Vendor | Vendor | Vendor | Vendor | All the hardwired signals required for interfacing between SCR machine and DCS shall be wired upto the land mounted Control JB.
36 | PLC with Redundant hot standby processor based wagon tippler system with One (1) no. OWS, One (1) no. OWES & A4 sized Color laser printer and Local control pane/Desk backed up by push button, switches, HW annunciation etc. for Wagon Tippler and Side Arm Charger (SAC). Operator shall be able to control & operate the wagon tippler and Side Arm Charger (SAC) from control desk as well as from OWS. PLC shall be connected to main CHP DDCMIS via redundant soft link for monitoring and Hard wired interfacing for time critical, interlock, control & protection signals. | Vendor | Vendor | Vendor | Vendor | All the interfacing signals required between WT PLC and DCS shall be wired by the Vendor.
37 | Micro processor based weigh bridge system with One (1) no. OWES & A3 sized DMP. Microprocessor shall be connected to main CHP DDCMIS via redundant soft link for monitoring and Hard wired interfacing for time critical, interlock, control & protection signals. | Vendor | Vendor | Vendor | Vendor
38 | Illumination system. | BHEL | BHEL | BHEL | BHEL | Any Machine/Equipment mounted Illumination system is in the scope of Vendor.
39 | Illumination system on Stacker and Reclaimer Machines | Vendor | Vendor | Vendor | Vendor | Total illumination for SCR Machines including the supply of Light fittings, Conduits, Lighting wires, Lighting panels, JB's, switchboxes ect.. Is in the scope of Vendor. However, Coal Stockyard lighting and High Masts shall be by BHEL.
40 | WDB / Receptacles except for SCR Machine | BHEL | BHEL | BHEL | BHEL
41 | ACDB / DCDB / PDB / WDB /Receptacles/Telephone/Fire extinguishers/Public addersing system (PA) /loudhailer etc. for SCR Machine | Vendor | Vendor | Vendor | Vendor
42 | Hoists and Cranes etc. | Vendor | Vendor | Vendor | Vendor | Complete scope of Electrical and C&I portion is in scope of Vendor. Total Hoists and Cranes shall be supplied in line with the Customer Contract specification. BHEL will provide only 415V AC,3Ph supply up to wall mounted Isolator (supply and erection of Isolator is in the scope of Vendor) , further distribution including busbar/Trailing/Festoon Cables , isolators, supporting structure etc. is in Vendor's scope. Hoist & Crane Schedule area wise to be submitted by Vendor. If multiple Hoist & Cranes are there in one location (JNT/Building etc.) Power Distribution Board(PDB) for the same shall be considered.
43 | Air Conditioning System for this package (Control rooms, DCS/RIO/PLC rooms,Cabins, Office room, Dozer room and E-house in Stacker Reclaimer etc. and any other area in line with the Customer Contract specification) with associated electrics. | Vendor | Vendor | Vendor | Vendor | Supply, erection and commissioning of Air conditioning Control Panel / Power distribution board (Two incomers with auto changepover) is in the scope of vendor. For supply and E&C of Cables , please refer Sl.no 12 to 15.
44 | Ventilation System for this package (MCC rooms,Battrey rooms, Pump Houses,Tunnels, WT- Complex, ERH,Toilets,Compressor House,Office room, Bulldozer shed,limestone shed etc.and any other area in line with the Customer Contract specification) with associated electrics.. | Vendor | Vendor | Vendor | Vendor | Supply, erection and commissioning of Ventilation Control Panel / Starter Control panel is in the scope of vendor. For supply and E&C of Cables , please refer Sl.no 12 to 15.
45 | DE- System for this package (Crusher Houses, Bunckers, TP's, Gypsum shed ,Storage and Day Silo's etc.and any other area in line with the Customer Contract specification) with associated electrics.. | Vendor | Vendor | Vendor | Vendor | Supply, erection and commissioning of DE system Control Panel / Starter Control panel is in the scope of vendor. For supply and E&C of Cables , please refer Sl.no 12 to 15.
46 | Dry Fog Dust Suppression System,Plain Water Dust Suppression System,Dust Suppression System for this package with associated electrics.. | Vendor | Vendor | Vendor | Vendor | Supply, erection and commissioning of DFDS/PWDS/DS system Control Panel / Starter Control panel/MB is in the scope of vendor. For supply and E&C of Cables , please refer Sl.no 12 to 15.
47 | 3-D stockpile volume/ Qty measurement system (Accoustic type) including all the required instruments,sensors ,Work stations,Hardware, software and furniture etc.. | Vendor | Vendor | Vendor | Vendor | Incase Accoustic type system is not proven for open coal Stock yard , Laser type system shall be considered by Vendor.
48 | Structural steel for the E&C of Vendor supplied Equipments/items | Vendor | Vendor | Vendor | Vendor
49 | All Spares related to Vendor supplied equipment | Vendor | Vendor | Vendor | Vendor | All the applicable spares as per the Customer NIT specs (Volume-II ,General & Schedules, Ch 9 : Mandatory Spares sheet 1 to 109) shall be supplied by Vendor after approval of Spares List from end user.
50 | Maintenance Tools and Tackles as applicable | Vendor | Vendor | Vendor | Vendor
Notes:
1 | Vendor shall supply all the Electrical and C&I items (including spares) as per attached Customer NIT/Contract Specification (including amendments, clarifications and MOM etc..)
2 | Makes of all Electrical and C&I Items/equipment shall be from the Customer/Customer Consultant's approved Vendors only.Bidder must follow the Customer approved vendor list attached in Annexure-2A. Further for any equipment, if makes are not specified in the approved vendor list, then Bidder must obtain the prior approval from Customer/Customer Consultant for that sub-Vendors during detailed Engineering.
3 | The Electrical and C&I items inspection category list shall be given to successful Vendor during detailed engineering.
4 | Construction Power of 415V, 3-phase, 4 wire (on chargeable basis) shall be provided at one point from the Distribution Transformer/Distribution Board. Further distribution (including Tariff Meter installation) from the Distribution Transformer/Distribution Board shall be carried out by Vendor as per requirement.
5 | Any Statutory Clerance required for Vendor Supplied/E&C equipments such as HT Motors and Hoist/Crane etc. shall be in the scope of Vendor.
6 | Beltwatch Panel shall be provided with Potential free contacts, Analog signals(4-20mA Live) and Soft communication Link with DCS.
7 | Control Philosophy,Control logic diagrams along with HMI Screens(MIMIC's), Drive list, IO List(including interfacing signal list ), P&I drawing,Instruments list/schedule,Interconnection Cable termination Chart (ICS), Hookup drawings,etc including KKS tags for this package is in the scope of Vendor. Vendor shall visit BHEL EDN/Site/Customer place to provide support for Control logics and HMI screens and shall also attend the inspection (if required) along with the customer.
8 | DFDS/DE/Ventilation system Compressor Motors Shall be considered in LV system range (i.e upto 200 KW) only.
9 | All Compressor Local control panels (Microprocessed based, inbulit skid type) shall have provision for communication with CHP DCS over soft link.
10 | Temperature Transmitters mounted in JBs shall be considered for Winding and Bearing temperature measurement of HT Motors (including BHEL supplied Motors) & Crushers and the same shall be in the scope of Vendor.
11 | Training of Customer and BHEL personnel for operation and maintenance of Vendor supplied equipment is included in the Vendor’s scope.
12 | Civil assignment drawing for Cable Trench/Trestle/Duct/Slit, Conduits,Foundations, Pull Pits, Cut-outs/Openings and Insert Plates etc. for this package is in the scope of Vendor.
13 | Final documentation as per Contract shall be in the Vendor’s scope.
14 | Preferably uniform make shall be considered for similar type of Electrical and C&I equipment’s/items.
15 | Any other Electrical and C&I item (Hardware or Software ) not covered above but required for completion of this package as per Customer NIT specs is in the scope of Vendor.
16 | In case of any conflict & ambiguity, decision of BHEL/customer shall be final and binding.
17 | Vendor shall sign and seal the scope matirx.
18 | O and M manuals shall be provided by Vendor for supplied equipments/items .
19 | 3 D model drawings for this package is in the scope of Vendor .