## BOM- APL Raipur 2x800 MW
Enquiry No 4202500017 dt 25.09.2025 Procurement of Low Pressure (LP) Piping for various Adani projects Annexure C- Detailed Piping System BOM (R01)
Schedule No | Project | Piping System | IBR / Non IBR | PGMA | Item Description | Specification | Drawing No | UOM | Assembly Indicator | Quantity | Weight (kg)
1 | APL Raipur 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 33.4X4.55 EP AT SITE D1-25.2 | SA106GRB | 2-80-453-A0365 | M |  | 730 | 2365.2
1 | APL Raipur 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRB | 2-80-453-A0365 | M |  | 30 | 224.4
1 | APL Raipur 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRC | 2-80-453-A0365 | M |  | 300 | 2244
1 | APL Raipur 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 21.3X3.73 EP AT SITE D1-14.5 | SA106GRB | 2-80-453-A0365 | M |  | 100 | 162
1 | APL Raipur 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 100 | 38
1 | APL Raipur 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 35 | 31.5
1 | APL Raipur 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 34 | 10.2
1 | APL Raipur 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 16 | 4.8
1 | APL Raipur 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | SW END CAP NB50 CL3000 SA105 | SA105 | 2-80-453-A0365 | NO |  | 4 | 1
1 | APL Raipur 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 33.4X4.55 EP AT SITE D1-25.2 | SA106GRB | 2-80-453-A0365 | M |  | 730 | 2365.2
1 | APL Raipur 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRB | 2-80-453-A0365 | M |  | 30 | 224.4
1 | APL Raipur 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRC | 2-80-453-A0365 | M |  | 300 | 2244
1 | APL Raipur 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 21.3X3.73 EP AT SITE D1-14.5 | SA106GRB | 2-80-453-A0365 | M |  | 100 | 162
1 | APL Raipur 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 100 | 38
1 | APL Raipur 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 35 | 31.5
1 | APL Raipur 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 34 | 10.2
1 | APL Raipur 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 16 | 4.8
1 | APL Raipur 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | SW END CAP NB50 CL3000 SA105 | SA105 | 2-80-453-A0365 | NO |  | 4 | 1
1 Total | [10 empty] | 10162.2
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (CS) | As per drawing | 3-80-418-38038 | NO | A | 130
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW | SA105 | 4-80-418-85267 | NO |  | 130 | 31.2
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA105 | 4-80-418-85269 | NO |  | 130 | 46.8
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA105 | 4-80-418-85270 | NO |  | 130 | 22.88
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TUBE 21.30 X 3.73 - SA106GRB | SA106GRB |  | M |  | 280 | 453.6
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | COND. LOOP (CS) | As per drawing | 3-80-999-99256 | NO | A | 10
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | LOOP CS OD21.3X4.78 L=700 | SA106GRC | 3-80-999-99256 | NO |  | 10 | 13.7
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA105 | 4-80-418-A0470 | NO |  | 130 | 26.52
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2" (PLAINXEXTTHRD)L=100MM | SA312TP316L | 4-80-418-A0517 | NO |  | 5 | 0.81
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 6 | 9.72
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | NO |  | 10 | 3.24
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2"-1/2"PLAIN X 1/2"NPT(M) | SA106GRB | 4-80-418-A0471 | NO |  | 10 | 1.62
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 10 | 2.56
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA182F316 | 4-80-418-A0518 | NO |  | 5 | 1.48
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (SS) | As per drawing | 3-80-418-A0856 | NO | A | 3
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2" NB-SW CL3000 | SA182F316 | 4-80-418-A0519 | NO |  | 3 | 0.888
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA182F316 | 4-80-418-A0520 | NO |  | 3 | 1.332
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA182F316 | 4-80-418-A0521 | NO |  | 3 | 0.651
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-50.4 | SA106GRB |  | M |  | 150 | 1122
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 27
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD33.4X4.55 EP STY D D1-25.2 AT SIT | SA106GRB |  | M |  | 165 | 534.6
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 30 | 5.7
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 60 | 22.8
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 5 | 8.25
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 10 | 4.3
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 1 | 1.4
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-49.0 | SA106GRB |  | M |  | 60 | 448.8
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 33.4 X 4.55 - SA106GRB | SA106GRB |  | M |  | 420 | 1360.8
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 21.3 X 3.73 - SA106GRB | SA106GRB |  | M |  | 240 | 388.8
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 25 | 22.5
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 120 | 45.6
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 35 | 10.5
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB50 CL3000 | SA105 |  | NO |  | 6 | 6
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 |  | NO |  | 45 | 13.5
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB50/25 CL3000 | SA105 |  | NO |  | 16 | 36
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 70 | 21
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 1/4"NPT/NB15 | SA105 |  | NO |  | 85 | 29.325
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 3/8"NPT/NB15 | SA105 |  | NO |  | 85 | 59.5
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 50 CL150 | SA515GR70 |  | NO |  | 2 | 4
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 25 CL150 | SA515GR70 |  | NO |  | 2 | 1.8
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT HEX GRA 8.8 M16X80 | IS:1364 (P-1) |  | NO |  | 4 | 0.62
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | HEX NUT M16 | IS:1364 (P-3) |  | NO |  | 4 | 0.12
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT-M12X70 -4.6-IS1364P1 | IS:1363 (P-1) |  | NO |  | 4 | 0.308
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NUT -M12 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 8 | 0.16
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD33.4X4.55 | SA515GR70 |  | NO |  | 30 | 4.14
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD60.3X5.54 | SA515GR70 | 3-80-709-99011 | NO |  | 2 | 0.8
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD114.3 X 6.02 SA106GRB | SA106GRB |  | M |  | 8 | 128.56
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 | SA234WPB |  | NO |  | 2 | 7.68
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 1 | 4.93
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE FOROD114.3X6.02 | SA515GR70 |  | NO |  | 1 | 2.19
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/40 CL3000 | SA105 |  | NO |  | 5 | 5
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/25 CL3000 | SA105 |  | NO |  | 8 | 8
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SW STUB NB15 CL 3000 | SA479TY304 |  | NO |  | 10 | 1.8
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (CS) | As per drawing | 3-80-418-38038 | NO | A | 25
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW | SA105 | 4-80-418-85267 | NO |  | 25 | 6
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA105 | 4-80-418-85269 | NO |  | 25 | 9
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA105 | 4-80-418-85270 | NO |  | 25 | 4.4
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TUBE 21.30 X 3.73 - SA106GRB | SA106GRB |  | M |  | 50 | 81
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | COND. LOOP (CS) | As per drawing | 3-80-999-99256 | NO | A | 25
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | LOOP CS OD21.3X4.78 L=700 | SA106GRC | 3-80-999-99256 | NO |  | 25 | 34.25
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA105 | 4-80-418-A0470 | NO |  | 25 | 5.1
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2" (PLAINXEXTTHRD)L=100MM | SA312TP316L | 4-80-418-A0517 | NO |  | 25 | 4.05
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 50 | 81
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | NO |  | 25 | 8.1
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2"-1/2"PLAIN X 1/2"NPT(M) | SA106GRB | 4-80-418-A0471 | NO |  | 25 | 4.05
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 25 | 4.9
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA182F316 | 4-80-418-A0518 | NO |  | 25 | 5.1
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (SS) | As per drawing | 3-80-418-A0856 | NO | A | 25
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2" NB-SW CL3000 | SA182F316 | 4-80-418-A0519 | NO |  | 25 | 7.4
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA182F316 | 4-80-418-A0520 | NO |  | 25 | 11.1
2 | APL Raipur 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA182F316 | 4-80-418-A0521 | NO |  | 25 | 5.425
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (CS) | As per drawing | 3-80-418-38038 | NO | A | 130
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW | SA105 | 4-80-418-85267 | NO |  | 130 | 31.2
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA105 | 4-80-418-85269 | NO |  | 130 | 46.8
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA105 | 4-80-418-85270 | NO |  | 130 | 22.88
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TUBE 21.30 X 3.73 - SA106GRB | SA106GRB |  | M |  | 280 | 453.6
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | COND. LOOP (CS) | As per drawing | 3-80-999-99256 | NO | A | 10
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | LOOP CS OD21.3X4.78 L=700 | SA106GRC | 3-80-999-99256 | NO |  | 10 | 13.7
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA105 | 4-80-418-A0470 | NO |  | 130 | 26.52
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2" (PLAINXEXTTHRD)L=100MM | SA312TP316L | 4-80-418-A0517 | NO |  | 5 | 0.81
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 6 | 9.72
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | NO |  | 10 | 3.24
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2"-1/2"PLAIN X 1/2"NPT(M) | SA106GRB | 4-80-418-A0471 | NO |  | 10 | 1.62
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 10 | 2.56
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA182F316 | 4-80-418-A0518 | NO |  | 5 | 1.48
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (SS) | As per drawing | 3-80-418-A0856 | NO | A | 3
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2" NB-SW CL3000 | SA182F316 | 4-80-418-A0519 | NO |  | 3 | 0.888
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA182F316 | 4-80-418-A0520 | NO |  | 3 | 1.332
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA182F316 | 4-80-418-A0521 | NO |  | 3 | 0.651
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-50.4 | SA106GRB |  | M |  | 150 | 1122
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 27
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD33.4X4.55 EP STY D D1-25.2 AT SIT | SA106GRB |  | M |  | 165 | 534.6
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 30 | 5.7
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 60 | 22.8
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 5 | 8.25
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 10 | 4.3
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 1 | 1.4
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-49.0 | SA106GRB |  | M |  | 60 | 448.8
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 33.4 X 4.55 - SA106GRB | SA106GRB |  | M |  | 420 | 1360.8
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 21.3 X 3.73 - SA106GRB | SA106GRB |  | M |  | 240 | 388.8
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 25 | 22.5
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 120 | 45.6
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 35 | 10.5
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB50 CL3000 | SA105 |  | NO |  | 6 | 6
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 |  | NO |  | 45 | 13.5
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB50/25 CL3000 | SA105 |  | NO |  | 16 | 36
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 70 | 21
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 1/4"NPT/NB15 | SA105 |  | NO |  | 85 | 29.325
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 3/8"NPT/NB15 | SA105 |  | NO |  | 85 | 59.5
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 50 CL150 | SA515GR70 |  | NO |  | 2 | 4
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 25 CL150 | SA515GR70 |  | NO |  | 2 | 1.8
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT HEX GRA 8.8 M16X80 | IS:1364 (P-1) |  | NO |  | 4 | 0.62
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | HEX NUT M16 | IS:1364 (P-3) |  | NO |  | 4 | 0.12
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT-M12X70 -4.6-IS1364P1 | IS:1363 (P-1) |  | NO |  | 4 | 0.308
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NUT -M12 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 8 | 0.16
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD33.4X4.55 | SA515GR70 |  | NO |  | 30 | 4.14
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD60.3X5.54 | SA515GR70 | 3-80-709-99011 | NO |  | 2 | 0.8
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD114.3 X 6.02 SA106GRB | SA106GRB |  | M |  | 8 | 128.56
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 | SA234WPB |  | NO |  | 2 | 7.68
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 1 | 4.93
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE FOROD114.3X6.02 | SA515GR70 |  | NO |  | 1 | 2.19
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/40 CL3000 | SA105 |  | NO |  | 5 | 5
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/25 CL3000 | SA105 |  | NO |  | 8 | 8
2 | APL Raipur 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SW STUB NB15 CL 3000 | SA479TY304 |  | NO |  | 10 | 1.8
2 Total | [10 empty] | 10207.843
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3762 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 32.357
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1733 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.906
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3644 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 31.342
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3079 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 26.482
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4807 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 41.345
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1662 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.295
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2728 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 23.464
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3978 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.215
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2539 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 21.838
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5201 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 44.734
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=298 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.563
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=326 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.804
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=104 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 0.895
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3339 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 28.719
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1739 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.957
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4942 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 42.506
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=892 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 7.672
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=171 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.471
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=562 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.834
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=699 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.012
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=782 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.726
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=780 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 5.178
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=268 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.779
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=3368 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 22.357
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=464 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.08
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=582 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.863
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=5178 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.372
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=673 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.467
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=151 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.002
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=1319 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 8.756
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 3 | 1.29
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 17 | 34
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 45DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 5 | 5.8
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BW EQUAL TEE OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 5.88
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.9BW UNEQT 114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 2.8
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1.75
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 1.54
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 0.56
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=3000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 25.803
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD88.9X3.05L=1000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.638
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X3.05L=2000 | SA312TP304H | 1-80-412-A0533 | NO |  | 1 | 12.92
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | BOTTOM PLATE 10THKX 1500X1500 | SA515GR70 | 1-80-412-A0533 | NO |  | 1 | 176.625
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1977 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 17.004
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD60.3X5.54 L=4000 | SA106GRB | 1-80-412-A0533 | NO |  | 1 | 29.924
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=264 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.271
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2672 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 22.982
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=360 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 3.096
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=242 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.081
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 50.66
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH CARRIER PLATES | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4382 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 37.69
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3039 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 26.138
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=192 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 1.651
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2938 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 25.27
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5544 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 47.684
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1001 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 8.61
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1583 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 13.615
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 8 | 16
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X5.49 L=2500 | SA106GRB | 2-80-412-A0362 | NO |  | 1 | 28.23
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 10MMX500X50010 | SA240TP304L | 2-80-412-A0362 | NO |  | 1 | 40.35
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=2000 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 17.202
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD168.3X3.4/114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 1 | 1.59
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 12MMX150X300 | SA515GR70 | 2-80-412-A0362 | NO |  | 1 | 4.239
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 230 | 591.56
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 50 | 8
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | BW UEQT 60.3X3.91/33.4X3.38 SA403WP316L | SA403WP316L |  | NO |  | 6 | 6.12
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25 SS | SA479TY304 |  | NO |  | 10 | 4.3
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | MULTI HOLE ORIFICE PLATE ASY(NB80)-OP43 | As per drawing | 3-80-412-A0952 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05 L=150MM | SA312TP316L | 3-80-412-A0952 | NO |  | 1 | 0.969
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE T=10THK, Ø84. 6 | SA240TP304 | 3-80-412-A0952 | NO |  | 1 | 0.37
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ORIFICE PLT NB80 (OP44) | As per drawing | 3-80-412-A0954 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05 L=150MM | SA312TP316L | 3-80-412-A0954 | NO |  | 1 | 0.969
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE T=10THK, Ø84.62 | SA240TP304 | 3-80-412-A0954 | NO |  | 1 | 0.37
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ORIFICE PLT NB100 (OP54)) | As per drawing | 3-80-412-A0955 | NO | A | 2
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 L=200MM SA312TP316L | SA312TP316L | 3-80-412-A0955 | NO |  | 2 | 3.44
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE T=12THK, Ø110.20 | SA240TP304 | 3-80-412-A0955 | NO |  | 2 | 1.39
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD60.3X5.54 EP STY D D1-50.4AT SITE | SA106GRB |  | M |  | 25 | 187
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 8 | 7.2
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-60.3X3.91 EP STY D D1-53.2AT SITE | SA312TP316L |  | M |  | 130 | 726.57
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 18 | 11.7
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 180 | 462.96
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 21 | 3.36
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | SW RED NB50/25 CL3000 SA182F316 | SA182F316 | 4-80-452-85266 | NO |  | 2 | 7.2
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L |  | NO |  | 2 | 3.5
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 60.3 X 3.91 EP STY D D1-53.2 | SA312TP304H |  | M |  | 50 | 272
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP304H |  | NO |  | 10 | 6.5
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 5 | 2.5
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 50 | 125
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD60.3X3.91/33.4X3.38 | SA403WP304L |  | NO |  | 5 | 5.1
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 65 | 923.845
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 14 | 69.58
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD168.3 X3.4 | SA403WP316L |  | NO |  | 2 | 13
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD168.3X3.4/88.9X3.05 | SA403WP316L |  | NO |  | 2 | 11.48
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 1 | 1.43
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 88.90 X 3.05 - SA312TP316L | SA312TP316L |  | M |  | 4 | 26.552
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L |  | NO |  | 2 | 2.32
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 RED OD168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 2 | 3.18
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | SOW FLANGE NB150 CL150 (RF) (SS316L) | SA182F316L |  | NO |  | 4 | 28
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 20 | 6.06
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | NUT -M20 -2H | BPS 41319 |  | NO |  | 40 | 2.6
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 75 | 1065.975
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 6 | 29.82
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 4 | 23.64
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 36 | 309.636
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 14 | 28
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD168.3X3.4/88.9X3.05 | SA403WP316L |  | NO |  | 1 | 5.74
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 1 | 1.43
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 88.90 X 3.05 - SA312TP316L | SA312TP316L |  | M |  | 4 | 26.552
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L |  | NO |  | 2 | 2.32
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 88.90 X 3.05 - SA312TP316L | SA312TP316L |  | M |  | 45 | 298.71
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L |  | NO |  | 10 | 11.6
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD88.9X3.05 | SA403WP316L |  | NO |  | 2 | 3.76
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD273.1 X 4.19 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 26 | 742.352
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD273.1X4.19 | SA403WP316L |  | NO |  | 2 | 33.26
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW EQT OD273.0X4.19 SA403WP316L | SA403WP316L |  | NO |  | 2 | 37.2
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW UEQT 273X4.19/219.1X3.76 SA403WP316L | SA403WP316L |  | NO |  | 2 | 36.328
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE D219.1 X 3.76 X6000 - SA312TP316L | SA312TP316L |  | M |  | 14 | 287.35
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X3.76 | SA403WP316L |  | NO |  | 2 | 19.14
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ECC RED219.1X3.76/168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 2 | 5.6
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 27 | 383.751
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 6 | 29.82
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 273.1X4.19/168.3X3.4 | SA403WP316L |  | NO |  | 4 | 69.76
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 ECCRED OD168.3X3.4/141.3X3.4 | SA403WP316L |  | NO |  | 4 | 7.16
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD141.3X3.4 L=6000 SA312TP316L | SA312TP316L |  | M |  | 6 | 69.222
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | 90 DEG LR ELBOW OD 141.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 4 | 15.2
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD273X4.19 SA403WP316L | SA403WP316L |  | NO |  | 2 | 8.12
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW SR 90DEG ELL OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 2 | 2
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 284.26
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 4 | 19.88
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 172.02
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 4 | 8
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L |  | NO |  | 50 | 21.5
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | SW STUB NB15 SS | SA182F316 | 4-80-473-A0623 | NO |  | 30 | 5.4
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 33.4 X 4.55SA312TP316L | SA312TP316L |  | M |  | 45 | 145.8
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 5 | 8.1
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA403WP316L |  | NO |  | 28 | 5.32
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 60.3 X 3.91 SA312TP316L | SA312TP316L |  | M |  | 20 | 111.78
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | SW STUB NB 50 SS CL:3000-SA182F316 | SA182F316 |  | NO |  | 5 | 4.6
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X6000 - SA312TP316L | SA312TP316L |  | M |  | 270 | 3837.51
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 12 | 59.64
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD168.3 X3.4 | SA403WP316L |  | NO |  | 2 | 13
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 2 | 11.82
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 172.02
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 6 | 12
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD 273.00 X 6.35 X 6000 - SA106GRB | SA106GRB |  | M |  | 270 | 11275.2
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 14 | 366.8
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 2 | 58.22
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 10 | 4.3
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | M |  | 25 | 81
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 18 | 3.42
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | FLAT END CLOSURE OD273X6.35 | SA515GR70 |  | NO |  | 2 | 34.92
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X6000 - SA312TP316L | SA312TP316L |  | M |  | 250 | 3553.25
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 12 | 59.64
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 2 | 11.82
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 172.02
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 4 | 8
3 | APL Raipur 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 2 | 2.86
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3762 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 32.357
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1733 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.906
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3644 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 31.342
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3079 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 26.482
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4807 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 41.345
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1662 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.295
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2728 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 23.464
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3978 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.215
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2539 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 21.838
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5201 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 44.734
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=298 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.563
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=326 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.804
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=104 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 0.895
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3339 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 28.719
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1739 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.957
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4942 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 42.506
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=892 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 7.672
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=171 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.471
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=562 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.834
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=699 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.012
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=782 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.726
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=780 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 5.178
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=268 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.779
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=3368 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 22.357
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=464 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.08
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=582 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.863
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=5178 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.372
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=673 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.467
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=151 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.002
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=1319 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 8.756
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 3 | 1.29
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 17 | 34
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 45DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 5 | 5.8
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BW EQUAL TEE OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 5.88
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.9BW UNEQT 114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 2.8
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1.75
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 1.54
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 0.56
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=3000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 25.803
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD88.9X3.05L=1000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.638
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X3.05L=2000 | SA312TP304H | 1-80-412-A0533 | NO |  | 1 | 12.92
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | BOTTOM PLATE 10THKX 1500X1500 | SA515GR70 | 1-80-412-A0533 | NO |  | 1 | 176.625
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1977 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 17.004
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD60.3X5.54 L=4000 | SA106GRB | 1-80-412-A0533 | NO |  | 1 | 29.924
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=264 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.271
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2672 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 22.982
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=360 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 3.096
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=242 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.081
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 50.66
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH CARRIER PLATES | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4382 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 37.69
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3039 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 26.138
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=192 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 1.651
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2938 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 25.27
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5544 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 47.684
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1001 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 8.61
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1583 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 13.615
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 8 | 16
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X5.49 L=2500 | SA106GRB | 2-80-412-A0362 | NO |  | 1 | 28.23
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 10MMX500X50010 | SA240TP304L | 2-80-412-A0362 | NO |  | 1 | 40.35
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=2000 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 17.202
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD168.3X3.4/114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 1 | 1.59
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 12MMX150X300 | SA515GR70 | 2-80-412-A0362 | NO |  | 1 | 4.239
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 230 | 591.56
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 50 | 8
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | BW UEQT 60.3X3.91/33.4X3.38 SA403WP316L | SA403WP316L |  | NO |  | 6 | 6.12
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25 SS | SA479TY304 |  | NO |  | 10 | 4.3
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD60.3X5.54 EP STY D D1-50.4AT SITE | SA106GRB |  | M |  | 25 | 187
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 8 | 7.2
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-60.3X3.91 EP STY D D1-53.2AT SITE | SA312TP316L |  | M |  | 130 | 726.57
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 18 | 11.7
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 180 | 462.96
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 21 | 3.36
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | SW RED NB50/25 CL3000 SA182F316 | SA182F316 | 4-80-452-85266 | NO |  | 2 | 7.2
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L |  | NO |  | 2 | 3.5
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 60.3 X 3.91 EP STY D D1-53.2 | SA312TP304H |  | M |  | 50 | 272
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP304H |  | NO |  | 10 | 6.5
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 5 | 2.5
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 50 | 125
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
3 | APL Raipur 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD60.3X3.91/33.4X3.38 | SA403WP304L |  | NO |  | 5 | 5.1
3 Total | [10 empty] | 34697.769
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1016 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 807.859
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PLATE 2500X2500X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 1 | 785
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT PIPE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=208 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 165.415
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=698 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 555.018
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 30DEG OD2032X16(R=0.75D)L=819 | SA515GR70 | 3-80-363-31709 | NO |  | 1 | 651.236
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 90DEG (R=0.75D) L=2457 | SA515GR70 | 3-80-363-31710 | NO |  | 2 | 3907.416
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | IMPULSE PIPE OD21.3X3.73 L=2750 | SA106GRB | 1-80-363-A0539 | NO |  | 4 | 17.82
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SPARE PIPE OD323.9X9.53 L=1000 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 73.88
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BLIND FLANGE ASSY. NB500 CL150 | SA515GR70 | 3-80-362-11781 | NO |  | 2 | 252
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STUD M30X200 | SA193B16 | 1-80-363-A0539 | NO |  | 44 | 37.4
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | HEX. NUT M30 | A194GR2H | 1-80-363-A0539 | NO |  | 88 | 20.24
4 | APL Raipur 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | GASKET, T=3 800X8 00 | NON-ASBESTOS | 1-80-363-A0539 | NO |  | 2 | 7.284
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1016 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 807.859
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PLATE 2500X2500X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 1 | 785
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT PIPE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=208 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 165.415
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=698 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 555.018
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 30DEG OD2032X16(R=0.75D)L=819 | SA515GR70 | 3-80-363-31709 | NO |  | 1 | 651.236
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 90DEG (R=0.75D) L=2457 | SA515GR70 | 3-80-363-31710 | NO |  | 2 | 3907.416
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | IMPULSE PIPE OD21.3X3.73 L=2750 | SA106GRB | 1-80-363-A0539 | NO |  | 4 | 17.82
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SPARE PIPE OD323.9X9.53 L=1000 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 73.88
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BLIND FLANGE ASSY. NB500 CL150 | SA515GR70 | 3-80-362-11781 | NO |  | 2 | 252
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STUD M30X200 | SA193B16 | 1-80-363-A0539 | NO |  | 44 | 37.4
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | HEX. NUT M30 | A194GR2H | 1-80-363-A0539 | NO |  | 88 | 20.24
4 | APL Raipur 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | GASKET, T=3 800X8 00 | NON-ASBESTOS | 1-80-363-A0539 | NO |  | 2 | 7.284
4 Total | [10 empty] | 51105.628
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | PIPE OD 273.00 X 6.35 X 6000 - SA106GRB | SA106GRB |  | M |  | 90 | 3758.4
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 14 | 366.8
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 1 | 29.11
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 5 | 2.15
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | M |  | 6 | 19.44
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 4 | 0.76
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | PIPE OD33.4X4.55 EP AT SITE 'D' D1=25.2 | SA106GRB |  | M |  | 280 | 907.2
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | PIPE OD60.3X5.54 EP AT SITE 'D' D1=49 | SA106GRB |  | M |  | 75 | 561
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | PIPE OD114.3X6.02EP AT SHOP 'D'D1=103.5 | SA106GRB |  | M |  | 950 | 15266.5
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | PIPE OD168.3X7.11EP AT SHOP 'D'D1=154.1 | SA106GRB |  | M |  | 50 | 1413
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 | SA234WPB |  | NO |  | 65 | 249.6
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X7.11 | SA234WPB |  | NO |  | 15 | 156
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 RED OD168.3X7.11/114.3X6.02 | SA234WPB |  | NO |  | 2 | 6.32
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | SW STUB NB25 CLASS 3000 | SA105 | 3-80-463-15996 | NO |  | 25 | 10.75
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 10 | 9
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 40 | 15.2
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 RED OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 2.82
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 3 | 4.95
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 1 | 1.4
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 UEQT OD168.3X7.11/114.3X6.02 | SA234WPB |  | NO |  | 2 | 24.04
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 88.9X5.49 EPD-79.0 AT SHOP | SA106GRB |  | M |  | 580 | 6554
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 - EP-D24.7(SITE L=40M | SA106GRB |  | M |  | 40 | 129.6
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD60.3X5.54 L=35M EP STY-D49.3(SITE | SA106GRB |  | M |  | 35 | 261.835
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 134 | 270.68
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 45DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 14 | 14.14
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 12 | 10.8
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 21 | 69.09
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 UEQT OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 14.85
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 4.3
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/48.3X5.08 | SA234WPB |  | NO |  | 5 | 3.85
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 15 | 2.85
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 EPSTY-D D1=24.7(SITE) | SA106GRB |  | M |  | 25 | 81
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 40 | 17.2
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NB50 OILHOSEASPERIS635 L=15 M WITH END | Rubber Hose |  | NO |  | 2 | 50
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT END CLOSURE OD88.9X5.49 | SA515GR70 |  | NO |  | 8 | 8.32
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT FACED FLANGE NB80 CL 150 SA105 | SA515GR70 | 4-80-340-73230 | NO |  | 4 | 36
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | STUD M16 X 2 X 160 SA193B7 | SA193B7 |  | NO |  | 10 | 2.24
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NUT -M16 -2H | A194GR2H |  | NO |  | 20 | 0.6
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 15 | 2.7
5 | APL Raipur 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 21.3 X 4.78 L=10M | SA106GRB |  | M |  | 10 | 19.5
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 88.9X5.49 EPD-79.0 AT SHOP | SA106GRB |  | M |  | 580 | 6554
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 - EP-D24.7(SITE L=40M | SA106GRB |  | M |  | 40 | 129.6
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD60.3X5.54 L=35M EP STY-D49.3(SITE | SA106GRB |  | M |  | 35 | 261.835
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 134 | 270.68
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 45DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 14 | 14.14
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 12 | 10.8
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 21 | 69.09
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 UEQT OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 14.85
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 4.3
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/48.3X5.08 | SA234WPB |  | NO |  | 5 | 3.85
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 15 | 2.85
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 EPSTY-D D1=24.7(SITE) | SA106GRB |  | M |  | 25 | 81
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 40 | 17.2
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NB50 OILHOSEASPERIS635 L=15 M WITH END | Rubber Hose |  | NO |  | 2 | 50
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT END CLOSURE OD88.9X5.49 | SA515GR70 |  | NO |  | 8 | 8.32
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT FACED FLANGE NB80 CL 150 SA105 | SA515GR70 | 4-80-340-73230 | NO |  | 4 | 36
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | STUD M16 X 2 X 160 SA193B7 | SA193B7 |  | NO |  | 10 | 2.24
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NUT -M16 -2H | A194GR2H |  | NO |  | 20 | 0.6
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 15 | 2.7
5 | APL Raipur 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 21.3 X 4.78 L=10M | SA106GRB |  | M |  | 10 | 19.5
5 Total | [10 empty] | 37919.15
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 90 | 561.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 120 | 358.8
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 7
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 15.25
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 2
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 24
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 1
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 220 | 1372.8
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 27.45
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 3
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB 50/40 IS1239 | IS1239 G&T |  | NO |  | 2 | 3.4
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 12 | 53.64
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 40 | 119.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 1.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 19.2
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 70 | 35
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 40 | 12
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 40 | 60
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 25 | 74.75
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 1.2
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 19.2
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 3
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 525 | 7717.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 360
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 45DEG BEND NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 28
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 48
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/150 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/100 G&T | As per drawing | 2-80-614-A0308 | NO | A | 4
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 4 | 40.284
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 4 | 8.984
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 27.879
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 30
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 22 | 88
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 4 | 41.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 10 | 28
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 299
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 45 | 9
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 54
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 42.155
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 130 | 169
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 98 | 410.13
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 180 | 40.32
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 40 | 18.72
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/25 | As per drawing | 2-80-616-10294 | NO | A | 5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/15 | As per drawing | 2-80-616-10294 | NO | A | 10
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB200 IS1239 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB200 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 60 | 179.4
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 120 | 24
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | EQTEE NB25 IS1239 GAL | IS1239 G&T |  | NO |  | 60 | 0.3
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 60 | 24
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 60 | 87.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 60 | 6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/25 | As per drawing | 2-80-614-A0308 | NO | A | 8
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 8 | 53.712
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 8 | 1.52
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 52 | 156
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 42.155
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 358 | 2233.92
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1575 | 4709.25
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 125 | 182.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 36 | 3.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 210 | 42
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 53.375
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 36 | 5.76
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 9
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 18 | 7.2
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 80
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 10 | 23
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 40 | 5.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | NUT -M16 -2H | A194GR2H |  | NO |  | 80 | 2.4
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 10 | 10
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 100 | 50
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 400 | 120
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 75 | 112.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 150
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 50 | 25
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 30 | 3
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 25 | 7.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 2
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB25 IS1239 GAL L=75MM | IS1239 G&T | 3-80-612-21071 | NO |  | 34 | 7.616
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 30 | 9
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SCREWED NIPPLE NB40 IS1239 | IS1239 G&T | 3-80-612-21072 | NO |  | 4 | 2.68
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 40 IS1239 | IS1239 G&T |  | NO |  | 15 | 12
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 250 | 5475
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 685 | 4274.4
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1405 | 4200.95
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 3335 | 4869.1
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 10 | 360
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 25 | 260
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 92 | 140.3
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 230 | 46
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 1020 | 102
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 27.25
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 9.504
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 0.8
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 4
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 108
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 295.085
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150/15 | As per drawing | 2-80-616-06449 | NO | A | 10
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4 L=200 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 42.4
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 L=65.4 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 0.94
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 60 | 72
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 365 | 146
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 32 | 16
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 10
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 4
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD NB50X4.5 | IS1239 BLACK | 4-80-612-50147 | NO |  | 50 | 46.25
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | SOCKET NB200 (GALVANISED) | IS3589-410MPA G&T | 4-80-616-71901 | NO |  | 25 | 157.65
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 65 | 97.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 175 | 87.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 360 | 108
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 840 | 84
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 200 IS1239 | IS1239 G&T |  | NO |  | 17 | 102
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 150 IS1239 | IS1239 G&T |  | NO |  | 45 | 441
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 120 | 180
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 25 IS1239 | IS1239 G&T |  | NO |  | 240 | 120
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 560 | 168
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB50 IS1239 L=150 | IS1239 G&T | 3-80-612-21073 | NO |  | 50 | 46.25
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB25 IS1239 L=150 | IS1239 G&T | 3-80-612-21071 | NO |  | 200 | 89.2
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB15 IS1239 L=150 | IS1239 G&T | 3-80-612-21070 | NO |  | 450 | 98.1
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25 WITH THREAD 1"BSP(M) | SA106GRB | 4-80-612-82549 | NO |  | 2 | 0.648
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 40 | 10.24
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD ISO7 RC-1-1/2"(F)(GAL) | SA105 (Galvanized) | 4-80-612-A0578 | NO |  | 65 | 91
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 525 | 7717.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 360
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 45DEG BEND NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 28
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB100 IS1239G&T | IS1239 G&T |  | NO |  | 12 | 72
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | UEQT 200/100 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 3
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 3 | 30.213
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 3 | 6.738
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 60
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 5 | 14
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/150 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 41.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 50 | 149.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/25 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 60
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/15 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 10
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB200 IS3589 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB200 IS3589 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 128 | 166.4
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 95 | 397.575
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 150 | 33.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 24 | 11.232
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB150 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 4 | 78.776
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB100 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 8 | 83.056
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | STUD M16 X 2 X 110 SA193B7 | SA193B7 |  | NO |  | 64 | 9.28
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 128 | 3.84
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 32 | 9.696
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M20 -2H | BPS 41319 |  | NO |  | 64 | 4.16
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 925 | 1350.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1640 | 4903.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 447
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 240 | 1497.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 86 | 13.76
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 58 | 29
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 218 | 87.2
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 7.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 20 | 24
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 341 | 34.1
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 418 | 83.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 53 | 80.825
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 2 | 4.6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 8 | 1.12
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 16 | 0.48
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 2 | 2
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB25 CL150- G&T | IS2062 |  | NO |  | 60 | 0.3
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 240 | 19.2
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 480 | 12
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB25CL150(GALV) | SA105 (Galvanized) |  | NO |  | 60 | 60
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB15 CL150- G&T | IS2062 |  | NO |  | 50 | 0.25
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 200 | 16
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 400 | 10
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB15 CL150(GALV | IS2062 |  | NO |  | 50 | 45
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 70 | 35
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 420 | 126
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 50 | 75
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 330 | 165
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 15 | 7.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 230 | 23
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 180 | 54
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB15 IS1239G&T | IS1239 G&T |  | NO |  | 50 | 5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 12
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 40 IS1239 | IS1239 G&T |  | NO |  | 20 | 16
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB 40 IS1239 | IS1239 G&T |  | NO |  | 12 | 4.8
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 200 | 2940
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB50X4.5 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 525 | 3276
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB25X4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 2200 | 6578
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 5850 | 8541
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 8 | 288
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 80
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 76.25
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 420 | 84
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1250 | 125
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 75 | 22.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB 200/100 IS1239 G&T | As per drawing | 2-80-616-10294 | NO | A | 2
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.0 L=300 | IS3589-410MPA | 2-80-616-10294 | NO |  | 2 | 18.918
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-616-10294 | NO |  | 2 | 4.492
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 1 | 6
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/50 IS1239 G&T | IS1239 G&T |  | NO |  | 13 | 52
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 140
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 12
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 48
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/15 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 108
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 20
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB25/15 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 120
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 50 IS1239 G7T | IS1239 G&T |  | NO |  | 10 | 5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 15 IS1239 G&T | IS1239 G&T |  | NO |  | 200 | 20
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB50X4.05 | IS1239 BLACK | 4-80-612-50147 | NO |  | 40 | 37
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB25X3.25 | IS1239 BLACK | 4-80-612-50147 | NO |  | 250 | 111.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB15X4.50 | IS1239 BLACK | 4-80-612-50147 | NO |  | 650 | 141.7
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 65
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 135 | 67.5
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB25 IS1329 G&T | IS1239 G&T |  | NO |  | 550 | 165
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1470 | 147
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 146.475
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 135
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 370 | 185
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 980 | 294
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0575 | NO |  | 10 | 6.17
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0574 | NO |  | 100 | 29.7
6 | APL Raipur 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1/2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0573 | NO |  | 650 | 94.25
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 90 | 561.6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 120 | 358.8
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 7
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 15.25
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 2
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 24
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 1
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 170 | 1060.8
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 14 | 21.35
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 3
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB 50/40 IS1239 | IS1239 G&T |  | NO |  | 2 | 3.4
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 12 | 53.64
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 40 | 119.6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 1.6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 19.2
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 60 | 30
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 35 | 10.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 32 | 48
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 12.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 18 | 53.82
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 1.2
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 16
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 3
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 585 | 8599.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 98 | 392
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 45DEG BEND NB100IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 42
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 48
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/150 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/100 G&T | As per drawing | 2-80-614-A0308 | NO | A | 4
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 4 | 40.284
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 4 | 8.984
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 27.879
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 30
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 22 | 88
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 4 | 41.6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 10 | 28
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 299
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 45 | 9
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 54
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 42.155
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 130 | 169
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 98 | 410.13
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 180 | 40.32
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 40 | 18.72
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/25 | As per drawing | 2-80-616-10294 | NO | A | 5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/15 | As per drawing | 2-80-616-10294 | NO | A | 10
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB200 IS1239 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB200 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 358 | 2233.92
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1575 | 4709.25
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 125 | 182.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 36 | 3.6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 210 | 42
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 53.375
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 36 | 5.76
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 9
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 18 | 7.2
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 80
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 10 | 23
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 40 | 5.6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | NUT -M16 -2H | A194GR2H |  | NO |  | 80 | 2.4
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 10 | 10
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 100 | 50
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 400 | 120
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 75 | 112.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 150
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 25 | 12.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 30 | 3
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 25 | 7.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB15 IS1239G&T | IS1239 G&T |  | NO |  | 10 | 1
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 250 | 5475
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 685 | 4274.4
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1405 | 4200.95
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 3335 | 4869.1
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 10 | 360
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 25 | 260
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 92 | 140.3
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 230 | 46
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 1020 | 102
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 27.25
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 9.504
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 0.8
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 4
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 108
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 295.085
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150/15 | As per drawing | 2-80-616-06449 | NO | A | 10
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4 L=200 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 42.4
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 L=65.4 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 0.94
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 60 | 72
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 365 | 146
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 32 | 16
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 10
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 4
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD NB50X4.5 | IS1239 BLACK | 4-80-612-50147 | NO |  | 50 | 46.25
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | SOCKET NB200 (GALVANISED) | IS3589-410MPA G&T | 4-80-616-71901 | NO |  | 25 | 157.65
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 65 | 97.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 175 | 87.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 360 | 108
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 840 | 84
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 200 IS1239 | IS1239 G&T |  | NO |  | 17 | 102
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 150 IS1239 | IS1239 G&T |  | NO |  | 45 | 441
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 120 | 180
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 25 IS1239 | IS1239 G&T |  | NO |  | 240 | 120
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 560 | 168
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB50 IS1239 L=150 | IS1239 G&T | 3-80-612-21073 | NO |  | 50 | 46.25
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB25 IS1239 L=150 | IS1239 G&T | 3-80-612-21071 | NO |  | 200 | 89.2
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB15 IS1239 L=150 | IS1239 G&T | 3-80-612-21070 | NO |  | 450 | 98.1
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25 WITH THREAD 1"BSP(M) | SA106GRB | 4-80-612-82549 | NO |  | 2 | 0.648
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 40 | 10.24
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD ISO7 RC-1-1/2"(F)(GAL) | SA105 (Galvanized) | 4-80-612-A0578 | NO |  | 65 | 91
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 580 | 8526
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 100 | 400
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 45DEG BEND NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 28
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB100 IS1239G&T | IS1239 G&T |  | NO |  | 15 | 90
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | UEQT 200/100 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 3
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 3 | 30.213
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 3 | 6.738
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 60
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 5 | 14
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/150 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 41.6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 50 | 149.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/25 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 60
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/15 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 10
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB200 IS3589 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB200 IS3589 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 128 | 166.4
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 95 | 397.575
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 150 | 33.6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 24 | 11.232
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB150 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 4 | 78.776
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB100 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 8 | 83.056
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | STUD M16 X 2 X 110 SA193B7 | SA193B7 |  | NO |  | 64 | 9.28
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 128 | 3.84
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 32 | 9.696
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M20 -2H | BPS 41319 |  | NO |  | 64 | 4.16
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 925 | 1350.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1640 | 4903.6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 447
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 240 | 1497.6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 86 | 13.76
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 58 | 29
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 218 | 87.2
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 7.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 20 | 24
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 341 | 34.1
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 418 | 83.6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 53 | 80.825
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 2 | 4.6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 8 | 1.12
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 16 | 0.48
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 2 | 2
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB25 CL150- G&T | IS2062 |  | NO |  | 60 | 0.3
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 240 | 19.2
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 480 | 12
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB25CL150(GALV) | SA105 (Galvanized) |  | NO |  | 60 | 60
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB15 CL150- G&T | IS2062 |  | NO |  | 50 | 0.25
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 200 | 16
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 400 | 10
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB15 CL150(GALV | IS2062 |  | NO |  | 50 | 45
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 70 | 35
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 420 | 126
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 50 | 75
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 330 | 165
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 15 | 7.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 230 | 23
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 180 | 54
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB15 IS1239G&T | IS1239 G&T |  | NO |  | 50 | 5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 12
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 40 IS1239 | IS1239 G&T |  | NO |  | 20 | 16
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB 40 IS1239 | IS1239 G&T |  | NO |  | 12 | 4.8
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 200 | 2940
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB50X4.5 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 525 | 3276
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB25X4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 2200 | 6578
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 5850 | 8541
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 8 | 288
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 80
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 76.25
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 420 | 84
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1250 | 125
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 75 | 22.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB 200/100 IS1239 G&T | As per drawing | 2-80-616-10294 | NO | A | 2
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.0 L=300 | IS3589-410MPA | 2-80-616-10294 | NO |  | 2 | 18.918
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-616-10294 | NO |  | 2 | 4.492
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 1 | 6
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/50 IS1239 G&T | IS1239 G&T |  | NO |  | 13 | 52
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 140
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 12
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 48
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/15 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 108
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 20
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB25/15 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 120
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 50 IS1239 G7T | IS1239 G&T |  | NO |  | 10 | 5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 15 IS1239 G&T | IS1239 G&T |  | NO |  | 200 | 20
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB50X4.05 | IS1239 BLACK | 4-80-612-50147 | NO |  | 40 | 37
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB25X3.25 | IS1239 BLACK | 4-80-612-50147 | NO |  | 250 | 111.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB15X4.50 | IS1239 BLACK | 4-80-612-50147 | NO |  | 650 | 141.7
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 65
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 135 | 67.5
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB25 IS1329 G&T | IS1239 G&T |  | NO |  | 550 | 165
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1470 | 147
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 146.475
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 135
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 370 | 185
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 980 | 294
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0575 | NO |  | 10 | 6.17
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0574 | NO |  | 100 | 29.7
6 | APL Raipur 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1/2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0573 | NO |  | 650 | 94.25
6 Total | [10 empty] | 205766.833
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 323.9X6.4 EP STY D D1-311.2 | IS3589-410MPA |  | M |  | 20 | 1001
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 273.1 X 6.4 EP STY D-D1 260.3 | IS3589-410MPA |  | M |  | 65 | 2735.85
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 219.1 X 6.4 EP STY D-D1 206.3 | IS3589-410MPA |  | M |  | 300 | 10071
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB150X5.4 EP STY D-D1-156.8 | IS1239 BLACK |  | M |  | 640 | 13568
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB100X5.4 EP STY D-D1-105.3 | IS1239 BLACK |  | M |  | 140 | 2016
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB80X4.8 EP STY D-D1-80.8 | IS1239 BLACK |  | M |  | 920 | 9292
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB50X4.5 EP STY D-D1-52.7 | IS1239 BLACK |  | M |  | 400 | 2468
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB40X 4.0 EP STY D-D1-41.5 | IS1239 BLACK |  | M |  | 310 | 1373.3
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB25X4.0 EP STY D-D1-26.9 | IS1239 BLACK |  | M |  | 725 | 2153.25
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB15X 3.2 EP STY D-D1-15.9 | IS1239 BLACK |  | M |  | 680 | 986
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 12 | 200.4
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 10 | 262
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 208
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 150
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 280.8
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 116.1
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 30
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 24
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 140 | 14
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 6 | 214.2
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 11
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 33
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 18
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 3.6
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 10.5
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD273X6.35/88.9X5.49 | SA234WPB |  | NO |  | 4 | 101.28
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 12 | 180
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 58
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 65 | 104
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 16.5
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 24
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 24
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 93.75
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 33
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 13.5
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 17.5
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 85 | 25.5
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 1
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 5
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 4 | 20
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 18
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | UEQT NB 150/100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 31
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/88.9X5.49 | SA234WPB |  | NO |  | 8 | 135.04
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD168.3X7.11/60.3X5.54 | SA234WPB |  | NO |  | 10 | 113.9
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 9
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 10
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 18
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 2.5
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 3 | 0.6
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 1.5
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/50) | As per drawing | 3-80-999-97670 | NO |  | 15 | 99.375
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/40) | As per drawing | 3-80-999-97669 | NO |  | 18 | 119.25
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/25) | As per drawing | 3-80-999-97668 | NO |  | 30 | 216.75
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/15) | As per drawing | 3-80-999-97667 | NO |  | 5 | 36.125
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB15 CL3000 | SA105 |  | NO |  | 130 | 23.4
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB25 CL3000 | SA105 |  | NO |  | 50 | 21.5
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB40 CL3000 | SA105 |  | NO |  | 25 | 18.75
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB50 CL3000 | SA105 |  | NO |  | 30 | 39.9
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=45 | SA105 |  | NO |  | 10 | 5
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=64 | SA105 |  | NO |  | 120 | 84
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB15 | SA106GRB | 3-80-463-27244 | NO |  | 430 | 104.49
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB25 | IS1239 BLACK | 3-80-463-27244 | NO |  | 95 | 42.37
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB40 | IS1239 BLACK | 3-80-463-27244 | NO |  | 18 | 11.952
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB50 | IS1239 BLACK | 3-80-463-27244 | NO |  | 64 | 59.2
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PLUG FOR THERMO COUPLE NIPPLE M33X2 (CS) | SA105 |  | NO |  | 130 | 104
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PACKING RING | IS1972 |  | NO |  | 130 | 1.3
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 310 | 17084.1
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD406.4X6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 105 | 6220.2
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD273.1X6.0 EP STY 'D' D1=261.1 | IS3589-410MPA |  | M |  | 50 | 1975
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB25X4.0 BLACK EP STY 'D' D1=26.9 | IS1239 BLACK |  | M |  | 175 | 519.75
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB50X4.5 EP ST Y D D1=52.7 | IS1239 BLACK |  | M |  | 85 | 524.45
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.0 EP STY 'D' D1=207.1 | IS3589-410MPA |  | M |  | 85 | 2680.05
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.35 EP STY 'D' D1=206.4 | SA106GRB |  | M |  | 35 | 1165.85
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB80 X 4.8 EP STY 'D' D1=80.8 SHOP | IS1239 BLACK |  | M |  | 25 | 252.5
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90 X 5.49 STY'D',78 SHOP | SA106GRB |  | M |  | 5 | 56.45
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90X11.13 STY'D',69.2 SHOP | SA106GRC |  | M |  | 120 | 2562
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE DIA 33.4 X 9.09 EP STY 'D' D1=17.2 | SA106GRC |  | M |  | 20 | 109
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 20 | 915.8
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 12 | 314.4
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 7
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 15 | 250.5
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL 90DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 15.48
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X11.13 | SA234WPC |  | NO |  | 12 | 45.84
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X9.09 | SA234WPC |  | NO |  | 6 | 1.98
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 30.4
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 2 | 4.04
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD355.6X6.35 | SA234WPB |  | NO |  | 4 | 196.56
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD406.4X9.53/219.1X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 161.44
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 112.3
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/219.1X6.35 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 54.83
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/88.9X5.49 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 3.84
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 3
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 32
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD88.9X11.13 | SA234WPC |  | NO |  | 1 | 6.21
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD88.9X11.13/60.3X11.07 | SA234WPC |  | NO |  | 2 | 11.16
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB15 | SA105 | 4-80-329-79004 | NO |  | 10 | 1.8
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB25 | SA105 | 4-80-329-79005 | NO |  | 30 | 12.9
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | TEMP.STUB M33X2 L=45 | SA105 |  | NO |  | 2 | 1
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 4 | 83.88
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 5 | 39.5
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED NB80/PUMP END | IS1239 |  | NO |  | 2 | 0.2
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED PUMP END/NB80 | IS1239 |  | NO |  | 2 | 0.2
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | NB25 SW END WITH 1" NPT (F), CS | SA105 | 4-80-471-84576 | NO |  | 2 | 0.4
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SCREW PLUG M33X2 | SA105 |  | NO |  | 2 | 0.32
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.11 SW RED NB50/25 CL9000 | SA105 |  | NO |  | 2 | 2
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SW END CAP NB 50 CL3000 | SA105 | 4-80-453-58056 | NO |  | 2 | 1.4
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 400 | 5760
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 200
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. LR 45DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 12
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 23.4
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB100 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 21.6
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BW CAP OD114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 5 | 5.9
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 40 | 118.8
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 20 | 8.6
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NIPPLE 1" PLAIN X EXT THRD L=100MM | SA106GRB | 4-80-418-A0468 | NO |  | 70 | 22.68
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NB25 RUBBER HOSE L=15M IS444 TYPE II | IS444 Type II |  | NO |  | 35 | 525
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 425 | 2622.25
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 448 | 1330.56
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 145.125
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. RED NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 24 | 9.6
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 96
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.4
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 224 | 44.8
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | ASME B16.5 BLIND FLANGE NB50 CL150 | SA515GR70 | 4-80-477-A0644 | NO |  | 24 | 76.8
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 96 | 13.44
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NUT -M16 -2H | A194GR2H |  | NO |  | 192 | 5.76
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FLAT FACED FLANGE NB50 CLASS 150 | SA515GR70 | 4-80-468-65420 | NO |  | 24 | 48
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 70 | 1008
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 30
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD273.1 X 6.4 EP STY 'D' D1=260.3 | IS3589-410MPA |  | M |  | 270 | 10665
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4 X 6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 160 | 9478.4
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 50 | 2755.5
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPENB25X4.0 EP STY D D1-26.9 | IS1239 BLACK |  | M |  | 475 | 1410.75
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB80X4.8 EP STY D D1-80.8 | IS1239 BLACK |  | M |  | 950 | 9595
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB40X4.0 EP STY D D1-41.5 | IS1239 BLACK |  | M |  | 80 | 354.4
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB50X4.5 EP STY D D1-52.7 | IS1239 BLACK |  | M |  | 160 | 987.2
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 28 | 733.6
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 8 | 366.32
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 27
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 180 | 684
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 48
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 58.05
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/273.1X6.35 | SA234WPB |  | NO |  | 2 | 38.42
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 2 | 41.94
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.6
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 4
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 1 | 29.11
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 1 | 60.78
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD406.4X9.53/355.6X9.53 | SA234WPB |  | NO |  | 2 | 177.66
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | WELDED UN EQ TEE NB400/NB80 | As per drawing | 3-80-471-33301 | NO | A | 2
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4X8 L=800 | IS3589-410MPA | 3-80-471-33301 | NO |  | 2 | 125.754
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 88.9X4 | IS1239 BLACK | 3-80-471-33301 | NO |  | 2 | 2.936
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 8
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 52 | 195
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 130 | 208
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 57
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 4
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED NB40/NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 3
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB15 CL3000 SA105 | SA105 |  | NO |  | 15 | 2.7
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB25 CL3000 SA105 | SA105 |  | NO |  | 20 | 8.6
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | TEMP.STUB M33X2(CS) L=45 | SA105 |  | NO |  | 2 | 1
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB |  | NO |  | 2 | 112.3
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PLUG FOR THREMOCOUPLE NIPPLE M33X29CS) | SA105 |  | NO |  | 2 | 1.6
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 RC-1-1/2 INCH(F) | SA105 | 4-80-480-82955 | NO |  | 30 | 30.45
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(F)BSPT | SA105 | 4-80-480-84585 | NO |  | 25 | 16.75
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(M)BSPT | SA105 | 4-80-480-A0580 | NO |  | 25 | 16.75
7 | APL Raipur 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 R 1-1/2 INCH | SA105 | 4-80-480-A0581 | NO |  | 70 | 98
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 323.9X6.4 EP STY D D1-311.2 | IS3589-410MPA |  | M |  | 20 | 1001
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 273.1 X 6.4 EP STY D-D1 260.3 | IS3589-410MPA |  | M |  | 65 | 2735.85
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 219.1 X 6.4 EP STY D-D1 206.3 | IS3589-410MPA |  | M |  | 300 | 10071
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB150X5.4 EP STY D-D1-156.8 | IS1239 BLACK |  | M |  | 640 | 13568
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB100X5.4 EP STY D-D1-105.3 | IS1239 BLACK |  | M |  | 140 | 2016
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB80X4.8 EP STY D-D1-80.8 | IS1239 BLACK |  | M |  | 920 | 9292
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB50X4.5 EP STY D-D1-52.7 | IS1239 BLACK |  | M |  | 400 | 2468
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB40X 4.0 EP STY D-D1-41.5 | IS1239 BLACK |  | M |  | 310 | 1373.3
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB25X4.0 EP STY D-D1-26.9 | IS1239 BLACK |  | M |  | 725 | 2153.25
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB15X 3.2 EP STY D-D1-15.9 | IS1239 BLACK |  | M |  | 680 | 986
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 12 | 200.4
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 10 | 262
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 208
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 150
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 280.8
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 116.1
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 30
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 24
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 140 | 14
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 6 | 214.2
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 11
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 33
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 18
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 3.6
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 10.5
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD273X6.35/88.9X5.49 | SA234WPB |  | NO |  | 4 | 101.28
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 12 | 180
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 58
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 65 | 104
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 16.5
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 24
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 24
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 93.75
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 33
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 13.5
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 17.5
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 85 | 25.5
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 1
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 5
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 4 | 20
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 18
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | UEQT NB 150/100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 31
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/88.9X5.49 | SA234WPB |  | NO |  | 8 | 135.04
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD168.3X7.11/60.3X5.54 | SA234WPB |  | NO |  | 10 | 113.9
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 9
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 10
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 18
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 2.5
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 3 | 0.6
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 1.5
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/50) | As per drawing | 3-80-999-97670 | NO |  | 15 | 99.375
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/40) | As per drawing | 3-80-999-97669 | NO |  | 18 | 119.25
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/25) | As per drawing | 3-80-999-97668 | NO |  | 30 | 216.75
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/15) | As per drawing | 3-80-999-97667 | NO |  | 5 | 36.125
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB15 CL3000 | SA105 |  | NO |  | 130 | 23.4
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB25 CL3000 | SA105 |  | NO |  | 50 | 21.5
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB40 CL3000 | SA105 |  | NO |  | 25 | 18.75
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB50 CL3000 | SA105 |  | NO |  | 30 | 39.9
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=45 | SA105 |  | NO |  | 10 | 5
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=64 | SA105 |  | NO |  | 120 | 84
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB15 | SA106GRB | 3-80-463-27244 | NO |  | 430 | 104.49
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB25 | IS1239 BLACK | 3-80-463-27244 | NO |  | 95 | 42.37
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB40 | IS1239 BLACK | 3-80-463-27244 | NO |  | 18 | 11.952
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB50 | IS1239 BLACK | 3-80-463-27244 | NO |  | 64 | 59.2
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PLUG FOR THERMO COUPLE NIPPLE M33X2 (CS) | SA105 |  | NO |  | 130 | 104
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PACKING RING | IS1972 |  | NO |  | 130 | 1.3
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 310 | 17084.1
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD406.4X6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 105 | 6220.2
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD273.1X6.0 EP STY 'D' D1=261.1 | IS3589-410MPA |  | M |  | 50 | 1975
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB25X4.0 BLACK EP STY 'D' D1=26.9 | IS1239 BLACK |  | M |  | 175 | 519.75
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB50X4.5 EP ST Y D D1=52.7 | IS1239 BLACK |  | M |  | 85 | 524.45
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.0 EP STY 'D' D1=207.1 | IS3589-410MPA |  | M |  | 85 | 2680.05
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.35 EP STY 'D' D1=206.4 | SA106GRB |  | M |  | 35 | 1165.85
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB80 X 4.8 EP STY 'D' D1=80.8 SHOP | IS1239 BLACK |  | M |  | 25 | 252.5
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90 X 5.49 STY'D',78 SHOP | SA106GRB |  | M |  | 5 | 56.45
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90X11.13 STY'D',69.2 SHOP | SA106GRC |  | M |  | 120 | 2562
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE DIA 33.4 X 9.09 EP STY 'D' D1=17.2 | SA106GRC |  | M |  | 20 | 109
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 20 | 915.8
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 12 | 314.4
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 7
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 15 | 250.5
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL 90DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 15.48
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X11.13 | SA234WPC |  | NO |  | 12 | 45.84
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X9.09 | SA234WPC |  | NO |  | 6 | 1.98
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 30.4
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 2 | 4.04
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD355.6X6.35 | SA234WPB |  | NO |  | 4 | 196.56
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD406.4X9.53/219.1X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 161.44
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 112.3
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/219.1X6.35 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 54.83
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/88.9X5.49 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 3.84
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 3
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 32
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD88.9X11.13 | SA234WPC |  | NO |  | 1 | 6.21
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD88.9X11.13/60.3X11.07 | SA234WPC |  | NO |  | 2 | 11.16
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB15 | SA105 | 4-80-329-79004 | NO |  | 10 | 1.8
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB25 | SA105 | 4-80-329-79005 | NO |  | 30 | 12.9
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | TEMP.STUB M33X2 L=45 | SA105 |  | NO |  | 2 | 1
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 4 | 83.88
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 5 | 39.5
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED NB80/PUMP END | IS1239 |  | NO |  | 2 | 0.2
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED PUMP END/NB80 | IS1239 |  | NO |  | 2 | 0.2
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | NB25 SW END WITH 1" NPT (F), CS | SA105 | 4-80-471-84576 | NO |  | 2 | 0.4
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SCREW PLUG M33X2 | SA105 |  | NO |  | 2 | 0.32
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.11 SW RED NB50/25 CL9000 | SA105 |  | NO |  | 2 | 2
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SW END CAP NB 50 CL3000 | SA105 | 4-80-453-58056 | NO |  | 2 | 1.4
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 400 | 5760
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 200
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. LR 45DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 12
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 23.4
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB100 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 21.6
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BW CAP OD114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 5 | 5.9
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 40 | 118.8
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 20 | 8.6
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NIPPLE 1" PLAIN X EXT THRD L=100MM | SA106GRB | 4-80-418-A0468 | NO |  | 70 | 22.68
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NB25 RUBBER HOSE L=15M IS444 TYPE II | IS444 Type II |  | NO |  | 10 | 150
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 425 | 2622.25
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 448 | 1330.56
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 145.125
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. RED NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 24 | 9.6
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 96
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.4
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 224 | 44.8
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | ASME B16.5 BLIND FLANGE NB50 CL150 | SA515GR70 | 4-80-477-A0644 | NO |  | 24 | 76.8
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 96 | 13.44
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NUT -M16 -2H | A194GR2H |  | NO |  | 192 | 5.76
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FLAT FACED FLANGE NB50 CLASS 150 | SA515GR70 | 4-80-468-65420 | NO |  | 24 | 48
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD273.1 X 6.4 EP STY 'D' D1=260.3 | IS3589-410MPA |  | M |  | 270 | 10665
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4 X 6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 160 | 9478.4
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 50 | 2755.5
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPENB25X4.0 EP STY D D1-26.9 | IS1239 BLACK |  | M |  | 475 | 1410.75
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB80X4.8 EP STY D D1-80.8 | IS1239 BLACK |  | M |  | 950 | 9595
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB40X4.0 EP STY D D1-41.5 | IS1239 BLACK |  | M |  | 80 | 354.4
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB50X4.5 EP STY D D1-52.7 | IS1239 BLACK |  | M |  | 160 | 987.2
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 28 | 733.6
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 8 | 366.32
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 27
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 180 | 684
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 48
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 58.05
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/273.1X6.35 | SA234WPB |  | NO |  | 2 | 38.42
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 2 | 41.94
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.6
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 4
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 1 | 29.11
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 1 | 60.78
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD406.4X9.53/355.6X9.53 | SA234WPB |  | NO |  | 2 | 177.66
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | WELDED UN EQ TEE NB400/NB80 | As per drawing | 3-80-471-33301 | NO | A | 2
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4X8 L=800 | IS3589-410MPA | 3-80-471-33301 | NO |  | 2 | 125.754
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 88.9X4 | IS1239 BLACK | 3-80-471-33301 | NO |  | 2 | 2.936
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 8
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 52 | 195
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 130 | 208
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 57
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 4
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED NB40/NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 3
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB15 CL3000 SA105 | SA105 |  | NO |  | 15 | 2.7
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB25 CL3000 SA105 | SA105 |  | NO |  | 20 | 8.6
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | TEMP.STUB M33X2(CS) L=45 | SA105 |  | NO |  | 2 | 1
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB |  | NO |  | 2 | 112.3
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PLUG FOR THREMOCOUPLE NIPPLE M33X29CS) | SA105 |  | NO |  | 2 | 1.6
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 RC-1-1/2 INCH(F) | SA105 | 4-80-480-82955 | NO |  | 30 | 30.45
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(F)BSPT | SA105 | 4-80-480-84585 | NO |  | 25 | 16.75
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(M)BSPT | SA105 | 4-80-480-A0580 | NO |  | 25 | 16.75
7 | APL Raipur 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 R 1-1/2 INCH | SA105 | 4-80-480-A0581 | NO |  | 70 | 98
7 Total | [10 empty] | 271619.014
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 20 | 50
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE DIA 114.30 X 3.05 - SA312TP304H | SA312TP304H |  | M |  | 55 | 460.35
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 98 | 291.06
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB40X 4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 80 | 354.4
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 202 | 1246.34
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE NB 80 HEAVY - IS1239 | IS1239 BLACK |  | M |  | 466 | 4590.1
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 88 | 1267.2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 336 | 7123.2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 219.1 X 6.0 IS3589-410MPA | IS3589-410MPA |  | M |  | 174 | 5486.22
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1 X 6.4 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 144 | 6060.96
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 323.9X 6.35 IS3589FE410 PA | IS3589-410MPA |  | M |  | 140 | 6962.2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 355.6 X 6.4 IS3589-410MPA | IS3589-410MPA |  | M |  | 50 | 2755.5
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 406.4 X 6.0 EFW IS3589 LS/SPIRA | IS3589-410MPA |  | M |  | 7.5 | 444.3
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA457.1X6.0EFW IS3589-410MPA(LS/SPI | IS3589-410MPA |  | M |  | 170 | 11342.4
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 94 | 6982.32
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 102 | 9115.536
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 EFW IS3589-410MPA-LS/SPIR | IS3589-410MPA |  | M |  | 107 | 14840.9
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP304H |  | NO |  | 7 | 14
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 8 | 1.2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 34 | 6.8
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 6.4
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 28 | 54.18
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. LR 45DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 16
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 144 | 547.2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 18 | 90
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 94 | 977.6
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 46 | 768.2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.92
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 24 | 399.84
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 33 | 786.06
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 4 | 71.36
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 10 | 457.9
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. UEQT NB150 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.752
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BW LR 60DEG ELL 219.1 X 8.18 SA234WPB | SA234WPB |  | NO |  | 4 | 56
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 6 | 1.2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 2 | 1.2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 14.4
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RED NB 100/80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 19.8
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 17.94
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.68
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 2 | 2.52
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 16.32
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/323.9X6.35 | SA234WPB |  | NO |  | 7 | 120.75
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/323.9X6.35 | SA234WPB |  | NO |  | 2 | 47.18
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 3 | 48.45
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X9.53/355.6X9.53 | SA234WPB |  | NO |  | 4 | 144.52
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/406.4X6.35 | SA234WPB |  | NO |  | 2 | 50.94
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD168.3X7.11/114.3X6.02 | SA234WPB |  | NO |  | 2 | 6.32
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD 114.3X3.05 | SA403WP304H |  | NO |  | 1 | 2.94
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 1 | 0.4
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD219.1X6.35 | SA234WPB |  | NO |  | 6 | 115.62
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD168.3X7.11 | SA234WPB |  | NO |  | 2 | 26.56
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 4 | 13.16
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 4 | 243.12
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD457.2X9.53 | SA234WPB |  | NO |  | 2 | 229.54
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 5.94
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 107.2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD168.3X7.11/88.9X5.49 | SA234WPB |  | NO |  | 8 | 93.04
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD355.6X7.92/168.3X7.11 | SA234WPB |  | NO |  | 4 | 215.84
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/168.3X6.35 | SA234WPB |  | NO |  | 2 | 36.38
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 51.26
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT OD711.2X8 | As per drawing | 3-80-463-31357 | NO | A | 1
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=1200 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 166.44
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=750 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 104.025
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 508 X 6 | As per drawing | 3-80-463-A0817 | NO | A | 5
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 790.975
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA508X10 L=239 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 146.69
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 610 X 8 | As per drawing | 3-80-463-A0818 | NO | A | 6
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 908.496
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA610X10 L=298 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 264.432
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD610X6/323.9X6 | As per drawing | 3-80-463-A0820 | NO | A | 2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD610X10 L=600 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 177.552
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD323.9X8 L=186 00 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 23.174
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/355.6X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 5
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 964.7
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA355.6X8LS/SPIRAL IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 131.865
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/323.9 X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 1
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 166.63
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 323.9 X 8 IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 20.372
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB700/NB450 | As per drawing | 3-80-463-A0821 | NO | A | 5
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD711X10 IS 2062E250B | IS2062E250GRBR | 3-80-468-32127 | NO |  | 5 | 876.06
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 457X8 IS 3589 | IS3589-410MPA | 3-80-463-A0821 | NO |  | 5 | 98.765
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD508X6/OD457X6 | IS2062E250GRBR | 4-80-463-A0473 | NO |  | 4 | 197.192
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCER NB700/NB450 | IS2062E250GRBR | 4-80-463-A0474 | NO |  | 1 | 141.379
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD711.2/OD610 | IS2062E250GRBR | 4-80-463-A0475 | NO |  | 1 | 105.111
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD711.2X8/OD508X6 | IS2062E250GRBR | 4-80-463-A0478 | NO |  | 6 | 614.184
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD508X6/OD323.9X6 | IS2062E250GRBR | 4-80-463-A0479 | NO |  | 4 | 254.216
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ECC RED OD610X6/OD406.4X6 | IS2062E250GRBR | 3-80-463-A0819 | NO |  | 3 | 157.125
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 18 | 1369.44
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD457.2X9.53 | SA234WPB |  | NO |  | 8 | 604.24
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 4 | 152.08
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD508X9.53 | SA234WPB |  | NO |  | 20 | 1869.6
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 30°MITRE BEND Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0806 | NO |  | 3 | 85.344
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 711X8 (R=700) | IS2062E250GRBR | 3-80-463-A0807 | NO |  | 6 | 974.028
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 45DEG OD711.2X8 (R=700) | IS2062E250GRBR | 3-80-463-A0808 | NO |  | 2 | 162.024
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 60° OD 457 X 8 (R=686) | IS2062E250GRBR | 3-80-463-A0809 | NO |  | 2 | 133.93
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 610.0X8 (R=600) | IS2062E250GRBR | 3-80-463-A0810 | NO |  | 8 | 957.576
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | MITREBEND 45DEG Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0822 | NO |  | 2 | 85.66
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 100 | 18
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 100 | 43
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 50 CLASS 3000 | SA105 |  | NO |  | 100 | 133
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L45 | SA105 | 4-80-463-63321 | NO |  | 70 | 59.08
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L64 | SA105 | 4-80-463-23357 | NO |  | 70 | 176.96
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLUG RC 1" | SA105 | 4-80-463-23358 | NO |  | 140 | 70
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1"(NB80/50) | As per drawing | 3-80-460-28909 | NO | A | 40
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28909 | NO |  | 40 | 60.6
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK | 3-80-460-28909 | NO |  | 80 | 144
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 3-80-460-28909 | NO |  | 40 | 101.12
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 3-80-460-28909 | NO |  | 40 | 44.12
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1" (NB80/25) | As per drawing | 3-80-460-28907 | NO | A | 40
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28907 | NO |  | 40 | 60.6
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 144
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 24
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 4-80-463-23357 | NO |  | 40 | 101.12
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 4-80-463-23358 | NO |  | 40 | 44.12
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 308.5
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 38.7
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 70 | 207.9
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 5
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE NB15 IS1239 | IS1239 BLACK |  | M |  | 50 | 73.4
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 20 | 2.6
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 30 | 636
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1X 6.35 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 150 | 6262.5
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 62 | 5540.816
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 813 X 8 EFW-LS/SPIRAL IS3589-410MPA | IS3589-410MPA |  | M |  | 69 | 10957.2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 15 | 1114.2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 62.4
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 45DEG BEND NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 24
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 20 | 524
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 8 | 104.8
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=600) | IS3589-410MPA | 3-80-468-32248 | NO |  | 8 | 943.744
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=915) | IS2062E250GRBR | 3-80-463-A0833 | NO |  | 10 | 1780.38
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 30DEG MITRE BEND OD813X10 (R=800) | IS2062E250GRBR | 3-80-463-A0834 | NO |  | 2 | 174.898
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD813X9.53 | SA234WPB |  | NO |  | 3 | 1084.74
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD813X10 (R=800) | IS3589-410MPA | 3-80-463-27732 | NO |  | 9 | 2322.504
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 9.68
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 13.68
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BW RED 168.3X7.11/114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 8 | 32
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB350 | IS2062E250GRBR | 4-80-463-A0488 | NO |  | 6 | 375.684
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB250 | IS2062E250GRBR | 4-80-463-A0489 | NO |  | 4 | 234.112
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB800/NB600 | IS2062E250GRBR | 4-80-463-A0490 | NO |  | 3 | 275.715
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RED NB800/NBXXX HOLD | IS1239 |  | NO |  | 4 | 0.02
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB500 | As per drawing | 3-80-463-A0829 | NO | A | 1
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=1000 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 122.696
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=427 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 52.36
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB600 | As per drawing | 3-80-463-A0828 | NO | A | 1
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X12 L=1200 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 212.138
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X10 L=515 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 76.145
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 8 | 214.4
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT NB500/NB350 | As per drawing | 3-80-463-A0830 | NO | A | 3
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD508X8 L=700 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 207.144
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD355.6X8 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 42.744
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/250 | As per drawing | 3-80-463-A0825 | NO | A | 1
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X10;L=900 | IS2062E250GRBR | 3-80-463-A0825 | NO |  | 1 | 133.058
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD273.1X6.0;L=222 | IS3589-410MPA | 3-80-463-A0825 | NO |  | 1 | 8.769
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/500 | As per drawing | 3-80-463-A0836 | NO | A | 1
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø610X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 118.221
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø508X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 50.947
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB800/600 | As per drawing | 3-80-463-A0826 | NO | A | 4
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1000 | IS2062E250GRBR | 3-80-463-A0826 | NO |  | 4 | 947.652
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X6;L=322 | IS3589-410MPA | 3-80-463-A0826 | NO |  | 4 | 115.104
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED EQUAL TEENB800 | As per drawing | 3-80-463-A0827 | NO | A | 1
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1200 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 284.296
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=394 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 93.352
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACED FLANGE NB 500 CLASS 150 | SA515GR70 | 4-80-468-65426 | NO |  | 3 | 162
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB500 | SA515GR70 | 4-80-463-A0484 | NO |  | 3 | 383.4
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | STUD M30 X 3.5 X 230 SA193B7 | SA193B7 |  | NO |  | 60 | 66.24
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M30 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 120 | 27.6
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACE FLANGE NB800 | IS2062E250GRBR | 3-80-468-27258 | NO |  | 2 | 196.2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB-800 | IS2062E250GRBR | 4-80-463-A0486 | NO |  | 2 | 507.46
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | STUD M36X4 - 290 SA193B7 | SA193B7 |  | NO |  | 56 | 112
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | HEX NUT M36 X 4 SA194GR2H | SA194GR2H |  | NO |  | 112 | 48.16
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 300 | 1851
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 77.4
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 150 | 385.8
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 20 | 3.2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000 SA182F316 | SA182F316 |  | NO |  | 1 | 0.25
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 25 | 64.3
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 25 | 4
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000SA182F316 | SA182F316 |  | NO |  | 15 | 3.75
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 15 | 44.55
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW STUB NB25 CL3000 SA479TY316L | SA479TY316L |  | NO |  | 25 | 10.75
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB300 (OP -1) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=12 Ø 404 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 21.724
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=12 40X104 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.744
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB300 (OP -2) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8 Ø404 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 13.056
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8, 40X104 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.496
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB150 (OP -3) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8 Ø 217.5 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 4.016
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8, 30X96 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.344
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB250 (OP -4) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8 Ø 334 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 9.372
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8, 40X99 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.472
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB500 ( OP -5) | As per drawing | 3-80-463-A0944 | NO | A | 2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=10 Ø 600 | IS2062E250GRBR | 3-80-463-A0944 | NO |  | 2 | 37.124
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=10, 40X115 | IS2062E250GRBR | 3-80-463-A0944 | NO |  | 2 | 0.686
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB80 ( OP -6) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=6 Ø 133 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 1.2
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=6, 30X93 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.25
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB80 CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 36.272
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB150 CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 78.776
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB250CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 185.412
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB300CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 8 | 531.8
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB500CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 769.3
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | STUD M16 X 2 X 110 SA193B7 | SA193B7 |  | NO |  | 8 | 1.16
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M16 -2H | A194GR2H |  | NO |  | 16 | 0.48
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 16 | 4.848
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M20 -2H | BPS 41319 |  | NO |  | 32 | 2.08
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | STUD M 24 X 3 X 220 SA193 B16 | SA193B16 |  | NO |  | 72 | 47.52
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M24 -CL6-IS1364P3 BPS 41301 | IS:1364 (P-3) |  | NO |  | 144 | 15.84
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | STUD M30 X 3.5 X 230SA193B7 | SA193B7 |  | NO |  | 40 | 44.16
8 | APL Raipur 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M30 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 80 | 18.4
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 20 | 50
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE DIA 114.30 X 3.05 - SA312TP304H | SA312TP304H |  | M |  | 55 | 460.35
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 98 | 291.06
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB40X 4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 80 | 354.4
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 202 | 1246.34
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE NB 80 HEAVY - IS1239 | IS1239 BLACK |  | M |  | 466 | 4590.1
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 88 | 1267.2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 336 | 7123.2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 219.1 X 6.0 IS3589-410MPA | IS3589-410MPA |  | M |  | 174 | 5486.22
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1 X 6.4 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 144 | 6060.96
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 323.9X 6.35 IS3589FE410 PA | IS3589-410MPA |  | M |  | 140 | 6962.2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 355.6 X 6.4 IS3589-410MPA | IS3589-410MPA |  | M |  | 50 | 2755.5
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 406.4 X 6.0 EFW IS3589 LS/SPIRA | IS3589-410MPA |  | M |  | 7.5 | 444.3
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA457.1X6.0EFW IS3589-410MPA(LS/SPI | IS3589-410MPA |  | M |  | 170 | 11342.4
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 94 | 6982.32
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 102 | 9115.536
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 EFW IS3589-410MPA-LS/SPIR | IS3589-410MPA |  | M |  | 107 | 14840.9
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP304H |  | NO |  | 7 | 14
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 8 | 1.2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 34 | 6.8
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 6.4
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 28 | 54.18
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. LR 45DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 16
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 144 | 547.2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 18 | 90
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 94 | 977.6
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 46 | 768.2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.92
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 24 | 399.84
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 33 | 786.06
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 4 | 71.36
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 10 | 457.9
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. UEQT NB150 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.752
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BW LR 60DEG ELL 219.1 X 8.18 SA234WPB | SA234WPB |  | NO |  | 4 | 56
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 6 | 1.2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 2 | 1.2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 14.4
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | RED NB 100/80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 19.8
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 17.94
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.68
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 2 | 2.52
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 16.32
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/323.9X6.35 | SA234WPB |  | NO |  | 7 | 120.75
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/323.9X6.35 | SA234WPB |  | NO |  | 2 | 47.18
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 3 | 48.45
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X9.53/355.6X9.53 | SA234WPB |  | NO |  | 4 | 144.52
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/406.4X6.35 | SA234WPB |  | NO |  | 2 | 50.94
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD168.3X7.11/114.3X6.02 | SA234WPB |  | NO |  | 2 | 6.32
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD 114.3X3.05 | SA403WP304H |  | NO |  | 1 | 2.94
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 1 | 0.4
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD219.1X6.35 | SA234WPB |  | NO |  | 6 | 115.62
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD168.3X7.11 | SA234WPB |  | NO |  | 2 | 26.56
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 4 | 13.16
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 4 | 243.12
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD457.2X9.53 | SA234WPB |  | NO |  | 2 | 229.54
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 5.94
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 107.2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD168.3X7.11/88.9X5.49 | SA234WPB |  | NO |  | 8 | 93.04
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD355.6X7.92/168.3X7.11 | SA234WPB |  | NO |  | 4 | 215.84
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/168.3X6.35 | SA234WPB |  | NO |  | 2 | 36.38
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 51.26
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT OD711.2X8 | As per drawing | 3-80-463-31357 | NO | A | 1
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=1200 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 166.44
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=750 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 104.025
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 508 X 6 | As per drawing | 3-80-463-A0817 | NO | A | 5
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 790.975
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA508X10 L=239 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 146.69
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 610 X 8 | As per drawing | 3-80-463-A0818 | NO | A | 6
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 908.496
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA610X10 L=298 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 264.432
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD610X6/323.9X6 | As per drawing | 3-80-463-A0820 | NO | A | 2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD610X10 L=600 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 177.552
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD323.9X8 L=186 00 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 23.174
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/355.6X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 5
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 964.7
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA355.6X8LS/SPIRAL IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 131.865
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/323.9 X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 1
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 166.63
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 323.9 X 8 IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 20.372
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB700/NB450 | As per drawing | 3-80-463-A0821 | NO | A | 5
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD711X10 IS 2062E250B | IS2062E250GRBR | 3-80-468-32127 | NO |  | 5 | 876.06
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 457X8 IS 3589 | IS3589-410MPA | 3-80-463-A0821 | NO |  | 5 | 98.765
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD508X6/OD457X6 | IS2062E250GRBR | 4-80-463-A0473 | NO |  | 4 | 197.192
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCER NB700/NB450 | IS2062E250GRBR | 4-80-463-A0474 | NO |  | 1 | 141.379
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD711.2/OD610 | IS2062E250GRBR | 4-80-463-A0475 | NO |  | 1 | 105.111
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD711.2X8/OD508X6 | IS2062E250GRBR | 4-80-463-A0478 | NO |  | 6 | 614.184
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD508X6/OD323.9X6 | IS2062E250GRBR | 4-80-463-A0479 | NO |  | 4 | 254.216
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ECC RED OD610X6/OD406.4X6 | IS2062E250GRBR | 3-80-463-A0819 | NO |  | 3 | 157.125
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 18 | 1369.44
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD457.2X9.53 | SA234WPB |  | NO |  | 8 | 604.24
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 4 | 152.08
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD508X9.53 | SA234WPB |  | NO |  | 20 | 1869.6
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 30°MITRE BEND Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0806 | NO |  | 3 | 85.344
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 711X8 (R=700) | IS2062E250GRBR | 3-80-463-A0807 | NO |  | 6 | 974.028
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 45DEG OD711.2X8 (R=700) | IS2062E250GRBR | 3-80-463-A0808 | NO |  | 2 | 162.024
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 60° OD 457 X 8 (R=686) | IS2062E250GRBR | 3-80-463-A0809 | NO |  | 2 | 133.93
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 610.0X8 (R=600) | IS2062E250GRBR | 3-80-463-A0810 | NO |  | 8 | 957.576
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | MITREBEND 45DEG Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0822 | NO |  | 2 | 85.66
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 100 | 18
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 100 | 43
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 50 CLASS 3000 | SA105 |  | NO |  | 100 | 133
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L45 | SA105 | 4-80-463-63321 | NO |  | 70 | 59.08
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L64 | SA105 | 4-80-463-23357 | NO |  | 70 | 176.96
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLUG RC 1" | SA105 | 4-80-463-23358 | NO |  | 140 | 70
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1"(NB80/50) | As per drawing | 3-80-460-28909 | NO | A | 40
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28909 | NO |  | 40 | 60.6
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK | 3-80-460-28909 | NO |  | 80 | 144
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 3-80-460-28909 | NO |  | 40 | 101.12
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 3-80-460-28909 | NO |  | 40 | 44.12
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1" (NB80/25) | As per drawing | 3-80-460-28907 | NO | A | 40
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28907 | NO |  | 40 | 60.6
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 144
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 24
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 4-80-463-23357 | NO |  | 40 | 101.12
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 4-80-463-23358 | NO |  | 40 | 44.12
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 308.5
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 38.7
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 70 | 207.9
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 5
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE NB15 IS1239 | IS1239 BLACK |  | M |  | 50 | 73.4
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 20 | 2.6
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 30 | 636
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1X 6.35 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 150 | 6262.5
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 62 | 5540.816
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 813 X 8 EFW-LS/SPIRAL IS3589-410MPA | IS3589-410MPA |  | M |  | 69 | 10957.2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 15 | 1114.2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 62.4
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 45DEG BEND NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 24
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 20 | 524
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 8 | 104.8
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=600) | IS3589-410MPA | 3-80-468-32248 | NO |  | 8 | 943.744
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=915) | IS2062E250GRBR | 3-80-463-A0833 | NO |  | 10 | 1780.38
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 30DEG MITRE BEND OD813X10 (R=800) | IS2062E250GRBR | 3-80-463-A0834 | NO |  | 2 | 174.898
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD813X9.53 | SA234WPB |  | NO |  | 3 | 1084.74
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD813X10 (R=800) | IS3589-410MPA | 3-80-463-27732 | NO |  | 9 | 2322.504
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 9.68
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 13.68
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BW RED 168.3X7.11/114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 8 | 32
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB350 | IS2062E250GRBR | 4-80-463-A0488 | NO |  | 6 | 375.684
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB250 | IS2062E250GRBR | 4-80-463-A0489 | NO |  | 4 | 234.112
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB800/NB600 | IS2062E250GRBR | 4-80-463-A0490 | NO |  | 3 | 275.715
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | RED NB800/NBXXX HOLD | IS1239 |  | NO |  | 4 | 0.02
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB500 | As per drawing | 3-80-463-A0829 | NO | A | 1
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=1000 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 122.696
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=427 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 52.36
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB600 | As per drawing | 3-80-463-A0828 | NO | A | 1
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X12 L=1200 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 212.138
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X10 L=515 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 76.145
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 8 | 214.4
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT NB500/NB350 | As per drawing | 3-80-463-A0830 | NO | A | 3
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD508X8 L=700 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 207.144
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD355.6X8 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 42.744
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/250 | As per drawing | 3-80-463-A0825 | NO | A | 1
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X10;L=900 | IS2062E250GRBR | 3-80-463-A0825 | NO |  | 1 | 133.058
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD273.1X6.0;L=222 | IS3589-410MPA | 3-80-463-A0825 | NO |  | 1 | 8.769
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/500 | As per drawing | 3-80-463-A0836 | NO | A | 1
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø610X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 118.221
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø508X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 50.947
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB800/600 | As per drawing | 3-80-463-A0826 | NO | A | 4
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1000 | IS2062E250GRBR | 3-80-463-A0826 | NO |  | 4 | 947.652
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X6;L=322 | IS3589-410MPA | 3-80-463-A0826 | NO |  | 4 | 115.104
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED EQUAL TEENB800 | As per drawing | 3-80-463-A0827 | NO | A | 1
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1200 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 284.296
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=394 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 93.352
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACED FLANGE NB 500 CLASS 150 | SA515GR70 | 4-80-468-65426 | NO |  | 3 | 162
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB500 | SA515GR70 | 4-80-463-A0484 | NO |  | 3 | 383.4
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | STUD M30 X 3.5 X 230 SA193B7 | SA193B7 |  | NO |  | 60 | 66.24
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M30 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 120 | 27.6
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACE FLANGE NB800 | IS2062E250GRBR | 3-80-468-27258 | NO |  | 2 | 196.2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB-800 | IS2062E250GRBR | 4-80-463-A0486 | NO |  | 2 | 507.46
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | STUD M36X4 - 290 SA193B7 | SA193B7 |  | NO |  | 56 | 112
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | HEX NUT M36 X 4 SA194GR2H | SA194GR2H |  | NO |  | 112 | 48.16
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 300 | 1851
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 77.4
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 150 | 385.8
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 20 | 3.2
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000 SA182F316 | SA182F316 |  | NO |  | 1 | 0.25
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 25 | 64.3
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 25 | 4
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000SA182F316 | SA182F316 |  | NO |  | 15 | 3.75
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 15 | 44.55
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
8 | APL Raipur 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW STUB NB25 CL3000 SA479TY316L | SA479TY316L |  | NO |  | 25 | 10.75
8 Total | [10 empty] | 281931.116
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | PIPE OD33.4X4.55 EP STY D D1-25.2 ATSITE | SA106GRB |  | M |  | 105 | 340.2
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 24 | 4.56
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 465 | 3478.2
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 74 | 66.6
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 209 | 677.16
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 88 | 16.72
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 4 | 5.6
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 3 | 14.79
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 7 | 2.87
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 75 | 561
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 17 | 15.3
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6AT SITE | SA106GRB |  | M |  | 145 | 833.17
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD48.3X5.08 | SA234WPB |  | NO |  | 30 | 14.4
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 180 | 450
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 25 | 3.75
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 30 | 97.2
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 5 | 0.95
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/48.3X5.54 | SA234WPB |  | NO |  | 1 | 0.51
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB50/40 CL3000 | SA105 |  | NO |  | 2 | 2
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 45 | 40.5
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6 ATSITE | SA106GRB |  | M |  | 40 | 229.84
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 1050 | 3402
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 162 | 30.78
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 3 | 2.58
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 2 | 0.74
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 2 | 2.8
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 16 | 6.88
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 3 | 0.36
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB25/10 | SA105 | 3-80-449-A0883 | NO |  | 10 | 0.4
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD60.3X5.54 SA234WPB | SA234WPB |  | NO |  | 1 | 0.33
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD48.3X3.68 SA234WPB | SA234WPB |  | NO |  | 1 | 0.17
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | SW B16.11 CAP OD33.4X4.55 SA105 | SA105 |  | NO |  | 1 | 0.005
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 10 | 3
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 10 | 32.4
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY DD1-49.5 AT SITE | SA106GRB |  | M |  | 70 | 523.6
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 14 | 12.6
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 10 | 14
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 45 | 145.8
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 60 | 150
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 12 | 1.8
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 4
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 5 | 1
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB15/10 | SA479TY304 | 3-80-449-A0883 | NO |  | 5 | 0.2
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 1000 | 3240
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 156 | 29.64
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 80 | 34.4
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 26 | 23.4
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 10 | 3.7
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 40 | 56
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 49.5
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 50 | 125
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 4 | 2
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 60.3X5.54 EPSTY D D1-49.5 ATSITE | SA106GRC |  | M |  | 50 | 374
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 8.9
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | EQT OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 0.05
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA21.3X2.77 EPATSITE STY-DD1=16.16 | SA312TP304H |  | M |  | 50 | 65
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 15 | 1.2
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD21.3X3.73EP ATSITE STY-D,D1=14.24 | SA106GRB |  | M |  | 300 | 486
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA 21.3X3.73EPATSITE STY-DD1=14.24 | SA312TP304H |  | M |  | 50 | 80.5
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 15 | 0.87
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB15X 3.2 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 100 | 145
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 4
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 25 | 36.5
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 10 | 1
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRB |  | M |  | 150 | 486
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 50 | 9.5
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 45 | 5.4
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRC |  | M |  | 110 | 356.4
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW LR 90DEG ELL 33.4X 4.55 SA234WPC | SA234WPC |  | NO |  | 40 | 0.2
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X6.35/21.3X4.55 | SA234WPC |  | NO |  | 40 | 6
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA33.4X3.38 EPATSITE STY-D,D1=27 | SA312TP304H |  | M |  | 50 | 125
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 20 | 3
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 20 | 4
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSY NB50(OP-40)&(OP-45) | As per drawing | 3-80-449-A0984 | NO | A | 4
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 L=210MM | SA106GRB | 3-80-449-A0984 | NO |  | 4 | 5.12
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø52.22 | SA240TP304 | 3-80-449-A0984 | NO |  | 4 | 0.64
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEMBLY NB25 (OP-46) | As per drawing | 3-80-449-A0985 | NO | A | 2
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 L=210MM | SA312TP316L | 3-80-449-A0985 | NO |  | 2 | 1.36
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø28.50 | SA240TP304 | 3-80-449-A0985 | NO |  | 2 | 0.086
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSY NB80(OP-51)&(OP-52) | As per drawing | 3-80-449-A0977 | NO | A | 4
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD88.9X7.42 L=210MM | SA106GRB | 3-80-449-A0977 | NO |  | 4 | 12.8
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø77.92 | SA240TP304 | 3-80-449-A0977 | NO |  | 4 | 1.408
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEY NB25(OP-47) | As per drawing | 3-80-449-A0981 | NO | A | 2
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X6.35 L=210MM | SA106GRC | 3-80-449-A0981 | NO |  | 2 | 1.78
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATET=10THK,Ø22.70 ORIFICEHOLE DIA10MM | SA240TP304 | 3-80-449-A0981 | NO |  | 2 | 0.05
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEY NB25(OP-38) | As per drawing | 3-80-452-A0965 | NO | A | 2
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X6.35 L=210MM | SA106GRB | 3-80-452-A0965 | NO |  | 2 | 1.592
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø23.80ORIFICE HOLE DIA10MM | SA240TP304 | 3-80-452-A0965 | NO |  | 2 | 0.056
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEMBLY NB25 (OP-53) | As per drawing | 3-80-449-A0981 | NO | A | 2
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X6.35 L=210MM | SA106GRB | 3-80-449-A0981 | NO |  | 2 | 1.78
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK, Ø2 2.70 ORIF HOL DIA10 | SA240TP304 | 3-80-449-A0981 | NO |  | 2 | 0.054
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 160 | 400
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 18 | 2.7
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X2.77 EP STY D D1-16.2 ATSITE | SA312TP304H |  | M |  | 160 | 208
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 20 | 1.6
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 2 | 0.8
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD21.3X2.77 | SA403WP304H |  | NO |  | 2 | 0.36
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE DIA 33.4X3.38EPSTYD D1=27.2(SITE) | SA106GRB |  | M |  | 110 | 275
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.14
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 300 | 750
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 26 | 3.9
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X3.73 EP D1-15.2 AT SITE | SA312TP304H |  | M |  | 10 | 16.1
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 5 | 0.29
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 60 | 154.32
9 | APL Raipur 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 6 | 0.96
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | PIPE OD33.4X4.55 EP STY D D1-25.2 ATSITE | SA106GRB |  | M |  | 105 | 340.2
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 24 | 4.56
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 465 | 3478.2
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 74 | 66.6
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 209 | 677.16
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 88 | 16.72
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 4 | 5.6
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 3 | 14.79
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 7 | 2.87
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 75 | 561
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 17 | 15.3
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6AT SITE | SA106GRB |  | M |  | 145 | 833.17
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD48.3X5.08 | SA234WPB |  | NO |  | 30 | 14.4
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 180 | 450
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 25 | 3.75
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 30 | 97.2
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 5 | 0.95
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/48.3X5.54 | SA234WPB |  | NO |  | 1 | 0.51
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB50/40 CL3000 | SA105 |  | NO |  | 2 | 2
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 45 | 40.5
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6 ATSITE | SA106GRB |  | M |  | 40 | 229.84
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 1050 | 3402
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 162 | 30.78
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 3 | 2.58
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 2 | 0.74
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 2 | 2.8
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 16 | 6.88
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 3 | 0.36
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB25/10 | SA105 | 3-80-449-A0883 | NO |  | 10 | 0.4
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD60.3X5.54 SA234WPB | SA234WPB |  | NO |  | 1 | 0.33
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD48.3X3.68 SA234WPB | SA234WPB |  | NO |  | 1 | 0.17
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | SW B16.11 CAP OD33.4X4.55 SA105 | SA105 |  | NO |  | 1 | 0.005
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 10 | 3
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 10 | 32.4
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY DD1-49.5 AT SITE | SA106GRB |  | M |  | 10 | 74.8
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 4 | 3.6
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 1 | 1.4
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 45 | 145.8
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 60 | 150
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 12 | 1.8
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 4
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 5 | 1
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB15/10 | SA479TY304 | 3-80-449-A0883 | NO |  | 5 | 0.2
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 1000 | 3240
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 156 | 29.64
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 80 | 34.4
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 26 | 23.4
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 10 | 3.7
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 40 | 56
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 49.5
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 50 | 125
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 4 | 2
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 60.3X5.54 EPSTY D D1-49.5 ATSITE | SA106GRC |  | M |  | 50 | 374
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 8.9
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | EQT OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 0.05
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA21.3X2.77 EPATSITE STY-DD1=16.16 | SA312TP304H |  | M |  | 50 | 65
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 15 | 1.2
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD21.3X3.73EP ATSITE STY-D,D1=14.24 | SA106GRB |  | M |  | 300 | 486
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA 21.3X3.73EPATSITE STY-DD1=14.24 | SA312TP304H |  | M |  | 50 | 80.5
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 15 | 0.87
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB15X 3.2 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 100 | 145
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 4
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 25 | 36.5
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 10 | 1
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRB |  | M |  | 150 | 486
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 50 | 9.5
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 45 | 5.4
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRC |  | M |  | 110 | 356.4
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW LR 90DEG ELL 33.4X 4.55 SA234WPC | SA234WPC |  | NO |  | 40 | 0.2
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X6.35/21.3X4.55 | SA234WPC |  | NO |  | 40 | 6
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA33.4X3.38 EPATSITE STY-D,D1=27 | SA312TP304H |  | M |  | 50 | 125
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 20 | 3
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 20 | 4
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 160 | 400
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 18 | 2.7
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X2.77 EP STY D D1-16.2 ATSITE | SA312TP304H |  | M |  | 160 | 208
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 20 | 1.6
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 2 | 0.8
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD21.3X2.77 | SA403WP304H |  | NO |  | 2 | 0.36
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE DIA 33.4X3.38EPSTYD D1=27.2(SITE) | SA106GRB |  | M |  | 110 | 275
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.14
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 300 | 750
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 26 | 3.9
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X3.73 EP D1-15.2 AT SITE | SA312TP304H |  | M |  | 10 | 16.1
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 5 | 0.29
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 60 | 154.32
9 | APL Raipur 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 6 | 0.96
9 Total | [10 empty] | 41640.756
Grand Total | [10 empty] | 945050.309
Note-
1. In case of Assembly items (indicated as 'A' under Assembly Indicator), exploded BOM will be indicated below the Assembly item. Weight of individual items of the Assembly shall be considered for arriving the final weight of the assembly. Individual drawings shall also be referred.
2. Bidders are required to thoroughly review the drawings before quoting.
3. in case of any mismatch between the Specification indicated against each item and corresponding Specification indicated in the drawing, Specification indicated in the drawing shall prevail.

## BOM- APL Raigarh 2x800 MW
Enquiry No 4202500017 dt 25.09.2025 Procurement of Low Pressure (LP) Piping for various Adani projects Annexure C- Detailed Piping System BOM (R01)
Schedule No | Project | Piping System | IBR / Non IBR | PGMA | Item Description | Specification | Drawing No | UOM | Assembly Indicator | Quantity | Weight (kg)
1 | APL Raigarh 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 33.4X4.55 EP AT SITE D1-25.2 | SA106GRB | 2-80-453-A0365 | M |  | 730 | 2365.2
1 | APL Raigarh 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRB | 2-80-453-A0365 | M |  | 30 | 224.4
1 | APL Raigarh 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRC | 2-80-453-A0365 | M |  | 300 | 2244
1 | APL Raigarh 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 21.3X3.73 EP AT SITE D1-14.5 | SA106GRB | 2-80-453-A0365 | M |  | 100 | 162
1 | APL Raigarh 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 100 | 38
1 | APL Raigarh 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 35 | 31.5
1 | APL Raigarh 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 34 | 10.2
1 | APL Raigarh 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 16 | 4.8
1 | APL Raigarh 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | SW END CAP NB50 CL3000 SA105 | SA105 | 2-80-453-A0365 | NO |  | 4 | 1
1 | APL Raigarh 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 33.4X4.55 EP AT SITE D1-25.2 | SA106GRB | 2-80-453-A0365 | M |  | 730 | 2365.2
1 | APL Raigarh 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRB | 2-80-453-A0365 | M |  | 30 | 224.4
1 | APL Raigarh 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRC | 2-80-453-A0365 | M |  | 300 | 2244
1 | APL Raigarh 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 21.3X3.73 EP AT SITE D1-14.5 | SA106GRB | 2-80-453-A0365 | M |  | 100 | 162
1 | APL Raigarh 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 100 | 38
1 | APL Raigarh 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 35 | 31.5
1 | APL Raigarh 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 34 | 10.2
1 | APL Raigarh 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 16 | 4.8
1 | APL Raigarh 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | SW END CAP NB50 CL3000 SA105 | SA105 | 2-80-453-A0365 | NO |  | 4 | 1
1 Total | [10 empty] | 10162.2
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (CS) | As per drawing | 3-80-418-38038 | NO | A | 130
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW | SA105 | 4-80-418-85267 | NO |  | 130 | 31.2
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA105 | 4-80-418-85269 | NO |  | 130 | 46.8
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA105 | 4-80-418-85270 | NO |  | 130 | 22.88
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TUBE 21.30 X 3.73 - SA106GRB | SA106GRB |  | M |  | 280 | 453.6
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | COND. LOOP (CS) | As per drawing | 3-80-999-99256 | NO | A | 10
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | LOOP CS OD21.3X4.78 L=700 | SA106GRC | 3-80-999-99256 | NO |  | 10 | 13.7
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA105 | 4-80-418-A0470 | NO |  | 130 | 26.52
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2" (PLAINXEXTTHRD)L=100MM | SA312TP316L | 4-80-418-A0517 | NO |  | 5 | 0.81
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 6 | 9.72
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | NO |  | 10 | 3.24
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2"-1/2"PLAIN X 1/2"NPT(M) | SA106GRB | 4-80-418-A0471 | NO |  | 10 | 1.62
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 10 | 2.56
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA182F316 | 4-80-418-A0518 | NO |  | 5 | 1.48
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (SS) | As per drawing | 3-80-418-A0856 | NO | A | 3
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2" NB-SW CL3000 | SA182F316 | 4-80-418-A0519 | NO |  | 3 | 0.888
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA182F316 | 4-80-418-A0520 | NO |  | 3 | 1.332
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA182F316 | 4-80-418-A0521 | NO |  | 3 | 0.651
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-50.4 | SA106GRB |  | M |  | 150 | 1122
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 27
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD33.4X4.55 EP STY D D1-25.2 AT SIT | SA106GRB |  | M |  | 165 | 534.6
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 30 | 5.7
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 60 | 22.8
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 5 | 8.25
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 10 | 4.3
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 1 | 1.4
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-49.0 | SA106GRB |  | M |  | 60 | 448.8
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 33.4 X 4.55 - SA106GRB | SA106GRB |  | M |  | 420 | 1360.8
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 21.3 X 3.73 - SA106GRB | SA106GRB |  | M |  | 240 | 388.8
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 25 | 22.5
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 120 | 45.6
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 35 | 10.5
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB50 CL3000 | SA105 |  | NO |  | 6 | 6
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 |  | NO |  | 45 | 13.5
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB50/25 CL3000 | SA105 |  | NO |  | 16 | 36
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 70 | 21
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 1/4"NPT/NB15 | SA105 |  | NO |  | 85 | 29.325
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 3/8"NPT/NB15 | SA105 |  | NO |  | 85 | 59.5
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 50 CL150 | SA515GR70 |  | NO |  | 2 | 4
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 25 CL150 | SA515GR70 |  | NO |  | 2 | 1.8
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT HEX GRA 8.8 M16X80 | IS:1364 (P-1) |  | NO |  | 4 | 0.62
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | HEX NUT M16 | IS:1364 (P-3) |  | NO |  | 4 | 0.12
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT-M12X70 -4.6-IS1364P1 | IS:1363 (P-1) |  | NO |  | 4 | 0.308
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NUT -M12 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 8 | 0.16
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD33.4X4.55 | SA515GR70 |  | NO |  | 30 | 4.14
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD60.3X5.54 | SA515GR70 | 3-80-709-99011 | NO |  | 2 | 0.8
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD114.3 X 6.02 SA106GRB | SA106GRB |  | M |  | 8 | 128.56
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 | SA234WPB |  | NO |  | 2 | 7.68
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 1 | 4.93
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE FOROD114.3X6.02 | SA515GR70 |  | NO |  | 1 | 2.19
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/40 CL3000 | SA105 |  | NO |  | 5 | 5
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/25 CL3000 | SA105 |  | NO |  | 8 | 8
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SW STUB NB15 CL 3000 | SA479TY304 |  | NO |  | 10 | 1.8
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (CS) | As per drawing | 3-80-418-38038 | NO | A | 25
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW | SA105 | 4-80-418-85267 | NO |  | 25 | 6
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA105 | 4-80-418-85269 | NO |  | 25 | 9
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA105 | 4-80-418-85270 | NO |  | 25 | 4.4
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TUBE 21.30 X 3.73 - SA106GRB | SA106GRB |  | M |  | 50 | 81
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | COND. LOOP (CS) | As per drawing | 3-80-999-99256 | NO | A | 25
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | LOOP CS OD21.3X4.78 L=700 | SA106GRC | 3-80-999-99256 | NO |  | 25 | 34.25
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA105 | 4-80-418-A0470 | NO |  | 25 | 5.1
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2" (PLAINXEXTTHRD)L=100MM | SA312TP316L | 4-80-418-A0517 | NO |  | 25 | 4.05
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 50 | 81
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | NO |  | 25 | 8.1
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2"-1/2"PLAIN X 1/2"NPT(M) | SA106GRB | 4-80-418-A0471 | NO |  | 25 | 4.05
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 25 | 4.9
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA182F316 | 4-80-418-A0518 | NO |  | 25 | 5.1
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (SS) | As per drawing | 3-80-418-A0856 | NO | A | 25
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2" NB-SW CL3000 | SA182F316 | 4-80-418-A0519 | NO |  | 25 | 7.4
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA182F316 | 4-80-418-A0520 | NO |  | 25 | 11.1
2 | APL Raigarh 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA182F316 | 4-80-418-A0521 | NO |  | 25 | 5.425
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (CS) | As per drawing | 3-80-418-38038 | NO | A | 130
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW | SA105 | 4-80-418-85267 | NO |  | 130 | 31.2
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA105 | 4-80-418-85269 | NO |  | 130 | 46.8
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA105 | 4-80-418-85270 | NO |  | 130 | 22.88
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TUBE 21.30 X 3.73 - SA106GRB | SA106GRB |  | M |  | 280 | 453.6
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | COND. LOOP (CS) | As per drawing | 3-80-999-99256 | NO | A | 10
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | LOOP CS OD21.3X4.78 L=700 | SA106GRC | 3-80-999-99256 | NO |  | 10 | 13.7
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA105 | 4-80-418-A0470 | NO |  | 130 | 26.52
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2" (PLAINXEXTTHRD)L=100MM | SA312TP316L | 4-80-418-A0517 | NO |  | 5 | 0.81
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 6 | 9.72
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | NO |  | 10 | 3.24
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2"-1/2"PLAIN X 1/2"NPT(M) | SA106GRB | 4-80-418-A0471 | NO |  | 10 | 1.62
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 10 | 2.56
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA182F316 | 4-80-418-A0518 | NO |  | 5 | 1.48
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (SS) | As per drawing | 3-80-418-A0856 | NO | A | 3
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2" NB-SW CL3000 | SA182F316 | 4-80-418-A0519 | NO |  | 3 | 0.888
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA182F316 | 4-80-418-A0520 | NO |  | 3 | 1.332
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA182F316 | 4-80-418-A0521 | NO |  | 3 | 0.651
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-50.4 | SA106GRB |  | M |  | 150 | 1122
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 27
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD33.4X4.55 EP STY D D1-25.2 AT SIT | SA106GRB |  | M |  | 165 | 534.6
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 30 | 5.7
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 60 | 22.8
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 5 | 8.25
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 10 | 4.3
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 1 | 1.4
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-49.0 | SA106GRB |  | M |  | 60 | 448.8
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 33.4 X 4.55 - SA106GRB | SA106GRB |  | M |  | 420 | 1360.8
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 21.3 X 3.73 - SA106GRB | SA106GRB |  | M |  | 240 | 388.8
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 25 | 22.5
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 120 | 45.6
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 35 | 10.5
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB50 CL3000 | SA105 |  | NO |  | 6 | 6
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 |  | NO |  | 45 | 13.5
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB50/25 CL3000 | SA105 |  | NO |  | 16 | 36
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 70 | 21
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 1/4"NPT/NB15 | SA105 |  | NO |  | 85 | 29.325
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 3/8"NPT/NB15 | SA105 |  | NO |  | 85 | 59.5
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 50 CL150 | SA515GR70 |  | NO |  | 2 | 4
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 25 CL150 | SA515GR70 |  | NO |  | 2 | 1.8
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT HEX GRA 8.8 M16X80 | IS:1364 (P-1) |  | NO |  | 4 | 0.62
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | HEX NUT M16 | IS:1364 (P-3) |  | NO |  | 4 | 0.12
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT-M12X70 -4.6-IS1364P1 | IS:1363 (P-1) |  | NO |  | 4 | 0.308
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NUT -M12 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 8 | 0.16
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD33.4X4.55 | SA515GR70 |  | NO |  | 30 | 4.14
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD60.3X5.54 | SA515GR70 | 3-80-709-99011 | NO |  | 2 | 0.8
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD114.3 X 6.02 SA106GRB | SA106GRB |  | M |  | 8 | 128.56
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 | SA234WPB |  | NO |  | 2 | 7.68
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 1 | 4.93
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE FOROD114.3X6.02 | SA515GR70 |  | NO |  | 1 | 2.19
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/40 CL3000 | SA105 |  | NO |  | 5 | 5
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/25 CL3000 | SA105 |  | NO |  | 8 | 8
2 | APL Raigarh 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SW STUB NB15 CL 3000 | SA479TY304 |  | NO |  | 10 | 1.8
2 Total | [10 empty] | 10207.843
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3762 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 32.357
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1733 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.906
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3644 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 31.342
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3079 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 26.482
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4807 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 41.345
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1662 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.295
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2728 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 23.464
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3978 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.215
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2539 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 21.838
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5201 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 44.734
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=298 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.563
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=326 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.804
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=104 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 0.895
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3339 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 28.719
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1739 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.957
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4942 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 42.506
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=892 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 7.672
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=171 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.471
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=562 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.834
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=699 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.012
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=782 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.726
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=780 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 5.178
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=268 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.779
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=3368 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 22.357
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=464 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.08
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=582 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.863
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=5178 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.372
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=673 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.467
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=151 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.002
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=1319 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 8.756
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 3 | 1.29
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 17 | 34
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 45DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 5 | 5.8
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BW EQUAL TEE OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 5.88
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.9BW UNEQT 114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 2.8
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1.75
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 1.54
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 0.56
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=3000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 25.803
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD88.9X3.05L=1000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.638
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X3.05L=2000 | SA312TP304H | 1-80-412-A0533 | NO |  | 1 | 12.92
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | BOTTOM PLATE 10THKX 1500X1500 | SA515GR70 | 1-80-412-A0533 | NO |  | 1 | 176.625
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1977 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 17.004
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD60.3X5.54 L=4000 | SA106GRB | 1-80-412-A0533 | NO |  | 1 | 29.924
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=264 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.271
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2672 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 22.982
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=360 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 3.096
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=242 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.081
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 50.66
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH CARRIER PLATES | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4382 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 37.69
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3039 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 26.138
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=192 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 1.651
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2938 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 25.27
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5544 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 47.684
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1001 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 8.61
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1583 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 13.615
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 8 | 16
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X5.49 L=2500 | SA106GRB | 2-80-412-A0362 | NO |  | 1 | 28.23
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 10MMX500X50010 | SA240TP304L | 2-80-412-A0362 | NO |  | 1 | 40.35
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=2000 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 17.202
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD168.3X3.4/114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 1 | 1.59
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 12MMX150X300 | SA515GR70 | 2-80-412-A0362 | NO |  | 1 | 4.239
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 230 | 591.56
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 50 | 8
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | BW UEQT 60.3X3.91/33.4X3.38 SA403WP316L | SA403WP316L |  | NO |  | 6 | 6.12
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25 SS | SA479TY304 |  | NO |  | 10 | 4.3
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | MULTI HOLE ORIFICE PLATE ASY(NB80)-OP43 | As per drawing | 3-80-412-A0952 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05 L=150MM | SA312TP316L | 3-80-412-A0952 | NO |  | 1 | 0.969
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE T=10THK, Ø84. 6 | SA240TP304 | 3-80-412-A0952 | NO |  | 1 | 0.37
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ORIFICE PLT NB80 (OP44) | As per drawing | 3-80-412-A0954 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05 L=150MM | SA312TP316L | 3-80-412-A0954 | NO |  | 1 | 0.969
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE T=10THK, Ø84.62 | SA240TP304 | 3-80-412-A0954 | NO |  | 1 | 0.37
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ORIFICE PLT NB100 (OP54)) | As per drawing | 3-80-412-A0955 | NO | A | 2
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 L=200MM SA312TP316L | SA312TP316L | 3-80-412-A0955 | NO |  | 2 | 3.44
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE T=12THK, Ø110.20 | SA240TP304 | 3-80-412-A0955 | NO |  | 2 | 1.39
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD60.3X5.54 EP STY D D1-50.4AT SITE | SA106GRB |  | M |  | 25 | 187
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 8 | 7.2
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-60.3X3.91 EP STY D D1-53.2AT SITE | SA312TP316L |  | M |  | 130 | 726.57
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 18 | 11.7
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 180 | 462.96
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 21 | 3.36
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | SW RED NB50/25 CL3000 SA182F316 | SA182F316 | 4-80-452-85266 | NO |  | 2 | 7.2
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L |  | NO |  | 2 | 3.5
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 60.3 X 3.91 EP STY D D1-53.2 | SA312TP304H |  | M |  | 50 | 272
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP304H |  | NO |  | 10 | 6.5
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 5 | 2.5
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 50 | 125
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD60.3X3.91/33.4X3.38 | SA403WP304L |  | NO |  | 5 | 5.1
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 65 | 923.845
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 14 | 69.58
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD168.3 X3.4 | SA403WP316L |  | NO |  | 2 | 13
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD168.3X3.4/88.9X3.05 | SA403WP316L |  | NO |  | 2 | 11.48
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 1 | 1.43
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 88.90 X 3.05 - SA312TP316L | SA312TP316L |  | M |  | 4 | 26.552
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L |  | NO |  | 2 | 2.32
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 RED OD168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 2 | 3.18
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | SOW FLANGE NB150 CL150 (RF) (SS316L) | SA182F316L |  | NO |  | 4 | 28
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 20 | 6.06
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | NUT -M20 -2H | BPS 41319 |  | NO |  | 40 | 2.6
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 75 | 1065.975
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 6 | 29.82
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 4 | 23.64
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 36 | 309.636
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 14 | 28
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD168.3X3.4/88.9X3.05 | SA403WP316L |  | NO |  | 1 | 5.74
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 1 | 1.43
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 88.90 X 3.05 - SA312TP316L | SA312TP316L |  | M |  | 4 | 26.552
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L |  | NO |  | 2 | 2.32
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 88.90 X 3.05 - SA312TP316L | SA312TP316L |  | M |  | 45 | 298.71
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L |  | NO |  | 10 | 11.6
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD88.9X3.05 | SA403WP316L |  | NO |  | 2 | 3.76
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD273.1 X 4.19 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 26 | 742.352
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD273.1X4.19 | SA403WP316L |  | NO |  | 2 | 33.26
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW EQT OD273.0X4.19 SA403WP316L | SA403WP316L |  | NO |  | 2 | 37.2
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW UEQT 273X4.19/219.1X3.76 SA403WP316L | SA403WP316L |  | NO |  | 2 | 36.328
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE D219.1 X 3.76 X6000 - SA312TP316L | SA312TP316L |  | M |  | 14 | 287.35
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X3.76 | SA403WP316L |  | NO |  | 2 | 19.14
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ECC RED219.1X3.76/168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 2 | 5.6
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 27 | 383.751
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 6 | 29.82
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 273.1X4.19/168.3X3.4 | SA403WP316L |  | NO |  | 4 | 69.76
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 ECCRED OD168.3X3.4/141.3X3.4 | SA403WP316L |  | NO |  | 4 | 7.16
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD141.3X3.4 L=6000 SA312TP316L | SA312TP316L |  | M |  | 6 | 69.222
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | 90 DEG LR ELBOW OD 141.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 4 | 15.2
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD273X4.19 SA403WP316L | SA403WP316L |  | NO |  | 2 | 8.12
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW SR 90DEG ELL OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 2 | 2
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 284.26
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 4 | 19.88
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 172.02
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 4 | 8
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L |  | NO |  | 50 | 21.5
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | SW STUB NB15 SS | SA182F316 | 4-80-473-A0623 | NO |  | 30 | 5.4
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 33.4 X 4.55SA312TP316L | SA312TP316L |  | M |  | 45 | 145.8
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 5 | 8.1
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA403WP316L |  | NO |  | 28 | 5.32
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 60.3 X 3.91 SA312TP316L | SA312TP316L |  | M |  | 20 | 111.78
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | SW STUB NB 50 SS CL:3000-SA182F316 | SA182F316 |  | NO |  | 5 | 4.6
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X6000 - SA312TP316L | SA312TP316L |  | M |  | 270 | 3837.51
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 12 | 59.64
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD168.3 X3.4 | SA403WP316L |  | NO |  | 2 | 13
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 2 | 11.82
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 172.02
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 6 | 12
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD 273.00 X 6.35 X 6000 - SA106GRB | SA106GRB |  | M |  | 270 | 11275.2
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 14 | 366.8
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 2 | 58.22
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 10 | 4.3
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | M |  | 25 | 81
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 18 | 3.42
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | FLAT END CLOSURE OD273X6.35 | SA515GR70 |  | NO |  | 2 | 34.92
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X6000 - SA312TP316L | SA312TP316L |  | M |  | 250 | 3553.25
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 12 | 59.64
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 2 | 11.82
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 172.02
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 4 | 8
3 | APL Raigarh 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 2 | 2.86
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3762 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 32.357
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1733 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.906
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3644 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 31.342
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3079 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 26.482
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4807 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 41.345
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1662 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.295
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2728 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 23.464
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3978 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.215
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2539 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 21.838
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5201 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 44.734
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=298 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.563
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=326 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.804
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=104 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 0.895
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3339 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 28.719
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1739 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.957
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4942 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 42.506
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=892 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 7.672
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=171 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.471
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=562 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.834
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=699 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.012
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=782 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.726
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=780 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 5.178
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=268 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.779
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=3368 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 22.357
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=464 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.08
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=582 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.863
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=5178 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.372
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=673 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.467
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=151 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.002
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=1319 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 8.756
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 3 | 1.29
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 17 | 34
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 45DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 5 | 5.8
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BW EQUAL TEE OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 5.88
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.9BW UNEQT 114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 2.8
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1.75
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 1.54
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 0.56
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=3000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 25.803
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD88.9X3.05L=1000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.638
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X3.05L=2000 | SA312TP304H | 1-80-412-A0533 | NO |  | 1 | 12.92
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | BOTTOM PLATE 10THKX 1500X1500 | SA515GR70 | 1-80-412-A0533 | NO |  | 1 | 176.625
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1977 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 17.004
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD60.3X5.54 L=4000 | SA106GRB | 1-80-412-A0533 | NO |  | 1 | 29.924
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=264 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.271
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2672 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 22.982
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=360 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 3.096
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=242 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.081
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 50.66
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH CARRIER PLATES | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4382 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 37.69
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3039 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 26.138
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=192 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 1.651
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2938 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 25.27
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5544 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 47.684
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1001 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 8.61
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1583 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 13.615
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 8 | 16
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X5.49 L=2500 | SA106GRB | 2-80-412-A0362 | NO |  | 1 | 28.23
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 10MMX500X50010 | SA240TP304L | 2-80-412-A0362 | NO |  | 1 | 40.35
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=2000 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 17.202
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD168.3X3.4/114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 1 | 1.59
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 12MMX150X300 | SA515GR70 | 2-80-412-A0362 | NO |  | 1 | 4.239
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 230 | 591.56
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 50 | 8
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | BW UEQT 60.3X3.91/33.4X3.38 SA403WP316L | SA403WP316L |  | NO |  | 6 | 6.12
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25 SS | SA479TY304 |  | NO |  | 10 | 4.3
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD60.3X5.54 EP STY D D1-50.4AT SITE | SA106GRB |  | M |  | 25 | 187
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 8 | 7.2
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-60.3X3.91 EP STY D D1-53.2AT SITE | SA312TP316L |  | M |  | 130 | 726.57
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 18 | 11.7
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 180 | 462.96
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 21 | 3.36
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | SW RED NB50/25 CL3000 SA182F316 | SA182F316 | 4-80-452-85266 | NO |  | 2 | 7.2
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L |  | NO |  | 2 | 3.5
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 60.3 X 3.91 EP STY D D1-53.2 | SA312TP304H |  | M |  | 50 | 272
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP304H |  | NO |  | 10 | 6.5
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 5 | 2.5
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 50 | 125
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
3 | APL Raigarh 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD60.3X3.91/33.4X3.38 | SA403WP304L |  | NO |  | 5 | 5.1
3 Total | [10 empty] | 34697.769
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1016 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 807.859
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PLATE 2500X2500X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 1 | 785
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT PIPE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=208 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 165.415
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=698 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 555.018
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 30DEG OD2032X16(R=0.75D)L=819 | SA515GR70 | 3-80-363-31709 | NO |  | 1 | 651.236
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 90DEG (R=0.75D) L=2457 | SA515GR70 | 3-80-363-31710 | NO |  | 2 | 3907.416
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | IMPULSE PIPE OD21.3X3.73 L=2750 | SA106GRB | 1-80-363-A0539 | NO |  | 4 | 17.82
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SPARE PIPE OD323.9X9.53 L=1000 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 73.88
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BLIND FLANGE ASSY. NB500 CL150 | SA515GR70 | 3-80-362-11781 | NO |  | 2 | 252
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STUD M30X200 | SA193B16 | 1-80-363-A0539 | NO |  | 44 | 37.4
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | HEX. NUT M30 | A194GR2H | 1-80-363-A0539 | NO |  | 88 | 20.24
4 | APL Raigarh 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | GASKET, T=3 800X8 00 | NON-ASBESTOS | 1-80-363-A0539 | NO |  | 2 | 7.284
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1016 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 807.859
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PLATE 2500X2500X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 1 | 785
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT PIPE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=208 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 165.415
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=698 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 555.018
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 30DEG OD2032X16(R=0.75D)L=819 | SA515GR70 | 3-80-363-31709 | NO |  | 1 | 651.236
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 90DEG (R=0.75D) L=2457 | SA515GR70 | 3-80-363-31710 | NO |  | 2 | 3907.416
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | IMPULSE PIPE OD21.3X3.73 L=2750 | SA106GRB | 1-80-363-A0539 | NO |  | 4 | 17.82
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SPARE PIPE OD323.9X9.53 L=1000 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 73.88
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BLIND FLANGE ASSY. NB500 CL150 | SA515GR70 | 3-80-362-11781 | NO |  | 2 | 252
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STUD M30X200 | SA193B16 | 1-80-363-A0539 | NO |  | 44 | 37.4
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | HEX. NUT M30 | A194GR2H | 1-80-363-A0539 | NO |  | 88 | 20.24
4 | APL Raigarh 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | GASKET, T=3 800X8 00 | NON-ASBESTOS | 1-80-363-A0539 | NO |  | 2 | 7.284
4 Total | [10 empty] | 51105.628
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | PIPE OD 273.00 X 6.35 X 6000 - SA106GRB | SA106GRB |  | M |  | 90 | 3758.4
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 14 | 366.8
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 1 | 29.11
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 5 | 2.15
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | M |  | 6 | 19.44
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 4 | 0.76
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | PIPE OD33.4X4.55 EP AT SITE 'D' D1=25.2 | SA106GRB |  | M |  | 280 | 907.2
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | PIPE OD60.3X5.54 EP AT SITE 'D' D1=49 | SA106GRB |  | M |  | 75 | 561
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | PIPE OD114.3X6.02EP AT SHOP 'D'D1=103.5 | SA106GRB |  | M |  | 950 | 15266.5
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | PIPE OD168.3X7.11EP AT SHOP 'D'D1=154.1 | SA106GRB |  | M |  | 50 | 1413
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 | SA234WPB |  | NO |  | 65 | 249.6
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X7.11 | SA234WPB |  | NO |  | 15 | 156
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 RED OD168.3X7.11/114.3X6.02 | SA234WPB |  | NO |  | 2 | 6.32
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | SW STUB NB25 CLASS 3000 | SA105 | 3-80-463-15996 | NO |  | 25 | 10.75
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 10 | 9
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 40 | 15.2
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 RED OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 2.82
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 3 | 4.95
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 1 | 1.4
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 UEQT OD168.3X7.11/114.3X6.02 | SA234WPB |  | NO |  | 2 | 24.04
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 88.9X5.49 EPD-79.0 AT SHOP | SA106GRB |  | M |  | 580 | 6554
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 - EP-D24.7(SITE L=40M | SA106GRB |  | M |  | 40 | 129.6
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD60.3X5.54 L=35M EP STY-D49.3(SITE | SA106GRB |  | M |  | 35 | 261.835
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 134 | 270.68
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 45DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 14 | 14.14
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 12 | 10.8
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 21 | 69.09
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 UEQT OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 14.85
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 4.3
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/48.3X5.08 | SA234WPB |  | NO |  | 5 | 3.85
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 15 | 2.85
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 EPSTY-D D1=24.7(SITE) | SA106GRB |  | M |  | 25 | 81
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 40 | 17.2
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NB50 OILHOSEASPERIS635 L=15 M WITH END | Rubber Hose |  | NO |  | 2 | 50
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT END CLOSURE OD88.9X5.49 | SA515GR70 |  | NO |  | 8 | 8.32
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT FACED FLANGE NB80 CL 150 SA105 | SA515GR70 | 4-80-340-73230 | NO |  | 4 | 36
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | STUD M16 X 2 X 160 SA193B7 | SA193B7 |  | NO |  | 10 | 2.24
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NUT -M16 -2H | A194GR2H |  | NO |  | 20 | 0.6
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 15 | 2.7
5 | APL Raigarh 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 21.3 X 4.78 L=10M | SA106GRB |  | M |  | 10 | 19.5
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 88.9X5.49 EPD-79.0 AT SHOP | SA106GRB |  | M |  | 580 | 6554
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 - EP-D24.7(SITE L=40M | SA106GRB |  | M |  | 40 | 129.6
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD60.3X5.54 L=35M EP STY-D49.3(SITE | SA106GRB |  | M |  | 35 | 261.835
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 134 | 270.68
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 45DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 14 | 14.14
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 12 | 10.8
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 21 | 69.09
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 UEQT OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 14.85
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 4.3
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/48.3X5.08 | SA234WPB |  | NO |  | 5 | 3.85
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 15 | 2.85
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 EPSTY-D D1=24.7(SITE) | SA106GRB |  | M |  | 25 | 81
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 40 | 17.2
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NB50 OILHOSEASPERIS635 L=15 M WITH END | Rubber Hose |  | NO |  | 2 | 50
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT END CLOSURE OD88.9X5.49 | SA515GR70 |  | NO |  | 8 | 8.32
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT FACED FLANGE NB80 CL 150 SA105 | SA515GR70 | 4-80-340-73230 | NO |  | 4 | 36
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | STUD M16 X 2 X 160 SA193B7 | SA193B7 |  | NO |  | 10 | 2.24
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NUT -M16 -2H | A194GR2H |  | NO |  | 20 | 0.6
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 15 | 2.7
5 | APL Raigarh 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 21.3 X 4.78 L=10M | SA106GRB |  | M |  | 10 | 19.5
5 Total | [10 empty] | 37919.15
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 90 | 561.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 120 | 358.8
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 7
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 15.25
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 2
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 24
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 1
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 220 | 1372.8
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 27.45
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 3
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB 50/40 IS1239 | IS1239 G&T |  | NO |  | 2 | 3.4
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 12 | 53.64
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 40 | 119.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 1.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 19.2
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 70 | 35
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 40 | 12
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 40 | 60
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 25 | 74.75
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 1.2
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 19.2
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 3
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 525 | 7717.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 360
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 45DEG BEND NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 28
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 48
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/150 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/100 G&T | As per drawing | 2-80-614-A0308 | NO | A | 4
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 4 | 40.284
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 4 | 8.984
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 27.879
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 30
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 22 | 88
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 4 | 41.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 10 | 28
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 299
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 45 | 9
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 54
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 42.155
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 130 | 169
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 98 | 410.13
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 180 | 40.32
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 40 | 18.72
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/25 | As per drawing | 2-80-616-10294 | NO | A | 5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/15 | As per drawing | 2-80-616-10294 | NO | A | 10
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB200 IS1239 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB200 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 60 | 179.4
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 120 | 24
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | EQTEE NB25 IS1239 GAL | IS1239 G&T |  | NO |  | 60 | 0.3
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 60 | 24
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 60 | 87.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 60 | 6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/25 | As per drawing | 2-80-614-A0308 | NO | A | 8
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 8 | 53.712
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 8 | 1.52
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 52 | 156
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 42.155
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 358 | 2233.92
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1575 | 4709.25
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 125 | 182.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 36 | 3.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 210 | 42
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 53.375
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 36 | 5.76
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 9
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 18 | 7.2
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 80
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 10 | 23
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 40 | 5.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | NUT -M16 -2H | A194GR2H |  | NO |  | 80 | 2.4
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 10 | 10
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 100 | 50
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 400 | 120
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 75 | 112.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 150
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 50 | 25
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 30 | 3
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 25 | 7.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 2
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB25 IS1239 GAL L=75MM | IS1239 G&T | 3-80-612-21071 | NO |  | 34 | 7.616
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 30 | 9
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SCREWED NIPPLE NB40 IS1239 | IS1239 G&T | 3-80-612-21072 | NO |  | 4 | 2.68
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 40 IS1239 | IS1239 G&T |  | NO |  | 15 | 12
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 250 | 5475
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 685 | 4274.4
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1405 | 4200.95
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 3335 | 4869.1
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 10 | 360
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 25 | 260
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 92 | 140.3
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 230 | 46
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 1020 | 102
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 27.25
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 9.504
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 0.8
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 4
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 108
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 295.085
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150/15 | As per drawing | 2-80-616-06449 | NO | A | 10
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4 L=200 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 42.4
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 L=65.4 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 0.94
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 60 | 72
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 365 | 146
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 32 | 16
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 10
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 4
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD NB50X4.5 | IS1239 BLACK | 4-80-612-50147 | NO |  | 50 | 46.25
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | SOCKET NB200 (GALVANISED) | IS3589-410MPA G&T | 4-80-616-71901 | NO |  | 25 | 157.65
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 65 | 97.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 175 | 87.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 360 | 108
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 840 | 84
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 200 IS1239 | IS1239 G&T |  | NO |  | 17 | 102
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 150 IS1239 | IS1239 G&T |  | NO |  | 45 | 441
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 120 | 180
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 25 IS1239 | IS1239 G&T |  | NO |  | 240 | 120
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 560 | 168
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB50 IS1239 L=150 | IS1239 G&T | 3-80-612-21073 | NO |  | 50 | 46.25
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB25 IS1239 L=150 | IS1239 G&T | 3-80-612-21071 | NO |  | 200 | 89.2
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB15 IS1239 L=150 | IS1239 G&T | 3-80-612-21070 | NO |  | 450 | 98.1
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25 WITH THREAD 1"BSP(M) | SA106GRB | 4-80-612-82549 | NO |  | 2 | 0.648
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 40 | 10.24
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD ISO7 RC-1-1/2"(F)(GAL) | SA105 (Galvanized) | 4-80-612-A0578 | NO |  | 65 | 91
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 525 | 7717.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 360
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 45DEG BEND NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 28
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB100 IS1239G&T | IS1239 G&T |  | NO |  | 12 | 72
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | UEQT 200/100 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 3
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 3 | 30.213
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 3 | 6.738
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 60
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 5 | 14
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/150 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 41.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 50 | 149.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/25 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 60
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/15 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 10
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB200 IS3589 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB200 IS3589 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 128 | 166.4
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 95 | 397.575
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 150 | 33.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 24 | 11.232
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB150 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 4 | 78.776
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB100 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 8 | 83.056
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | STUD M16 X 2 X 110 SA193B7 | SA193B7 |  | NO |  | 64 | 9.28
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 128 | 3.84
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 32 | 9.696
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M20 -2H | BPS 41319 |  | NO |  | 64 | 4.16
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 925 | 1350.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1640 | 4903.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 447
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 240 | 1497.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 86 | 13.76
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 58 | 29
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 218 | 87.2
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 7.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 20 | 24
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 341 | 34.1
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 418 | 83.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 53 | 80.825
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 2 | 4.6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 8 | 1.12
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 16 | 0.48
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 2 | 2
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB25 CL150- G&T | IS2062 |  | NO |  | 60 | 0.3
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 240 | 19.2
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 480 | 12
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB25CL150(GALV) | SA105 (Galvanized) |  | NO |  | 60 | 60
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB15 CL150- G&T | IS2062 |  | NO |  | 50 | 0.25
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 200 | 16
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 400 | 10
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB15 CL150(GALV | IS2062 |  | NO |  | 50 | 45
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 70 | 35
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 420 | 126
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 50 | 75
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 330 | 165
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 15 | 7.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 230 | 23
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 180 | 54
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB15 IS1239G&T | IS1239 G&T |  | NO |  | 50 | 5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 12
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 40 IS1239 | IS1239 G&T |  | NO |  | 20 | 16
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB 40 IS1239 | IS1239 G&T |  | NO |  | 12 | 4.8
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 200 | 2940
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB50X4.5 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 525 | 3276
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB25X4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 2200 | 6578
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 5850 | 8541
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 8 | 288
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 80
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 76.25
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 420 | 84
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1250 | 125
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 75 | 22.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB 200/100 IS1239 G&T | As per drawing | 2-80-616-10294 | NO | A | 2
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.0 L=300 | IS3589-410MPA | 2-80-616-10294 | NO |  | 2 | 18.918
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-616-10294 | NO |  | 2 | 4.492
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 1 | 6
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/50 IS1239 G&T | IS1239 G&T |  | NO |  | 13 | 52
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 140
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 12
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 48
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/15 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 108
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 20
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB25/15 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 120
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 50 IS1239 G7T | IS1239 G&T |  | NO |  | 10 | 5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 15 IS1239 G&T | IS1239 G&T |  | NO |  | 200 | 20
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB50X4.05 | IS1239 BLACK | 4-80-612-50147 | NO |  | 40 | 37
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB25X3.25 | IS1239 BLACK | 4-80-612-50147 | NO |  | 250 | 111.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB15X4.50 | IS1239 BLACK | 4-80-612-50147 | NO |  | 650 | 141.7
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 65
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 135 | 67.5
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB25 IS1329 G&T | IS1239 G&T |  | NO |  | 550 | 165
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1470 | 147
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 146.475
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 135
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 370 | 185
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 980 | 294
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0575 | NO |  | 10 | 6.17
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0574 | NO |  | 100 | 29.7
6 | APL Raigarh 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1/2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0573 | NO |  | 650 | 94.25
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 90 | 561.6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 120 | 358.8
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 7
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 15.25
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 2
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 24
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 1
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 170 | 1060.8
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 14 | 21.35
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 3
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB 50/40 IS1239 | IS1239 G&T |  | NO |  | 2 | 3.4
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 12 | 53.64
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 40 | 119.6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 1.6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 19.2
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 60 | 30
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 35 | 10.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 32 | 48
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 12.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 18 | 53.82
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 1.2
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 16
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 3
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 585 | 8599.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 98 | 392
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 45DEG BEND NB100IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 42
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 48
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/150 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/100 G&T | As per drawing | 2-80-614-A0308 | NO | A | 4
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 4 | 40.284
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 4 | 8.984
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 27.879
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 30
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 22 | 88
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 4 | 41.6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 10 | 28
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 299
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 45 | 9
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 54
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 42.155
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 130 | 169
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 98 | 410.13
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 180 | 40.32
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 40 | 18.72
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/25 | As per drawing | 2-80-616-10294 | NO | A | 5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/15 | As per drawing | 2-80-616-10294 | NO | A | 10
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB200 IS1239 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB200 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 358 | 2233.92
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1575 | 4709.25
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 125 | 182.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 36 | 3.6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 210 | 42
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 53.375
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 36 | 5.76
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 9
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 18 | 7.2
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 80
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 10 | 23
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 40 | 5.6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | NUT -M16 -2H | A194GR2H |  | NO |  | 80 | 2.4
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 10 | 10
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 100 | 50
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 400 | 120
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 75 | 112.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 150
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 25 | 12.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 30 | 3
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 25 | 7.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB15 IS1239G&T | IS1239 G&T |  | NO |  | 10 | 1
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 250 | 5475
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 685 | 4274.4
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1405 | 4200.95
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 3335 | 4869.1
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 10 | 360
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 25 | 260
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 92 | 140.3
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 230 | 46
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 1020 | 102
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 27.25
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 9.504
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 0.8
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 4
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 108
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 295.085
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150/15 | As per drawing | 2-80-616-06449 | NO | A | 10
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4 L=200 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 42.4
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 L=65.4 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 0.94
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 60 | 72
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 365 | 146
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 32 | 16
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 10
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 4
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD NB50X4.5 | IS1239 BLACK | 4-80-612-50147 | NO |  | 50 | 46.25
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | SOCKET NB200 (GALVANISED) | IS3589-410MPA G&T | 4-80-616-71901 | NO |  | 25 | 157.65
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 65 | 97.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 175 | 87.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 360 | 108
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 840 | 84
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 200 IS1239 | IS1239 G&T |  | NO |  | 17 | 102
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 150 IS1239 | IS1239 G&T |  | NO |  | 45 | 441
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 120 | 180
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 25 IS1239 | IS1239 G&T |  | NO |  | 240 | 120
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 560 | 168
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB50 IS1239 L=150 | IS1239 G&T | 3-80-612-21073 | NO |  | 50 | 46.25
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB25 IS1239 L=150 | IS1239 G&T | 3-80-612-21071 | NO |  | 200 | 89.2
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB15 IS1239 L=150 | IS1239 G&T | 3-80-612-21070 | NO |  | 450 | 98.1
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25 WITH THREAD 1"BSP(M) | SA106GRB | 4-80-612-82549 | NO |  | 2 | 0.648
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 40 | 10.24
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD ISO7 RC-1-1/2"(F)(GAL) | SA105 (Galvanized) | 4-80-612-A0578 | NO |  | 65 | 91
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 580 | 8526
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 100 | 400
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 45DEG BEND NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 28
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB100 IS1239G&T | IS1239 G&T |  | NO |  | 15 | 90
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | UEQT 200/100 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 3
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 3 | 30.213
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 3 | 6.738
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 60
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 5 | 14
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/150 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 41.6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 50 | 149.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/25 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 60
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/15 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 10
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB200 IS3589 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB200 IS3589 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 128 | 166.4
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 95 | 397.575
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 150 | 33.6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 24 | 11.232
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB150 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 4 | 78.776
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB100 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 8 | 83.056
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | STUD M16 X 2 X 110 SA193B7 | SA193B7 |  | NO |  | 64 | 9.28
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 128 | 3.84
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 32 | 9.696
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M20 -2H | BPS 41319 |  | NO |  | 64 | 4.16
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 925 | 1350.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1640 | 4903.6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 447
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 240 | 1497.6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 86 | 13.76
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 58 | 29
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 218 | 87.2
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 7.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 20 | 24
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 341 | 34.1
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 418 | 83.6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 53 | 80.825
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 2 | 4.6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 8 | 1.12
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 16 | 0.48
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 2 | 2
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB25 CL150- G&T | IS2062 |  | NO |  | 60 | 0.3
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 240 | 19.2
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 480 | 12
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB25CL150(GALV) | SA105 (Galvanized) |  | NO |  | 60 | 60
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB15 CL150- G&T | IS2062 |  | NO |  | 50 | 0.25
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 200 | 16
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 400 | 10
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB15 CL150(GALV | IS2062 |  | NO |  | 50 | 45
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 70 | 35
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 420 | 126
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 50 | 75
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 330 | 165
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 15 | 7.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 230 | 23
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 180 | 54
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB15 IS1239G&T | IS1239 G&T |  | NO |  | 50 | 5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 12
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 40 IS1239 | IS1239 G&T |  | NO |  | 20 | 16
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB 40 IS1239 | IS1239 G&T |  | NO |  | 12 | 4.8
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 200 | 2940
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB50X4.5 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 525 | 3276
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB25X4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 2200 | 6578
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 5850 | 8541
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 8 | 288
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 80
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 76.25
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 420 | 84
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1250 | 125
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 75 | 22.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB 200/100 IS1239 G&T | As per drawing | 2-80-616-10294 | NO | A | 2
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.0 L=300 | IS3589-410MPA | 2-80-616-10294 | NO |  | 2 | 18.918
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-616-10294 | NO |  | 2 | 4.492
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 1 | 6
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/50 IS1239 G&T | IS1239 G&T |  | NO |  | 13 | 52
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 140
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 12
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 48
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/15 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 108
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 20
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB25/15 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 120
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 50 IS1239 G7T | IS1239 G&T |  | NO |  | 10 | 5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 15 IS1239 G&T | IS1239 G&T |  | NO |  | 200 | 20
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB50X4.05 | IS1239 BLACK | 4-80-612-50147 | NO |  | 40 | 37
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB25X3.25 | IS1239 BLACK | 4-80-612-50147 | NO |  | 250 | 111.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB15X4.50 | IS1239 BLACK | 4-80-612-50147 | NO |  | 650 | 141.7
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 65
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 135 | 67.5
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB25 IS1329 G&T | IS1239 G&T |  | NO |  | 550 | 165
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1470 | 147
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 146.475
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 135
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 370 | 185
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 980 | 294
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0575 | NO |  | 10 | 6.17
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0574 | NO |  | 100 | 29.7
6 | APL Raigarh 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1/2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0573 | NO |  | 650 | 94.25
6 Total | [10 empty] | 205766.833
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 323.9X6.4 EP STY D D1-311.2 | IS3589-410MPA |  | M |  | 20 | 1001
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 273.1 X 6.4 EP STY D-D1 260.3 | IS3589-410MPA |  | M |  | 65 | 2735.85
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 219.1 X 6.4 EP STY D-D1 206.3 | IS3589-410MPA |  | M |  | 300 | 10071
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB150X5.4 EP STY D-D1-156.8 | IS1239 BLACK |  | M |  | 640 | 13568
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB100X5.4 EP STY D-D1-105.3 | IS1239 BLACK |  | M |  | 140 | 2016
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB80X4.8 EP STY D-D1-80.8 | IS1239 BLACK |  | M |  | 920 | 9292
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB50X4.5 EP STY D-D1-52.7 | IS1239 BLACK |  | M |  | 400 | 2468
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB40X 4.0 EP STY D-D1-41.5 | IS1239 BLACK |  | M |  | 310 | 1373.3
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB25X4.0 EP STY D-D1-26.9 | IS1239 BLACK |  | M |  | 725 | 2153.25
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB15X 3.2 EP STY D-D1-15.9 | IS1239 BLACK |  | M |  | 680 | 986
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 12 | 200.4
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 10 | 262
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 208
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 150
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 280.8
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 116.1
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 30
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 24
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 140 | 14
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 6 | 214.2
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 11
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 33
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 18
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 3.6
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 10.5
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD273X6.35/88.9X5.49 | SA234WPB |  | NO |  | 4 | 101.28
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 12 | 180
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 58
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 65 | 104
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 16.5
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 24
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 24
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 93.75
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 33
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 13.5
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 17.5
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 85 | 25.5
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 1
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 5
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 4 | 20
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 18
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | UEQT NB 150/100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 31
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/88.9X5.49 | SA234WPB |  | NO |  | 8 | 135.04
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD168.3X7.11/60.3X5.54 | SA234WPB |  | NO |  | 10 | 113.9
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 9
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 10
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 18
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 2.5
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 3 | 0.6
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 1.5
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/50) | As per drawing | 3-80-999-97670 | NO |  | 15 | 99.375
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/40) | As per drawing | 3-80-999-97669 | NO |  | 18 | 119.25
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/25) | As per drawing | 3-80-999-97668 | NO |  | 30 | 216.75
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/15) | As per drawing | 3-80-999-97667 | NO |  | 5 | 36.125
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB15 CL3000 | SA105 |  | NO |  | 130 | 23.4
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB25 CL3000 | SA105 |  | NO |  | 50 | 21.5
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB40 CL3000 | SA105 |  | NO |  | 25 | 18.75
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB50 CL3000 | SA105 |  | NO |  | 30 | 39.9
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=45 | SA105 |  | NO |  | 10 | 5
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=64 | SA105 |  | NO |  | 120 | 84
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB15 | SA106GRB | 3-80-463-27244 | NO |  | 430 | 104.49
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB25 | IS1239 BLACK | 3-80-463-27244 | NO |  | 95 | 42.37
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB40 | IS1239 BLACK | 3-80-463-27244 | NO |  | 18 | 11.952
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB50 | IS1239 BLACK | 3-80-463-27244 | NO |  | 64 | 59.2
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PLUG FOR THERMO COUPLE NIPPLE M33X2 (CS) | SA105 |  | NO |  | 130 | 104
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PACKING RING | IS1972 |  | NO |  | 130 | 1.3
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 310 | 17084.1
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD406.4X6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 105 | 6220.2
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD273.1X6.0 EP STY 'D' D1=261.1 | IS3589-410MPA |  | M |  | 50 | 1975
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB25X4.0 BLACK EP STY 'D' D1=26.9 | IS1239 BLACK |  | M |  | 175 | 519.75
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB50X4.5 EP ST Y D D1=52.7 | IS1239 BLACK |  | M |  | 85 | 524.45
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.0 EP STY 'D' D1=207.1 | IS3589-410MPA |  | M |  | 85 | 2680.05
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.35 EP STY 'D' D1=206.4 | SA106GRB |  | M |  | 35 | 1165.85
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB80 X 4.8 EP STY 'D' D1=80.8 SHOP | IS1239 BLACK |  | M |  | 25 | 252.5
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90 X 5.49 STY'D',78 SHOP | SA106GRB |  | M |  | 5 | 56.45
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90X11.13 STY'D',69.2 SHOP | SA106GRC |  | M |  | 120 | 2562
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE DIA 33.4 X 9.09 EP STY 'D' D1=17.2 | SA106GRC |  | M |  | 20 | 109
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 20 | 915.8
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 12 | 314.4
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 7
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 15 | 250.5
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL 90DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 15.48
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X11.13 | SA234WPC |  | NO |  | 12 | 45.84
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X9.09 | SA234WPC |  | NO |  | 6 | 1.98
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 30.4
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 2 | 4.04
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD355.6X6.35 | SA234WPB |  | NO |  | 4 | 196.56
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD406.4X9.53/219.1X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 161.44
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 112.3
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/219.1X6.35 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 54.83
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/88.9X5.49 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 3.84
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 3
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 32
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD88.9X11.13 | SA234WPC |  | NO |  | 1 | 6.21
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD88.9X11.13/60.3X11.07 | SA234WPC |  | NO |  | 2 | 11.16
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB15 | SA105 | 4-80-329-79004 | NO |  | 10 | 1.8
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB25 | SA105 | 4-80-329-79005 | NO |  | 30 | 12.9
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | TEMP.STUB M33X2 L=45 | SA105 |  | NO |  | 2 | 1
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 4 | 83.88
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 5 | 39.5
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED NB80/PUMP END | IS1239 |  | NO |  | 2 | 0.2
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED PUMP END/NB80 | IS1239 |  | NO |  | 2 | 0.2
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | NB25 SW END WITH 1" NPT (F), CS | SA105 | 4-80-471-84576 | NO |  | 2 | 0.4
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SCREW PLUG M33X2 | SA105 |  | NO |  | 2 | 0.32
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.11 SW RED NB50/25 CL9000 | SA105 |  | NO |  | 2 | 2
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SW END CAP NB 50 CL3000 | SA105 | 4-80-453-58056 | NO |  | 2 | 1.4
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 400 | 5760
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 200
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. LR 45DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 12
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 23.4
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB100 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 21.6
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BW CAP OD114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 5 | 5.9
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 40 | 118.8
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 20 | 8.6
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NIPPLE 1" PLAIN X EXT THRD L=100MM | SA106GRB | 4-80-418-A0468 | NO |  | 70 | 22.68
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NB25 RUBBER HOSE L=15M IS444 TYPE II | IS444 Type II |  | NO |  | 35 | 525
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 425 | 2622.25
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 448 | 1330.56
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 145.125
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. RED NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 24 | 9.6
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 96
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.4
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 224 | 44.8
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | ASME B16.5 BLIND FLANGE NB50 CL150 | SA515GR70 | 4-80-477-A0644 | NO |  | 24 | 76.8
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 96 | 13.44
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NUT -M16 -2H | A194GR2H |  | NO |  | 192 | 5.76
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FLAT FACED FLANGE NB50 CLASS 150 | SA515GR70 | 4-80-468-65420 | NO |  | 24 | 48
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 70 | 1008
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 30
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD273.1 X 6.4 EP STY 'D' D1=260.3 | IS3589-410MPA |  | M |  | 270 | 10665
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4 X 6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 160 | 9478.4
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 50 | 2755.5
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPENB25X4.0 EP STY D D1-26.9 | IS1239 BLACK |  | M |  | 475 | 1410.75
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB80X4.8 EP STY D D1-80.8 | IS1239 BLACK |  | M |  | 950 | 9595
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB40X4.0 EP STY D D1-41.5 | IS1239 BLACK |  | M |  | 80 | 354.4
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB50X4.5 EP STY D D1-52.7 | IS1239 BLACK |  | M |  | 160 | 987.2
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 28 | 733.6
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 8 | 366.32
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 27
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 180 | 684
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 48
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 58.05
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/273.1X6.35 | SA234WPB |  | NO |  | 2 | 38.42
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 2 | 41.94
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.6
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 4
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 1 | 29.11
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 1 | 60.78
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD406.4X9.53/355.6X9.53 | SA234WPB |  | NO |  | 2 | 177.66
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | WELDED UN EQ TEE NB400/NB80 | As per drawing | 3-80-471-33301 | NO | A | 2
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4X8 L=800 | IS3589-410MPA | 3-80-471-33301 | NO |  | 2 | 125.754
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 88.9X4 | IS1239 BLACK | 3-80-471-33301 | NO |  | 2 | 2.936
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 8
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 52 | 195
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 130 | 208
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 57
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 4
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED NB40/NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 3
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB15 CL3000 SA105 | SA105 |  | NO |  | 15 | 2.7
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB25 CL3000 SA105 | SA105 |  | NO |  | 20 | 8.6
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | TEMP.STUB M33X2(CS) L=45 | SA105 |  | NO |  | 2 | 1
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB |  | NO |  | 2 | 112.3
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PLUG FOR THREMOCOUPLE NIPPLE M33X29CS) | SA105 |  | NO |  | 2 | 1.6
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 RC-1-1/2 INCH(F) | SA105 | 4-80-480-82955 | NO |  | 30 | 30.45
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(F)BSPT | SA105 | 4-80-480-84585 | NO |  | 25 | 16.75
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(M)BSPT | SA105 | 4-80-480-A0580 | NO |  | 25 | 16.75
7 | APL Raigarh 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 R 1-1/2 INCH | SA105 | 4-80-480-A0581 | NO |  | 70 | 98
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 323.9X6.4 EP STY D D1-311.2 | IS3589-410MPA |  | M |  | 20 | 1001
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 273.1 X 6.4 EP STY D-D1 260.3 | IS3589-410MPA |  | M |  | 65 | 2735.85
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 219.1 X 6.4 EP STY D-D1 206.3 | IS3589-410MPA |  | M |  | 300 | 10071
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB150X5.4 EP STY D-D1-156.8 | IS1239 BLACK |  | M |  | 640 | 13568
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB100X5.4 EP STY D-D1-105.3 | IS1239 BLACK |  | M |  | 140 | 2016
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB80X4.8 EP STY D-D1-80.8 | IS1239 BLACK |  | M |  | 920 | 9292
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB50X4.5 EP STY D-D1-52.7 | IS1239 BLACK |  | M |  | 400 | 2468
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB40X 4.0 EP STY D-D1-41.5 | IS1239 BLACK |  | M |  | 310 | 1373.3
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB25X4.0 EP STY D-D1-26.9 | IS1239 BLACK |  | M |  | 725 | 2153.25
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB15X 3.2 EP STY D-D1-15.9 | IS1239 BLACK |  | M |  | 680 | 986
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 12 | 200.4
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 10 | 262
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 208
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 150
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 280.8
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 116.1
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 30
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 24
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 140 | 14
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 6 | 214.2
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 11
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 33
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 18
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 3.6
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 10.5
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD273X6.35/88.9X5.49 | SA234WPB |  | NO |  | 4 | 101.28
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 12 | 180
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 58
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 65 | 104
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 16.5
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 24
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 24
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 93.75
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 33
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 13.5
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 17.5
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 85 | 25.5
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 1
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 5
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 4 | 20
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 18
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | UEQT NB 150/100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 31
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/88.9X5.49 | SA234WPB |  | NO |  | 8 | 135.04
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD168.3X7.11/60.3X5.54 | SA234WPB |  | NO |  | 10 | 113.9
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 9
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 10
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 18
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 2.5
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 3 | 0.6
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 1.5
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/50) | As per drawing | 3-80-999-97670 | NO |  | 15 | 99.375
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/40) | As per drawing | 3-80-999-97669 | NO |  | 18 | 119.25
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/25) | As per drawing | 3-80-999-97668 | NO |  | 30 | 216.75
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/15) | As per drawing | 3-80-999-97667 | NO |  | 5 | 36.125
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB15 CL3000 | SA105 |  | NO |  | 130 | 23.4
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB25 CL3000 | SA105 |  | NO |  | 50 | 21.5
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB40 CL3000 | SA105 |  | NO |  | 25 | 18.75
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB50 CL3000 | SA105 |  | NO |  | 30 | 39.9
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=45 | SA105 |  | NO |  | 10 | 5
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=64 | SA105 |  | NO |  | 120 | 84
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB15 | SA106GRB | 3-80-463-27244 | NO |  | 430 | 104.49
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB25 | IS1239 BLACK | 3-80-463-27244 | NO |  | 95 | 42.37
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB40 | IS1239 BLACK | 3-80-463-27244 | NO |  | 18 | 11.952
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB50 | IS1239 BLACK | 3-80-463-27244 | NO |  | 64 | 59.2
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PLUG FOR THERMO COUPLE NIPPLE M33X2 (CS) | SA105 |  | NO |  | 130 | 104
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PACKING RING | IS1972 |  | NO |  | 130 | 1.3
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 310 | 17084.1
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD406.4X6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 105 | 6220.2
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD273.1X6.0 EP STY 'D' D1=261.1 | IS3589-410MPA |  | M |  | 50 | 1975
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB25X4.0 BLACK EP STY 'D' D1=26.9 | IS1239 BLACK |  | M |  | 175 | 519.75
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB50X4.5 EP ST Y D D1=52.7 | IS1239 BLACK |  | M |  | 85 | 524.45
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.0 EP STY 'D' D1=207.1 | IS3589-410MPA |  | M |  | 85 | 2680.05
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.35 EP STY 'D' D1=206.4 | SA106GRB |  | M |  | 35 | 1165.85
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB80 X 4.8 EP STY 'D' D1=80.8 SHOP | IS1239 BLACK |  | M |  | 25 | 252.5
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90 X 5.49 STY'D',78 SHOP | SA106GRB |  | M |  | 5 | 56.45
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90X11.13 STY'D',69.2 SHOP | SA106GRC |  | M |  | 120 | 2562
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE DIA 33.4 X 9.09 EP STY 'D' D1=17.2 | SA106GRC |  | M |  | 20 | 109
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 20 | 915.8
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 12 | 314.4
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 7
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 15 | 250.5
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL 90DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 15.48
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X11.13 | SA234WPC |  | NO |  | 12 | 45.84
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X9.09 | SA234WPC |  | NO |  | 6 | 1.98
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 30.4
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 2 | 4.04
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD355.6X6.35 | SA234WPB |  | NO |  | 4 | 196.56
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD406.4X9.53/219.1X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 161.44
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 112.3
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/219.1X6.35 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 54.83
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/88.9X5.49 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 3.84
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 3
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 32
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD88.9X11.13 | SA234WPC |  | NO |  | 1 | 6.21
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD88.9X11.13/60.3X11.07 | SA234WPC |  | NO |  | 2 | 11.16
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB15 | SA105 | 4-80-329-79004 | NO |  | 10 | 1.8
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB25 | SA105 | 4-80-329-79005 | NO |  | 30 | 12.9
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | TEMP.STUB M33X2 L=45 | SA105 |  | NO |  | 2 | 1
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 4 | 83.88
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 5 | 39.5
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED NB80/PUMP END | IS1239 |  | NO |  | 2 | 0.2
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED PUMP END/NB80 | IS1239 |  | NO |  | 2 | 0.2
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | NB25 SW END WITH 1" NPT (F), CS | SA105 | 4-80-471-84576 | NO |  | 2 | 0.4
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SCREW PLUG M33X2 | SA105 |  | NO |  | 2 | 0.32
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.11 SW RED NB50/25 CL9000 | SA105 |  | NO |  | 2 | 2
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SW END CAP NB 50 CL3000 | SA105 | 4-80-453-58056 | NO |  | 2 | 1.4
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 400 | 5760
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 200
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. LR 45DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 12
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 23.4
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB100 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 21.6
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BW CAP OD114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 5 | 5.9
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 40 | 118.8
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 20 | 8.6
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NIPPLE 1" PLAIN X EXT THRD L=100MM | SA106GRB | 4-80-418-A0468 | NO |  | 70 | 22.68
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NB25 RUBBER HOSE L=15M IS444 TYPE II | IS444 Type II |  | NO |  | 10 | 150
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 425 | 2622.25
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 448 | 1330.56
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 145.125
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. RED NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 24 | 9.6
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 96
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.4
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 224 | 44.8
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | ASME B16.5 BLIND FLANGE NB50 CL150 | SA515GR70 | 4-80-477-A0644 | NO |  | 24 | 76.8
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 96 | 13.44
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NUT -M16 -2H | A194GR2H |  | NO |  | 192 | 5.76
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FLAT FACED FLANGE NB50 CLASS 150 | SA515GR70 | 4-80-468-65420 | NO |  | 24 | 48
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD273.1 X 6.4 EP STY 'D' D1=260.3 | IS3589-410MPA |  | M |  | 270 | 10665
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4 X 6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 160 | 9478.4
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 50 | 2755.5
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPENB25X4.0 EP STY D D1-26.9 | IS1239 BLACK |  | M |  | 475 | 1410.75
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB80X4.8 EP STY D D1-80.8 | IS1239 BLACK |  | M |  | 950 | 9595
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB40X4.0 EP STY D D1-41.5 | IS1239 BLACK |  | M |  | 80 | 354.4
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB50X4.5 EP STY D D1-52.7 | IS1239 BLACK |  | M |  | 160 | 987.2
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 28 | 733.6
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 8 | 366.32
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 27
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 180 | 684
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 48
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 58.05
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/273.1X6.35 | SA234WPB |  | NO |  | 2 | 38.42
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 2 | 41.94
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.6
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 4
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 1 | 29.11
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 1 | 60.78
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD406.4X9.53/355.6X9.53 | SA234WPB |  | NO |  | 2 | 177.66
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | WELDED UN EQ TEE NB400/NB80 | As per drawing | 3-80-471-33301 | NO | A | 2
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4X8 L=800 | IS3589-410MPA | 3-80-471-33301 | NO |  | 2 | 125.754
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 88.9X4 | IS1239 BLACK | 3-80-471-33301 | NO |  | 2 | 2.936
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 8
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 52 | 195
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 130 | 208
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 57
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 4
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED NB40/NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 3
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB15 CL3000 SA105 | SA105 |  | NO |  | 15 | 2.7
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB25 CL3000 SA105 | SA105 |  | NO |  | 20 | 8.6
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | TEMP.STUB M33X2(CS) L=45 | SA105 |  | NO |  | 2 | 1
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB |  | NO |  | 2 | 112.3
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PLUG FOR THREMOCOUPLE NIPPLE M33X29CS) | SA105 |  | NO |  | 2 | 1.6
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 RC-1-1/2 INCH(F) | SA105 | 4-80-480-82955 | NO |  | 30 | 30.45
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(F)BSPT | SA105 | 4-80-480-84585 | NO |  | 25 | 16.75
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(M)BSPT | SA105 | 4-80-480-A0580 | NO |  | 25 | 16.75
7 | APL Raigarh 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 R 1-1/2 INCH | SA105 | 4-80-480-A0581 | NO |  | 70 | 98
7 Total | [10 empty] | 271619.014
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 20 | 50
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE DIA 114.30 X 3.05 - SA312TP304H | SA312TP304H |  | M |  | 55 | 460.35
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 98 | 291.06
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB40X 4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 80 | 354.4
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 202 | 1246.34
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE NB 80 HEAVY - IS1239 | IS1239 BLACK |  | M |  | 466 | 4590.1
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 88 | 1267.2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 336 | 7123.2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 219.1 X 6.0 IS3589-410MPA | IS3589-410MPA |  | M |  | 174 | 5486.22
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1 X 6.4 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 144 | 6060.96
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 323.9X 6.35 IS3589FE410 PA | IS3589-410MPA |  | M |  | 140 | 6962.2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 355.6 X 6.4 IS3589-410MPA | IS3589-410MPA |  | M |  | 50 | 2755.5
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 406.4 X 6.0 EFW IS3589 LS/SPIRA | IS3589-410MPA |  | M |  | 7.5 | 444.3
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA457.1X6.0EFW IS3589-410MPA(LS/SPI | IS3589-410MPA |  | M |  | 170 | 11342.4
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 94 | 6982.32
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 102 | 9115.536
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 EFW IS3589-410MPA-LS/SPIR | IS3589-410MPA |  | M |  | 107 | 14840.9
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP304H |  | NO |  | 7 | 14
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 8 | 1.2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 34 | 6.8
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 6.4
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 28 | 54.18
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. LR 45DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 16
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 144 | 547.2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 18 | 90
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 94 | 977.6
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 46 | 768.2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.92
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 24 | 399.84
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 33 | 786.06
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 4 | 71.36
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 10 | 457.9
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. UEQT NB150 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.752
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BW LR 60DEG ELL 219.1 X 8.18 SA234WPB | SA234WPB |  | NO |  | 4 | 56
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 6 | 1.2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 2 | 1.2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 14.4
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RED NB 100/80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 19.8
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 17.94
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.68
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 2 | 2.52
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 16.32
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/323.9X6.35 | SA234WPB |  | NO |  | 7 | 120.75
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/323.9X6.35 | SA234WPB |  | NO |  | 2 | 47.18
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 3 | 48.45
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X9.53/355.6X9.53 | SA234WPB |  | NO |  | 4 | 144.52
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/406.4X6.35 | SA234WPB |  | NO |  | 2 | 50.94
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD168.3X7.11/114.3X6.02 | SA234WPB |  | NO |  | 2 | 6.32
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD 114.3X3.05 | SA403WP304H |  | NO |  | 1 | 2.94
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 1 | 0.4
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD219.1X6.35 | SA234WPB |  | NO |  | 6 | 115.62
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD168.3X7.11 | SA234WPB |  | NO |  | 2 | 26.56
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 4 | 13.16
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 4 | 243.12
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD457.2X9.53 | SA234WPB |  | NO |  | 2 | 229.54
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 5.94
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 107.2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD168.3X7.11/88.9X5.49 | SA234WPB |  | NO |  | 8 | 93.04
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD355.6X7.92/168.3X7.11 | SA234WPB |  | NO |  | 4 | 215.84
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/168.3X6.35 | SA234WPB |  | NO |  | 2 | 36.38
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 51.26
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT OD711.2X8 | As per drawing | 3-80-463-31357 | NO | A | 1
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=1200 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 166.44
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=750 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 104.025
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 508 X 6 | As per drawing | 3-80-463-A0817 | NO | A | 5
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 790.975
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA508X10 L=239 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 146.69
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 610 X 8 | As per drawing | 3-80-463-A0818 | NO | A | 6
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 908.496
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA610X10 L=298 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 264.432
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD610X6/323.9X6 | As per drawing | 3-80-463-A0820 | NO | A | 2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD610X10 L=600 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 177.552
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD323.9X8 L=186 00 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 23.174
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/355.6X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 5
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 964.7
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA355.6X8LS/SPIRAL IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 131.865
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/323.9 X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 1
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 166.63
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 323.9 X 8 IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 20.372
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB700/NB450 | As per drawing | 3-80-463-A0821 | NO | A | 5
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD711X10 IS 2062E250B | IS2062E250GRBR | 3-80-468-32127 | NO |  | 5 | 876.06
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 457X8 IS 3589 | IS3589-410MPA | 3-80-463-A0821 | NO |  | 5 | 98.765
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD508X6/OD457X6 | IS2062E250GRBR | 4-80-463-A0473 | NO |  | 4 | 197.192
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCER NB700/NB450 | IS2062E250GRBR | 4-80-463-A0474 | NO |  | 1 | 141.379
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD711.2/OD610 | IS2062E250GRBR | 4-80-463-A0475 | NO |  | 1 | 105.111
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD711.2X8/OD508X6 | IS2062E250GRBR | 4-80-463-A0478 | NO |  | 6 | 614.184
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD508X6/OD323.9X6 | IS2062E250GRBR | 4-80-463-A0479 | NO |  | 4 | 254.216
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ECC RED OD610X6/OD406.4X6 | IS2062E250GRBR | 3-80-463-A0819 | NO |  | 3 | 157.125
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 18 | 1369.44
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD457.2X9.53 | SA234WPB |  | NO |  | 8 | 604.24
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 4 | 152.08
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD508X9.53 | SA234WPB |  | NO |  | 20 | 1869.6
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 30°MITRE BEND Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0806 | NO |  | 3 | 85.344
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 711X8 (R=700) | IS2062E250GRBR | 3-80-463-A0807 | NO |  | 6 | 974.028
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 45DEG OD711.2X8 (R=700) | IS2062E250GRBR | 3-80-463-A0808 | NO |  | 2 | 162.024
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 60° OD 457 X 8 (R=686) | IS2062E250GRBR | 3-80-463-A0809 | NO |  | 2 | 133.93
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 610.0X8 (R=600) | IS2062E250GRBR | 3-80-463-A0810 | NO |  | 8 | 957.576
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | MITREBEND 45DEG Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0822 | NO |  | 2 | 85.66
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 100 | 18
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 100 | 43
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 50 CLASS 3000 | SA105 |  | NO |  | 100 | 133
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L45 | SA105 | 4-80-463-63321 | NO |  | 70 | 59.08
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L64 | SA105 | 4-80-463-23357 | NO |  | 70 | 176.96
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLUG RC 1" | SA105 | 4-80-463-23358 | NO |  | 140 | 70
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1"(NB80/50) | As per drawing | 3-80-460-28909 | NO | A | 40
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28909 | NO |  | 40 | 60.6
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK | 3-80-460-28909 | NO |  | 80 | 144
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 3-80-460-28909 | NO |  | 40 | 101.12
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 3-80-460-28909 | NO |  | 40 | 44.12
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1" (NB80/25) | As per drawing | 3-80-460-28907 | NO | A | 40
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28907 | NO |  | 40 | 60.6
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 144
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 24
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 4-80-463-23357 | NO |  | 40 | 101.12
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 4-80-463-23358 | NO |  | 40 | 44.12
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 308.5
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 38.7
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 70 | 207.9
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 5
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE NB15 IS1239 | IS1239 BLACK |  | M |  | 50 | 73.4
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 20 | 2.6
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 30 | 636
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1X 6.35 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 150 | 6262.5
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 62 | 5540.816
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 813 X 8 EFW-LS/SPIRAL IS3589-410MPA | IS3589-410MPA |  | M |  | 69 | 10957.2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 15 | 1114.2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 62.4
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 45DEG BEND NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 24
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 20 | 524
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 8 | 104.8
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=600) | IS3589-410MPA | 3-80-468-32248 | NO |  | 8 | 943.744
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=915) | IS2062E250GRBR | 3-80-463-A0833 | NO |  | 10 | 1780.38
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 30DEG MITRE BEND OD813X10 (R=800) | IS2062E250GRBR | 3-80-463-A0834 | NO |  | 2 | 174.898
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD813X9.53 | SA234WPB |  | NO |  | 3 | 1084.74
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD813X10 (R=800) | IS3589-410MPA | 3-80-463-27732 | NO |  | 9 | 2322.504
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 9.68
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 13.68
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BW RED 168.3X7.11/114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 8 | 32
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB350 | IS2062E250GRBR | 4-80-463-A0488 | NO |  | 6 | 375.684
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB250 | IS2062E250GRBR | 4-80-463-A0489 | NO |  | 4 | 234.112
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB800/NB600 | IS2062E250GRBR | 4-80-463-A0490 | NO |  | 3 | 275.715
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RED NB800/NBXXX HOLD | IS1239 |  | NO |  | 4 | 0.02
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB500 | As per drawing | 3-80-463-A0829 | NO | A | 1
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=1000 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 122.696
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=427 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 52.36
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB600 | As per drawing | 3-80-463-A0828 | NO | A | 1
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X12 L=1200 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 212.138
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X10 L=515 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 76.145
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 8 | 214.4
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT NB500/NB350 | As per drawing | 3-80-463-A0830 | NO | A | 3
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD508X8 L=700 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 207.144
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD355.6X8 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 42.744
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/250 | As per drawing | 3-80-463-A0825 | NO | A | 1
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X10;L=900 | IS2062E250GRBR | 3-80-463-A0825 | NO |  | 1 | 133.058
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD273.1X6.0;L=222 | IS3589-410MPA | 3-80-463-A0825 | NO |  | 1 | 8.769
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/500 | As per drawing | 3-80-463-A0836 | NO | A | 1
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø610X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 118.221
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø508X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 50.947
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB800/600 | As per drawing | 3-80-463-A0826 | NO | A | 4
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1000 | IS2062E250GRBR | 3-80-463-A0826 | NO |  | 4 | 947.652
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X6;L=322 | IS3589-410MPA | 3-80-463-A0826 | NO |  | 4 | 115.104
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED EQUAL TEENB800 | As per drawing | 3-80-463-A0827 | NO | A | 1
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1200 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 284.296
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=394 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 93.352
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACED FLANGE NB 500 CLASS 150 | SA515GR70 | 4-80-468-65426 | NO |  | 3 | 162
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB500 | SA515GR70 | 4-80-463-A0484 | NO |  | 3 | 383.4
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | STUD M30 X 3.5 X 230 SA193B7 | SA193B7 |  | NO |  | 60 | 66.24
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M30 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 120 | 27.6
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACE FLANGE NB800 | IS2062E250GRBR | 3-80-468-27258 | NO |  | 2 | 196.2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB-800 | IS2062E250GRBR | 4-80-463-A0486 | NO |  | 2 | 507.46
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | STUD M36X4 - 290 SA193B7 | SA193B7 |  | NO |  | 56 | 112
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | HEX NUT M36 X 4 SA194GR2H | SA194GR2H |  | NO |  | 112 | 48.16
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 300 | 1851
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 77.4
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 150 | 385.8
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 20 | 3.2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000 SA182F316 | SA182F316 |  | NO |  | 1 | 0.25
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 25 | 64.3
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 25 | 4
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000SA182F316 | SA182F316 |  | NO |  | 15 | 3.75
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 15 | 44.55
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW STUB NB25 CL3000 SA479TY316L | SA479TY316L |  | NO |  | 25 | 10.75
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB300 (OP -1) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=12 Ø 404 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 21.724
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=12 40X104 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.744
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB300 (OP -2) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8 Ø404 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 13.056
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8, 40X104 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.496
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB150 (OP -3) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8 Ø 217.5 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 4.016
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8, 30X96 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.344
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB250 (OP -4) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8 Ø 334 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 9.372
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8, 40X99 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.472
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB500 ( OP -5) | As per drawing | 3-80-463-A0944 | NO | A | 2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=10 Ø 600 | IS2062E250GRBR | 3-80-463-A0944 | NO |  | 2 | 37.124
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=10, 40X115 | IS2062E250GRBR | 3-80-463-A0944 | NO |  | 2 | 0.686
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB80 ( OP -6) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=6 Ø 133 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 1.2
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=6, 30X93 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.25
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB80 CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 36.272
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB150 CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 78.776
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB250CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 185.412
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB300CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 8 | 531.8
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB500CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 769.3
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | STUD M16 X 2 X 110 SA193B7 | SA193B7 |  | NO |  | 8 | 1.16
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M16 -2H | A194GR2H |  | NO |  | 16 | 0.48
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 16 | 4.848
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M20 -2H | BPS 41319 |  | NO |  | 32 | 2.08
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | STUD M 24 X 3 X 220 SA193 B16 | SA193B16 |  | NO |  | 72 | 47.52
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M24 -CL6-IS1364P3 BPS 41301 | IS:1364 (P-3) |  | NO |  | 144 | 15.84
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | STUD M30 X 3.5 X 230SA193B7 | SA193B7 |  | NO |  | 40 | 44.16
8 | APL Raigarh 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M30 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 80 | 18.4
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 20 | 50
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE DIA 114.30 X 3.05 - SA312TP304H | SA312TP304H |  | M |  | 55 | 460.35
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 98 | 291.06
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB40X 4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 80 | 354.4
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 202 | 1246.34
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE NB 80 HEAVY - IS1239 | IS1239 BLACK |  | M |  | 466 | 4590.1
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 88 | 1267.2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 336 | 7123.2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 219.1 X 6.0 IS3589-410MPA | IS3589-410MPA |  | M |  | 174 | 5486.22
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1 X 6.4 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 144 | 6060.96
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 323.9X 6.35 IS3589FE410 PA | IS3589-410MPA |  | M |  | 140 | 6962.2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 355.6 X 6.4 IS3589-410MPA | IS3589-410MPA |  | M |  | 50 | 2755.5
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 406.4 X 6.0 EFW IS3589 LS/SPIRA | IS3589-410MPA |  | M |  | 7.5 | 444.3
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA457.1X6.0EFW IS3589-410MPA(LS/SPI | IS3589-410MPA |  | M |  | 170 | 11342.4
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 94 | 6982.32
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 102 | 9115.536
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 EFW IS3589-410MPA-LS/SPIR | IS3589-410MPA |  | M |  | 107 | 14840.9
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP304H |  | NO |  | 7 | 14
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 8 | 1.2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 34 | 6.8
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 6.4
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 28 | 54.18
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. LR 45DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 16
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 144 | 547.2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 18 | 90
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 94 | 977.6
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 46 | 768.2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.92
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 24 | 399.84
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 33 | 786.06
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 4 | 71.36
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 10 | 457.9
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. UEQT NB150 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.752
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BW LR 60DEG ELL 219.1 X 8.18 SA234WPB | SA234WPB |  | NO |  | 4 | 56
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 6 | 1.2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 2 | 1.2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 14.4
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | RED NB 100/80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 19.8
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 17.94
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.68
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 2 | 2.52
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 16.32
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/323.9X6.35 | SA234WPB |  | NO |  | 7 | 120.75
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/323.9X6.35 | SA234WPB |  | NO |  | 2 | 47.18
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 3 | 48.45
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X9.53/355.6X9.53 | SA234WPB |  | NO |  | 4 | 144.52
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/406.4X6.35 | SA234WPB |  | NO |  | 2 | 50.94
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD168.3X7.11/114.3X6.02 | SA234WPB |  | NO |  | 2 | 6.32
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD 114.3X3.05 | SA403WP304H |  | NO |  | 1 | 2.94
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 1 | 0.4
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD219.1X6.35 | SA234WPB |  | NO |  | 6 | 115.62
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD168.3X7.11 | SA234WPB |  | NO |  | 2 | 26.56
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 4 | 13.16
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 4 | 243.12
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD457.2X9.53 | SA234WPB |  | NO |  | 2 | 229.54
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 5.94
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 107.2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD168.3X7.11/88.9X5.49 | SA234WPB |  | NO |  | 8 | 93.04
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD355.6X7.92/168.3X7.11 | SA234WPB |  | NO |  | 4 | 215.84
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/168.3X6.35 | SA234WPB |  | NO |  | 2 | 36.38
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 51.26
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT OD711.2X8 | As per drawing | 3-80-463-31357 | NO | A | 1
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=1200 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 166.44
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=750 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 104.025
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 508 X 6 | As per drawing | 3-80-463-A0817 | NO | A | 5
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 790.975
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA508X10 L=239 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 146.69
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 610 X 8 | As per drawing | 3-80-463-A0818 | NO | A | 6
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 908.496
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA610X10 L=298 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 264.432
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD610X6/323.9X6 | As per drawing | 3-80-463-A0820 | NO | A | 2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD610X10 L=600 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 177.552
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD323.9X8 L=186 00 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 23.174
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/355.6X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 5
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 964.7
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA355.6X8LS/SPIRAL IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 131.865
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/323.9 X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 1
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 166.63
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 323.9 X 8 IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 20.372
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB700/NB450 | As per drawing | 3-80-463-A0821 | NO | A | 5
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD711X10 IS 2062E250B | IS2062E250GRBR | 3-80-468-32127 | NO |  | 5 | 876.06
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 457X8 IS 3589 | IS3589-410MPA | 3-80-463-A0821 | NO |  | 5 | 98.765
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD508X6/OD457X6 | IS2062E250GRBR | 4-80-463-A0473 | NO |  | 4 | 197.192
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCER NB700/NB450 | IS2062E250GRBR | 4-80-463-A0474 | NO |  | 1 | 141.379
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD711.2/OD610 | IS2062E250GRBR | 4-80-463-A0475 | NO |  | 1 | 105.111
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD711.2X8/OD508X6 | IS2062E250GRBR | 4-80-463-A0478 | NO |  | 6 | 614.184
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD508X6/OD323.9X6 | IS2062E250GRBR | 4-80-463-A0479 | NO |  | 4 | 254.216
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ECC RED OD610X6/OD406.4X6 | IS2062E250GRBR | 3-80-463-A0819 | NO |  | 3 | 157.125
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 18 | 1369.44
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD457.2X9.53 | SA234WPB |  | NO |  | 8 | 604.24
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 4 | 152.08
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD508X9.53 | SA234WPB |  | NO |  | 20 | 1869.6
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 30°MITRE BEND Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0806 | NO |  | 3 | 85.344
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 711X8 (R=700) | IS2062E250GRBR | 3-80-463-A0807 | NO |  | 6 | 974.028
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 45DEG OD711.2X8 (R=700) | IS2062E250GRBR | 3-80-463-A0808 | NO |  | 2 | 162.024
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 60° OD 457 X 8 (R=686) | IS2062E250GRBR | 3-80-463-A0809 | NO |  | 2 | 133.93
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 610.0X8 (R=600) | IS2062E250GRBR | 3-80-463-A0810 | NO |  | 8 | 957.576
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | MITREBEND 45DEG Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0822 | NO |  | 2 | 85.66
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 100 | 18
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 100 | 43
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 50 CLASS 3000 | SA105 |  | NO |  | 100 | 133
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L45 | SA105 | 4-80-463-63321 | NO |  | 70 | 59.08
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L64 | SA105 | 4-80-463-23357 | NO |  | 70 | 176.96
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLUG RC 1" | SA105 | 4-80-463-23358 | NO |  | 140 | 70
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1"(NB80/50) | As per drawing | 3-80-460-28909 | NO | A | 40
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28909 | NO |  | 40 | 60.6
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK | 3-80-460-28909 | NO |  | 80 | 144
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 3-80-460-28909 | NO |  | 40 | 101.12
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 3-80-460-28909 | NO |  | 40 | 44.12
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1" (NB80/25) | As per drawing | 3-80-460-28907 | NO | A | 40
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28907 | NO |  | 40 | 60.6
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 144
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 24
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 4-80-463-23357 | NO |  | 40 | 101.12
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 4-80-463-23358 | NO |  | 40 | 44.12
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 308.5
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 38.7
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 70 | 207.9
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 5
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE NB15 IS1239 | IS1239 BLACK |  | M |  | 50 | 73.4
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 20 | 2.6
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 30 | 636
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1X 6.35 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 150 | 6262.5
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 62 | 5540.816
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 813 X 8 EFW-LS/SPIRAL IS3589-410MPA | IS3589-410MPA |  | M |  | 69 | 10957.2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 15 | 1114.2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 62.4
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 45DEG BEND NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 24
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 20 | 524
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 8 | 104.8
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=600) | IS3589-410MPA | 3-80-468-32248 | NO |  | 8 | 943.744
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=915) | IS2062E250GRBR | 3-80-463-A0833 | NO |  | 10 | 1780.38
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 30DEG MITRE BEND OD813X10 (R=800) | IS2062E250GRBR | 3-80-463-A0834 | NO |  | 2 | 174.898
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD813X9.53 | SA234WPB |  | NO |  | 3 | 1084.74
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD813X10 (R=800) | IS3589-410MPA | 3-80-463-27732 | NO |  | 9 | 2322.504
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 9.68
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 13.68
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BW RED 168.3X7.11/114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 8 | 32
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB350 | IS2062E250GRBR | 4-80-463-A0488 | NO |  | 6 | 375.684
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB250 | IS2062E250GRBR | 4-80-463-A0489 | NO |  | 4 | 234.112
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB800/NB600 | IS2062E250GRBR | 4-80-463-A0490 | NO |  | 3 | 275.715
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | RED NB800/NBXXX HOLD | IS1239 |  | NO |  | 4 | 0.02
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB500 | As per drawing | 3-80-463-A0829 | NO | A | 1
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=1000 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 122.696
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=427 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 52.36
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB600 | As per drawing | 3-80-463-A0828 | NO | A | 1
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X12 L=1200 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 212.138
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X10 L=515 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 76.145
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 8 | 214.4
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT NB500/NB350 | As per drawing | 3-80-463-A0830 | NO | A | 3
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD508X8 L=700 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 207.144
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD355.6X8 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 42.744
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/250 | As per drawing | 3-80-463-A0825 | NO | A | 1
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X10;L=900 | IS2062E250GRBR | 3-80-463-A0825 | NO |  | 1 | 133.058
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD273.1X6.0;L=222 | IS3589-410MPA | 3-80-463-A0825 | NO |  | 1 | 8.769
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/500 | As per drawing | 3-80-463-A0836 | NO | A | 1
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø610X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 118.221
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø508X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 50.947
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB800/600 | As per drawing | 3-80-463-A0826 | NO | A | 4
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1000 | IS2062E250GRBR | 3-80-463-A0826 | NO |  | 4 | 947.652
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X6;L=322 | IS3589-410MPA | 3-80-463-A0826 | NO |  | 4 | 115.104
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED EQUAL TEENB800 | As per drawing | 3-80-463-A0827 | NO | A | 1
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1200 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 284.296
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=394 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 93.352
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACED FLANGE NB 500 CLASS 150 | SA515GR70 | 4-80-468-65426 | NO |  | 3 | 162
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB500 | SA515GR70 | 4-80-463-A0484 | NO |  | 3 | 383.4
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | STUD M30 X 3.5 X 230 SA193B7 | SA193B7 |  | NO |  | 60 | 66.24
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M30 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 120 | 27.6
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACE FLANGE NB800 | IS2062E250GRBR | 3-80-468-27258 | NO |  | 2 | 196.2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB-800 | IS2062E250GRBR | 4-80-463-A0486 | NO |  | 2 | 507.46
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | STUD M36X4 - 290 SA193B7 | SA193B7 |  | NO |  | 56 | 112
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | HEX NUT M36 X 4 SA194GR2H | SA194GR2H |  | NO |  | 112 | 48.16
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 300 | 1851
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 77.4
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 150 | 385.8
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 20 | 3.2
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000 SA182F316 | SA182F316 |  | NO |  | 1 | 0.25
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 25 | 64.3
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 25 | 4
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000SA182F316 | SA182F316 |  | NO |  | 15 | 3.75
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 15 | 44.55
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
8 | APL Raigarh 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW STUB NB25 CL3000 SA479TY316L | SA479TY316L |  | NO |  | 25 | 10.75
8 Total | [10 empty] | 281931.116
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | PIPE OD33.4X4.55 EP STY D D1-25.2 ATSITE | SA106GRB |  | M |  | 105 | 340.2
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 24 | 4.56
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 465 | 3478.2
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 74 | 66.6
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 209 | 677.16
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 88 | 16.72
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 4 | 5.6
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 3 | 14.79
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 7 | 2.87
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 75 | 561
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 17 | 15.3
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6AT SITE | SA106GRB |  | M |  | 145 | 833.17
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD48.3X5.08 | SA234WPB |  | NO |  | 30 | 14.4
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 180 | 450
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 25 | 3.75
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 30 | 97.2
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 5 | 0.95
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/48.3X5.54 | SA234WPB |  | NO |  | 1 | 0.51
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB50/40 CL3000 | SA105 |  | NO |  | 2 | 2
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 45 | 40.5
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6 ATSITE | SA106GRB |  | M |  | 40 | 229.84
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 1050 | 3402
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 162 | 30.78
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 3 | 2.58
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 2 | 0.74
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 2 | 2.8
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 16 | 6.88
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 3 | 0.36
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB25/10 | SA105 | 3-80-449-A0883 | NO |  | 10 | 0.4
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD60.3X5.54 SA234WPB | SA234WPB |  | NO |  | 1 | 0.33
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD48.3X3.68 SA234WPB | SA234WPB |  | NO |  | 1 | 0.17
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | SW B16.11 CAP OD33.4X4.55 SA105 | SA105 |  | NO |  | 1 | 0.005
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 10 | 3
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 10 | 32.4
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY DD1-49.5 AT SITE | SA106GRB |  | M |  | 70 | 523.6
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 14 | 12.6
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 10 | 14
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 45 | 145.8
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 60 | 150
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 12 | 1.8
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 4
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 5 | 1
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB15/10 | SA479TY304 | 3-80-449-A0883 | NO |  | 5 | 0.2
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 1000 | 3240
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 156 | 29.64
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 80 | 34.4
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 26 | 23.4
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 10 | 3.7
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 40 | 56
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 49.5
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 50 | 125
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 4 | 2
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 60.3X5.54 EPSTY D D1-49.5 ATSITE | SA106GRC |  | M |  | 50 | 374
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 8.9
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | EQT OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 0.05
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA21.3X2.77 EPATSITE STY-DD1=16.16 | SA312TP304H |  | M |  | 50 | 65
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 15 | 1.2
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD21.3X3.73EP ATSITE STY-D,D1=14.24 | SA106GRB |  | M |  | 300 | 486
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA 21.3X3.73EPATSITE STY-DD1=14.24 | SA312TP304H |  | M |  | 50 | 80.5
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 15 | 0.87
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB15X 3.2 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 100 | 145
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 4
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 25 | 36.5
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 10 | 1
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRB |  | M |  | 150 | 486
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 50 | 9.5
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 45 | 5.4
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRC |  | M |  | 110 | 356.4
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW LR 90DEG ELL 33.4X 4.55 SA234WPC | SA234WPC |  | NO |  | 40 | 0.2
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X6.35/21.3X4.55 | SA234WPC |  | NO |  | 40 | 6
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA33.4X3.38 EPATSITE STY-D,D1=27 | SA312TP304H |  | M |  | 50 | 125
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 20 | 3
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 20 | 4
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSY NB50(OP-40)&(OP-45) | As per drawing | 3-80-449-A0984 | NO | A | 4
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 L=210MM | SA106GRB | 3-80-449-A0984 | NO |  | 4 | 5.12
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø52.22 | SA240TP304 | 3-80-449-A0984 | NO |  | 4 | 0.64
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEMBLY NB25 (OP-46) | As per drawing | 3-80-449-A0985 | NO | A | 2
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 L=210MM | SA312TP316L | 3-80-449-A0985 | NO |  | 2 | 1.36
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø28.50 | SA240TP304 | 3-80-449-A0985 | NO |  | 2 | 0.086
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSY NB80(OP-51)&(OP-52) | As per drawing | 3-80-449-A0977 | NO | A | 4
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD88.9X7.42 L=210MM | SA106GRB | 3-80-449-A0977 | NO |  | 4 | 12.8
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø77.92 | SA240TP304 | 3-80-449-A0977 | NO |  | 4 | 1.408
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEY NB25(OP-47) | As per drawing | 3-80-449-A0981 | NO | A | 2
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X6.35 L=210MM | SA106GRC | 3-80-449-A0981 | NO |  | 2 | 1.78
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATET=10THK,Ø22.70 ORIFICEHOLE DIA10MM | SA240TP304 | 3-80-449-A0981 | NO |  | 2 | 0.05
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEY NB25(OP-38) | As per drawing | 3-80-452-A0965 | NO | A | 2
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X6.35 L=210MM | SA106GRB | 3-80-452-A0965 | NO |  | 2 | 1.592
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø23.80ORIFICE HOLE DIA10MM | SA240TP304 | 3-80-452-A0965 | NO |  | 2 | 0.056
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEMBLY NB25 (OP-53) | As per drawing | 3-80-449-A0981 | NO | A | 2
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X6.35 L=210MM | SA106GRB | 3-80-449-A0981 | NO |  | 2 | 1.78
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK, Ø2 2.70 ORIF HOL DIA10 | SA240TP304 | 3-80-449-A0981 | NO |  | 2 | 0.054
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 160 | 400
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 18 | 2.7
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X2.77 EP STY D D1-16.2 ATSITE | SA312TP304H |  | M |  | 160 | 208
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 20 | 1.6
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 2 | 0.8
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD21.3X2.77 | SA403WP304H |  | NO |  | 2 | 0.36
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE DIA 33.4X3.38EPSTYD D1=27.2(SITE) | SA106GRB |  | M |  | 110 | 275
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.14
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 300 | 750
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 26 | 3.9
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X3.73 EP D1-15.2 AT SITE | SA312TP304H |  | M |  | 10 | 16.1
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 5 | 0.29
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 60 | 154.32
9 | APL Raigarh 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 6 | 0.96
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | PIPE OD33.4X4.55 EP STY D D1-25.2 ATSITE | SA106GRB |  | M |  | 105 | 340.2
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 24 | 4.56
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 465 | 3478.2
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 74 | 66.6
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 209 | 677.16
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 88 | 16.72
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 4 | 5.6
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 3 | 14.79
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 7 | 2.87
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 75 | 561
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 17 | 15.3
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6AT SITE | SA106GRB |  | M |  | 145 | 833.17
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD48.3X5.08 | SA234WPB |  | NO |  | 30 | 14.4
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 180 | 450
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 25 | 3.75
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 30 | 97.2
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 5 | 0.95
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/48.3X5.54 | SA234WPB |  | NO |  | 1 | 0.51
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB50/40 CL3000 | SA105 |  | NO |  | 2 | 2
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 45 | 40.5
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6 ATSITE | SA106GRB |  | M |  | 40 | 229.84
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 1050 | 3402
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 162 | 30.78
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 3 | 2.58
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 2 | 0.74
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 2 | 2.8
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 16 | 6.88
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 3 | 0.36
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB25/10 | SA105 | 3-80-449-A0883 | NO |  | 10 | 0.4
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD60.3X5.54 SA234WPB | SA234WPB |  | NO |  | 1 | 0.33
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD48.3X3.68 SA234WPB | SA234WPB |  | NO |  | 1 | 0.17
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | SW B16.11 CAP OD33.4X4.55 SA105 | SA105 |  | NO |  | 1 | 0.005
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 10 | 3
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 10 | 32.4
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY DD1-49.5 AT SITE | SA106GRB |  | M |  | 10 | 74.8
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 4 | 3.6
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 1 | 1.4
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 45 | 145.8
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 60 | 150
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 12 | 1.8
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 4
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 5 | 1
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB15/10 | SA479TY304 | 3-80-449-A0883 | NO |  | 5 | 0.2
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 1000 | 3240
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 156 | 29.64
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 80 | 34.4
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 26 | 23.4
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 10 | 3.7
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 40 | 56
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 49.5
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 50 | 125
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 4 | 2
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 60.3X5.54 EPSTY D D1-49.5 ATSITE | SA106GRC |  | M |  | 50 | 374
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 8.9
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | EQT OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 0.05
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA21.3X2.77 EPATSITE STY-DD1=16.16 | SA312TP304H |  | M |  | 50 | 65
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 15 | 1.2
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD21.3X3.73EP ATSITE STY-D,D1=14.24 | SA106GRB |  | M |  | 300 | 486
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA 21.3X3.73EPATSITE STY-DD1=14.24 | SA312TP304H |  | M |  | 50 | 80.5
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 15 | 0.87
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB15X 3.2 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 100 | 145
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 4
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 25 | 36.5
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 10 | 1
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRB |  | M |  | 150 | 486
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 50 | 9.5
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 45 | 5.4
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRC |  | M |  | 110 | 356.4
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW LR 90DEG ELL 33.4X 4.55 SA234WPC | SA234WPC |  | NO |  | 40 | 0.2
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X6.35/21.3X4.55 | SA234WPC |  | NO |  | 40 | 6
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA33.4X3.38 EPATSITE STY-D,D1=27 | SA312TP304H |  | M |  | 50 | 125
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 20 | 3
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 20 | 4
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 160 | 400
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 18 | 2.7
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X2.77 EP STY D D1-16.2 ATSITE | SA312TP304H |  | M |  | 160 | 208
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 20 | 1.6
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 2 | 0.8
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD21.3X2.77 | SA403WP304H |  | NO |  | 2 | 0.36
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE DIA 33.4X3.38EPSTYD D1=27.2(SITE) | SA106GRB |  | M |  | 110 | 275
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.14
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 300 | 750
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 26 | 3.9
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X3.73 EP D1-15.2 AT SITE | SA312TP304H |  | M |  | 10 | 16.1
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 5 | 0.29
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 60 | 154.32
9 | APL Raigarh 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 6 | 0.96
9 Total | [10 empty] | 41640.756
Grand Total | [10 empty] | 945050.309
Note-
1. In case of Assembly items (indicated as 'A' under Assembly Indicator), exploded BOM will be indicated below the Assembly item. Weight of individual items of the Assembly shall be considered for arriving the final weight of the assembly. Individual drawings shall also be referred.
2. Bidders are required to thoroughly review the drawings before quoting.
3. in case of any mismatch between the Specification indicated against each item and corresponding Specification indicated in the drawing, Specification indicated in the drawing shall prevail.

## BOM- Mirzapur MTEUPPL 2x800 MW
Enquiry No 4202500017 dt 25.09.2025 Procurement of Low Pressure (LP) Piping for various Adani projects Annexure C- Detailed Piping System BOM (R01)
Schedule No | Project | Piping System | IBR / Non IBR | PGMA | Item Description | Specification | Drawing No | UOM | Assembly Indicator | Quantity | Weight (kg)
1 | Mirzapur MTEUPPL 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 33.4X4.55 EP AT SITE D1-25.2 | SA106GRB | 2-80-453-A0365 | M |  | 730 | 2365.2
1 | Mirzapur MTEUPPL 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRB | 2-80-453-A0365 | M |  | 30 | 224.4
1 | Mirzapur MTEUPPL 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRC | 2-80-453-A0365 | M |  | 300 | 2244
1 | Mirzapur MTEUPPL 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 21.3X3.73 EP AT SITE D1-14.5 | SA106GRB | 2-80-453-A0365 | M |  | 100 | 162
1 | Mirzapur MTEUPPL 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 100 | 38
1 | Mirzapur MTEUPPL 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 35 | 31.5
1 | Mirzapur MTEUPPL 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 34 | 10.2
1 | Mirzapur MTEUPPL 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 16 | 4.8
1 | Mirzapur MTEUPPL 2x800 MW Unit 1 | LP Piping Drains- SG Scope | IBR | 82453 | SW END CAP NB50 CL3000 SA105 | SA105 | 2-80-453-A0365 | NO |  | 4 | 1
1 | Mirzapur MTEUPPL 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 33.4X4.55 EP AT SITE D1-25.2 | SA106GRB | 2-80-453-A0365 | M |  | 730 | 2365.2
1 | Mirzapur MTEUPPL 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRB | 2-80-453-A0365 | M |  | 30 | 224.4
1 | Mirzapur MTEUPPL 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRC | 2-80-453-A0365 | M |  | 300 | 2244
1 | Mirzapur MTEUPPL 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 21.3X3.73 EP AT SITE D1-14.5 | SA106GRB | 2-80-453-A0365 | M |  | 100 | 162
1 | Mirzapur MTEUPPL 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 100 | 38
1 | Mirzapur MTEUPPL 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 35 | 31.5
1 | Mirzapur MTEUPPL 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 34 | 10.2
1 | Mirzapur MTEUPPL 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 16 | 4.8
1 | Mirzapur MTEUPPL 2x800 MW Unit 2 | LP Piping Drains- SG Scope | IBR | 82453 | SW END CAP NB50 CL3000 SA105 | SA105 | 2-80-453-A0365 | NO |  | 4 | 1
1 Total | [10 empty] | 10162.2
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (CS) | As per drawing | 3-80-418-38038 | NO | A | 130
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW | SA105 | 4-80-418-85267 | NO |  | 130 | 31.2
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA105 | 4-80-418-85269 | NO |  | 130 | 46.8
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA105 | 4-80-418-85270 | NO |  | 130 | 22.88
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TUBE 21.30 X 3.73 - SA106GRB | SA106GRB |  | M |  | 280 | 453.6
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | COND. LOOP (CS) | As per drawing | 3-80-999-99256 | NO | A | 10
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | LOOP CS OD21.3X4.78 L=700 | SA106GRC | 3-80-999-99256 | NO |  | 10 | 13.7
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA105 | 4-80-418-A0470 | NO |  | 130 | 26.52
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2" (PLAINXEXTTHRD)L=100MM | SA312TP316L | 4-80-418-A0517 | NO |  | 5 | 0.81
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 6 | 9.72
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | NO |  | 10 | 3.24
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2"-1/2"PLAIN X 1/2"NPT(M) | SA106GRB | 4-80-418-A0471 | NO |  | 10 | 1.62
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 10 | 2.56
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA182F316 | 4-80-418-A0518 | NO |  | 5 | 1.48
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (SS) | As per drawing | 3-80-418-A0856 | NO | A | 3
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2" NB-SW CL3000 | SA182F316 | 4-80-418-A0519 | NO |  | 3 | 0.888
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA182F316 | 4-80-418-A0520 | NO |  | 3 | 1.332
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA182F316 | 4-80-418-A0521 | NO |  | 3 | 0.651
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-50.4 | SA106GRB |  | M |  | 150 | 1122
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 27
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD33.4X4.55 EP STY D D1-25.2 AT SIT | SA106GRB |  | M |  | 165 | 534.6
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 30 | 5.7
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 60 | 22.8
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 5 | 8.25
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 10 | 4.3
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 1 | 1.4
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-49.0 | SA106GRB |  | M |  | 60 | 448.8
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 33.4 X 4.55 - SA106GRB | SA106GRB |  | M |  | 420 | 1360.8
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 21.3 X 3.73 - SA106GRB | SA106GRB |  | M |  | 240 | 388.8
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 25 | 22.5
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 120 | 45.6
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 35 | 10.5
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB50 CL3000 | SA105 |  | NO |  | 6 | 6
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 |  | NO |  | 45 | 13.5
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB50/25 CL3000 | SA105 |  | NO |  | 16 | 36
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 70 | 21
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 1/4"NPT/NB15 | SA105 |  | NO |  | 85 | 29.325
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 3/8"NPT/NB15 | SA105 |  | NO |  | 85 | 59.5
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 50 CL150 | SA515GR70 |  | NO |  | 2 | 4
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 25 CL150 | SA515GR70 |  | NO |  | 2 | 1.8
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT HEX GRA 8.8 M16X80 | IS:1364 (P-1) |  | NO |  | 4 | 0.62
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | HEX NUT M16 | IS:1364 (P-3) |  | NO |  | 4 | 0.12
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT-M12X70 -4.6-IS1364P1 | IS:1363 (P-1) |  | NO |  | 4 | 0.308
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NUT -M12 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 8 | 0.16
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD33.4X4.55 | SA515GR70 |  | NO |  | 30 | 4.14
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD60.3X5.54 | SA515GR70 | 3-80-709-99011 | NO |  | 2 | 0.8
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD114.3 X 6.02 SA106GRB | SA106GRB |  | M |  | 8 | 128.56
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 | SA234WPB |  | NO |  | 2 | 7.68
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 1 | 4.93
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE FOROD114.3X6.02 | SA515GR70 |  | NO |  | 1 | 2.19
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/40 CL3000 | SA105 |  | NO |  | 5 | 5
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/25 CL3000 | SA105 |  | NO |  | 8 | 8
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SW STUB NB15 CL 3000 | SA479TY304 |  | NO |  | 10 | 1.8
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (CS) | As per drawing | 3-80-418-38038 | NO | A | 25
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW | SA105 | 4-80-418-85267 | NO |  | 25 | 6
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA105 | 4-80-418-85269 | NO |  | 25 | 9
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA105 | 4-80-418-85270 | NO |  | 25 | 4.4
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TUBE 21.30 X 3.73 - SA106GRB | SA106GRB |  | M |  | 50 | 81
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | COND. LOOP (CS) | As per drawing | 3-80-999-99256 | NO | A | 25
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | LOOP CS OD21.3X4.78 L=700 | SA106GRC | 3-80-999-99256 | NO |  | 25 | 34.25
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA105 | 4-80-418-A0470 | NO |  | 25 | 5.1
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2" (PLAINXEXTTHRD)L=100MM | SA312TP316L | 4-80-418-A0517 | NO |  | 25 | 4.05
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 50 | 81
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | NO |  | 25 | 8.1
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2"-1/2"PLAIN X 1/2"NPT(M) | SA106GRB | 4-80-418-A0471 | NO |  | 25 | 4.05
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 25 | 4.9
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA182F316 | 4-80-418-A0518 | NO |  | 25 | 5.1
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (SS) | As per drawing | 3-80-418-A0856 | NO | A | 25
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2" NB-SW CL3000 | SA182F316 | 4-80-418-A0519 | NO |  | 25 | 7.4
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA182F316 | 4-80-418-A0520 | NO |  | 25 | 11.1
2 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA182F316 | 4-80-418-A0521 | NO |  | 25 | 5.425
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (CS) | As per drawing | 3-80-418-38038 | NO | A | 130
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW | SA105 | 4-80-418-85267 | NO |  | 130 | 31.2
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA105 | 4-80-418-85269 | NO |  | 130 | 46.8
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA105 | 4-80-418-85270 | NO |  | 130 | 22.88
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TUBE 21.30 X 3.73 - SA106GRB | SA106GRB |  | M |  | 280 | 453.6
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | COND. LOOP (CS) | As per drawing | 3-80-999-99256 | NO | A | 10
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | LOOP CS OD21.3X4.78 L=700 | SA106GRC | 3-80-999-99256 | NO |  | 10 | 13.7
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA105 | 4-80-418-A0470 | NO |  | 130 | 26.52
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2" (PLAINXEXTTHRD)L=100MM | SA312TP316L | 4-80-418-A0517 | NO |  | 5 | 0.81
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 6 | 9.72
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | NO |  | 10 | 3.24
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2"-1/2"PLAIN X 1/2"NPT(M) | SA106GRB | 4-80-418-A0471 | NO |  | 10 | 1.62
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 10 | 2.56
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA182F316 | 4-80-418-A0518 | NO |  | 5 | 1.48
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (SS) | As per drawing | 3-80-418-A0856 | NO | A | 3
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2" NB-SW CL3000 | SA182F316 | 4-80-418-A0519 | NO |  | 3 | 0.888
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA182F316 | 4-80-418-A0520 | NO |  | 3 | 1.332
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA182F316 | 4-80-418-A0521 | NO |  | 3 | 0.651
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-50.4 | SA106GRB |  | M |  | 150 | 1122
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 27
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD33.4X4.55 EP STY D D1-25.2 AT SIT | SA106GRB |  | M |  | 165 | 534.6
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 30 | 5.7
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 60 | 22.8
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 5 | 8.25
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 10 | 4.3
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 1 | 1.4
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-49.0 | SA106GRB |  | M |  | 60 | 448.8
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 33.4 X 4.55 - SA106GRB | SA106GRB |  | M |  | 420 | 1360.8
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 21.3 X 3.73 - SA106GRB | SA106GRB |  | M |  | 240 | 388.8
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 25 | 22.5
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 120 | 45.6
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 35 | 10.5
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB50 CL3000 | SA105 |  | NO |  | 6 | 6
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 |  | NO |  | 45 | 13.5
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB50/25 CL3000 | SA105 |  | NO |  | 16 | 36
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 70 | 21
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 1/4"NPT/NB15 | SA105 |  | NO |  | 85 | 29.325
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 3/8"NPT/NB15 | SA105 |  | NO |  | 85 | 59.5
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 50 CL150 | SA515GR70 |  | NO |  | 2 | 4
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 25 CL150 | SA515GR70 |  | NO |  | 2 | 1.8
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT HEX GRA 8.8 M16X80 | IS:1364 (P-1) |  | NO |  | 4 | 0.62
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | HEX NUT M16 | IS:1364 (P-3) |  | NO |  | 4 | 0.12
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT-M12X70 -4.6-IS1364P1 | IS:1363 (P-1) |  | NO |  | 4 | 0.308
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NUT -M12 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 8 | 0.16
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD33.4X4.55 | SA515GR70 |  | NO |  | 30 | 4.14
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD60.3X5.54 | SA515GR70 | 3-80-709-99011 | NO |  | 2 | 0.8
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD114.3 X 6.02 SA106GRB | SA106GRB |  | M |  | 8 | 128.56
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 | SA234WPB |  | NO |  | 2 | 7.68
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 1 | 4.93
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE FOROD114.3X6.02 | SA515GR70 |  | NO |  | 1 | 2.19
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/40 CL3000 | SA105 |  | NO |  | 5 | 5
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/25 CL3000 | SA105 |  | NO |  | 8 | 8
2 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SW STUB NB15 CL 3000 | SA479TY304 |  | NO |  | 10 | 1.8
2 Total | [10 empty] | 10207.843
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3762 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 32.357
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1733 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.906
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3644 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 31.342
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3079 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 26.482
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4807 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 41.345
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1662 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.295
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2728 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 23.464
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3978 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.215
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2539 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 21.838
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5201 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 44.734
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=298 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.563
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=326 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.804
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=104 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 0.895
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3339 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 28.719
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1739 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.957
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4942 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 42.506
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=892 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 7.672
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=171 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.471
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=562 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.834
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=699 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.012
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=782 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.726
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=780 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 5.178
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=268 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.779
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=3368 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 22.357
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=464 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.08
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=582 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.863
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=5178 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.372
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=673 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.467
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=151 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.002
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=1319 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 8.756
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 3 | 1.29
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 17 | 34
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 45DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 5 | 5.8
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BW EQUAL TEE OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 5.88
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.9BW UNEQT 114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 2.8
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1.75
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 1.54
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 0.56
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=3000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 25.803
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD88.9X3.05L=1000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.638
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X3.05L=2000 | SA312TP304H | 1-80-412-A0533 | NO |  | 1 | 12.92
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | BOTTOM PLATE 10THKX 1500X1500 | SA515GR70 | 1-80-412-A0533 | NO |  | 1 | 176.625
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1977 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 17.004
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD60.3X5.54 L=4000 | SA106GRB | 1-80-412-A0533 | NO |  | 1 | 29.924
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=264 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.271
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2672 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 22.982
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=360 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 3.096
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=242 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.081
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 50.66
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH CARRIER PLATES | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4382 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 37.69
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3039 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 26.138
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=192 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 1.651
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2938 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 25.27
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5544 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 47.684
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1001 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 8.61
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1583 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 13.615
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 8 | 16
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X5.49 L=2500 | SA106GRB | 2-80-412-A0362 | NO |  | 1 | 28.23
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 10MMX500X50010 | SA240TP304L | 2-80-412-A0362 | NO |  | 1 | 40.35
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=2000 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 17.202
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD168.3X3.4/114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 1 | 1.59
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 12MMX150X300 | SA515GR70 | 2-80-412-A0362 | NO |  | 1 | 4.239
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 230 | 591.56
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 50 | 8
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | BW UEQT 60.3X3.91/33.4X3.38 SA403WP316L | SA403WP316L |  | NO |  | 6 | 6.12
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25 SS | SA479TY304 |  | NO |  | 10 | 4.3
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | MULTI HOLE ORIFICE PLATE ASY(NB80)-OP43 | As per drawing | 3-80-412-A0952 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05 L=150MM | SA312TP316L | 3-80-412-A0952 | NO |  | 1 | 0.969
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE T=10THK, Ø84. 6 | SA240TP304 | 3-80-412-A0952 | NO |  | 1 | 0.37
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ORIFICE PLT NB80 (OP44) | As per drawing | 3-80-412-A0954 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05 L=150MM | SA312TP316L | 3-80-412-A0954 | NO |  | 1 | 0.969
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE T=10THK, Ø84.62 | SA240TP304 | 3-80-412-A0954 | NO |  | 1 | 0.37
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | ORIFICE PLT NB100 (OP54)) | As per drawing | 3-80-412-A0955 | NO | A | 2
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 L=200MM SA312TP316L | SA312TP316L | 3-80-412-A0955 | NO |  | 2 | 3.44
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE T=12THK, Ø110.20 | SA240TP304 | 3-80-412-A0955 | NO |  | 2 | 1.39
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD60.3X5.54 EP STY D D1-50.4AT SITE | SA106GRB |  | M |  | 25 | 187
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 8 | 7.2
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-60.3X3.91 EP STY D D1-53.2AT SITE | SA312TP316L |  | M |  | 130 | 726.57
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 18 | 11.7
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 180 | 462.96
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 21 | 3.36
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | SW RED NB50/25 CL3000 SA182F316 | SA182F316 | 4-80-452-85266 | NO |  | 2 | 7.2
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L |  | NO |  | 2 | 3.5
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 60.3 X 3.91 EP STY D D1-53.2 | SA312TP304H |  | M |  | 50 | 272
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP304H |  | NO |  | 10 | 6.5
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 5 | 2.5
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 50 | 125
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD60.3X3.91/33.4X3.38 | SA403WP304L |  | NO |  | 5 | 5.1
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 65 | 923.845
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 14 | 69.58
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD168.3 X3.4 | SA403WP316L |  | NO |  | 2 | 13
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD168.3X3.4/88.9X3.05 | SA403WP316L |  | NO |  | 2 | 11.48
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 1 | 1.43
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 88.90 X 3.05 - SA312TP316L | SA312TP316L |  | M |  | 4 | 26.552
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L |  | NO |  | 2 | 2.32
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 RED OD168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 2 | 3.18
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | SOW FLANGE NB150 CL150 (RF) (SS316L) | SA182F316L |  | NO |  | 4 | 28
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 20 | 6.06
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | NUT -M20 -2H | BPS 41319 |  | NO |  | 40 | 2.6
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 75 | 1065.975
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 6 | 29.82
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 4 | 23.64
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 36 | 309.636
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 14 | 28
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD168.3X3.4/88.9X3.05 | SA403WP316L |  | NO |  | 1 | 5.74
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 1 | 1.43
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 88.90 X 3.05 - SA312TP316L | SA312TP316L |  | M |  | 4 | 26.552
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L |  | NO |  | 2 | 2.32
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 88.90 X 3.05 - SA312TP316L | SA312TP316L |  | M |  | 45 | 298.71
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L |  | NO |  | 10 | 11.6
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD88.9X3.05 | SA403WP316L |  | NO |  | 2 | 3.76
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD273.1 X 4.19 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 26 | 742.352
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD273.1X4.19 | SA403WP316L |  | NO |  | 2 | 33.26
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW EQT OD273.0X4.19 SA403WP316L | SA403WP316L |  | NO |  | 2 | 37.2
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW UEQT 273X4.19/219.1X3.76 SA403WP316L | SA403WP316L |  | NO |  | 2 | 36.328
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE D219.1 X 3.76 X6000 - SA312TP316L | SA312TP316L |  | M |  | 14 | 287.35
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X3.76 | SA403WP316L |  | NO |  | 2 | 19.14
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ECC RED219.1X3.76/168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 2 | 5.6
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 27 | 383.751
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 6 | 29.82
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 273.1X4.19/168.3X3.4 | SA403WP316L |  | NO |  | 4 | 69.76
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 ECCRED OD168.3X3.4/141.3X3.4 | SA403WP316L |  | NO |  | 4 | 7.16
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD141.3X3.4 L=6000 SA312TP316L | SA312TP316L |  | M |  | 6 | 69.222
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | 90 DEG LR ELBOW OD 141.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 4 | 15.2
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD273X4.19 SA403WP316L | SA403WP316L |  | NO |  | 2 | 8.12
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW SR 90DEG ELL OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 2 | 2
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 284.26
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 4 | 19.88
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 172.02
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 4 | 8
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L |  | NO |  | 50 | 21.5
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | SW STUB NB15 SS | SA182F316 | 4-80-473-A0623 | NO |  | 30 | 5.4
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 33.4 X 4.55SA312TP316L | SA312TP316L |  | M |  | 45 | 145.8
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 5 | 8.1
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA403WP316L |  | NO |  | 28 | 5.32
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 60.3 X 3.91 SA312TP316L | SA312TP316L |  | M |  | 20 | 111.78
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | SW STUB NB 50 SS CL:3000-SA182F316 | SA182F316 |  | NO |  | 5 | 4.6
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X6000 - SA312TP316L | SA312TP316L |  | M |  | 270 | 3837.51
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 12 | 59.64
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD168.3 X3.4 | SA403WP316L |  | NO |  | 2 | 13
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 2 | 11.82
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 172.02
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 6 | 12
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD 273.00 X 6.35 X 6000 - SA106GRB | SA106GRB |  | M |  | 270 | 11275.2
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 14 | 366.8
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 2 | 58.22
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 10 | 4.3
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | M |  | 25 | 81
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 18 | 3.42
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | FLAT END CLOSURE OD273X6.35 | SA515GR70 |  | NO |  | 2 | 34.92
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X6000 - SA312TP316L | SA312TP316L |  | M |  | 250 | 3553.25
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 12 | 59.64
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 2 | 11.82
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 172.02
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 4 | 8
3 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 2 | 2.86
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3762 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 32.357
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1733 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.906
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3644 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 31.342
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3079 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 26.482
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4807 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 41.345
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1662 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.295
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2728 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 23.464
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3978 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.215
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2539 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 21.838
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5201 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 44.734
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=298 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.563
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=326 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.804
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=104 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 0.895
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3339 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 28.719
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1739 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.957
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4942 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 42.506
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=892 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 7.672
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=171 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.471
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=562 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.834
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=699 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.012
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=782 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.726
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=780 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 5.178
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=268 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.779
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=3368 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 22.357
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=464 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.08
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=582 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.863
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=5178 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.372
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=673 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.467
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=151 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.002
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=1319 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 8.756
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 3 | 1.29
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 17 | 34
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 45DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 5 | 5.8
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BW EQUAL TEE OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 5.88
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.9BW UNEQT 114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 2.8
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1.75
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 1.54
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 0.56
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=3000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 25.803
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD88.9X3.05L=1000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.638
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X3.05L=2000 | SA312TP304H | 1-80-412-A0533 | NO |  | 1 | 12.92
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | BOTTOM PLATE 10THKX 1500X1500 | SA515GR70 | 1-80-412-A0533 | NO |  | 1 | 176.625
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1977 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 17.004
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD60.3X5.54 L=4000 | SA106GRB | 1-80-412-A0533 | NO |  | 1 | 29.924
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=264 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.271
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2672 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 22.982
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=360 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 3.096
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=242 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.081
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 50.66
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH CARRIER PLATES | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4382 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 37.69
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3039 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 26.138
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=192 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 1.651
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2938 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 25.27
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5544 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 47.684
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1001 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 8.61
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1583 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 13.615
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 8 | 16
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X5.49 L=2500 | SA106GRB | 2-80-412-A0362 | NO |  | 1 | 28.23
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 10MMX500X50010 | SA240TP304L | 2-80-412-A0362 | NO |  | 1 | 40.35
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=2000 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 17.202
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD168.3X3.4/114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 1 | 1.59
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 12MMX150X300 | SA515GR70 | 2-80-412-A0362 | NO |  | 1 | 4.239
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 230 | 591.56
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 50 | 8
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | BW UEQT 60.3X3.91/33.4X3.38 SA403WP316L | SA403WP316L |  | NO |  | 6 | 6.12
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25 SS | SA479TY304 |  | NO |  | 10 | 4.3
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD60.3X5.54 EP STY D D1-50.4AT SITE | SA106GRB |  | M |  | 25 | 187
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 8 | 7.2
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-60.3X3.91 EP STY D D1-53.2AT SITE | SA312TP316L |  | M |  | 130 | 726.57
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 18 | 11.7
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 180 | 462.96
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 21 | 3.36
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | SW RED NB50/25 CL3000 SA182F316 | SA182F316 | 4-80-452-85266 | NO |  | 2 | 7.2
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L |  | NO |  | 2 | 3.5
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 60.3 X 3.91 EP STY D D1-53.2 | SA312TP304H |  | M |  | 50 | 272
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP304H |  | NO |  | 10 | 6.5
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 5 | 2.5
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 50 | 125
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
3 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD60.3X3.91/33.4X3.38 | SA403WP304L |  | NO |  | 5 | 5.1
3 Total | [10 empty] | 34697.769
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1016 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 807.859
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PLATE 2500X2500X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 1 | 785
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT PIPE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=208 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 165.415
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=698 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 555.018
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 30DEG OD2032X16(R=0.75D)L=819 | SA515GR70 | 3-80-363-31709 | NO |  | 1 | 651.236
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 90DEG (R=0.75D) L=2457 | SA515GR70 | 3-80-363-31710 | NO |  | 2 | 3907.416
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | IMPULSE PIPE OD21.3X3.73 L=2750 | SA106GRB | 1-80-363-A0539 | NO |  | 4 | 17.82
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SPARE PIPE OD323.9X9.53 L=1000 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 73.88
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BLIND FLANGE ASSY. NB500 CL150 | SA515GR70 | 3-80-362-11781 | NO |  | 2 | 252
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STUD M30X200 | SA193B16 | 1-80-363-A0539 | NO |  | 44 | 37.4
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | HEX. NUT M30 | A194GR2H | 1-80-363-A0539 | NO |  | 88 | 20.24
4 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | GASKET, T=3 800X8 00 | NON-ASBESTOS | 1-80-363-A0539 | NO |  | 2 | 7.284
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1016 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 807.859
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PLATE 2500X2500X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 1 | 785
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT PIPE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=208 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 165.415
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=698 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 555.018
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 30DEG OD2032X16(R=0.75D)L=819 | SA515GR70 | 3-80-363-31709 | NO |  | 1 | 651.236
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 90DEG (R=0.75D) L=2457 | SA515GR70 | 3-80-363-31710 | NO |  | 2 | 3907.416
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | IMPULSE PIPE OD21.3X3.73 L=2750 | SA106GRB | 1-80-363-A0539 | NO |  | 4 | 17.82
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SPARE PIPE OD323.9X9.53 L=1000 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 73.88
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BLIND FLANGE ASSY. NB500 CL150 | SA515GR70 | 3-80-362-11781 | NO |  | 2 | 252
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STUD M30X200 | SA193B16 | 1-80-363-A0539 | NO |  | 44 | 37.4
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | HEX. NUT M30 | A194GR2H | 1-80-363-A0539 | NO |  | 88 | 20.24
4 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | GASKET, T=3 800X8 00 | NON-ASBESTOS | 1-80-363-A0539 | NO |  | 2 | 7.284
4 Total | [10 empty] | 51105.628
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | PIPE OD 273.00 X 6.35 X 6000 - SA106GRB | SA106GRB |  | M |  | 90 | 3758.4
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 14 | 366.8
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 1 | 29.11
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 5 | 2.15
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | M |  | 6 | 19.44
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 4 | 0.76
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | PIPE OD33.4X4.55 EP AT SITE 'D' D1=25.2 | SA106GRB |  | M |  | 280 | 907.2
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | PIPE OD60.3X5.54 EP AT SITE 'D' D1=49 | SA106GRB |  | M |  | 75 | 561
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | PIPE OD114.3X6.02EP AT SHOP 'D'D1=103.5 | SA106GRB |  | M |  | 950 | 15266.5
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | PIPE OD168.3X7.11EP AT SHOP 'D'D1=154.1 | SA106GRB |  | M |  | 50 | 1413
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 | SA234WPB |  | NO |  | 65 | 249.6
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X7.11 | SA234WPB |  | NO |  | 15 | 156
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 RED OD168.3X7.11/114.3X6.02 | SA234WPB |  | NO |  | 2 | 6.32
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | SW STUB NB25 CLASS 3000 | SA105 | 3-80-463-15996 | NO |  | 25 | 10.75
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 10 | 9
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 40 | 15.2
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 RED OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 2.82
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 3 | 4.95
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 1 | 1.4
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82650 | ASMEB16.9 UEQT OD168.3X7.11/114.3X6.02 | SA234WPB |  | NO |  | 2 | 24.04
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 88.9X5.49 EPD-79.0 AT SHOP | SA106GRB |  | M |  | 580 | 6554
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 - EP-D24.7(SITE L=40M | SA106GRB |  | M |  | 40 | 129.6
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD60.3X5.54 L=35M EP STY-D49.3(SITE | SA106GRB |  | M |  | 35 | 261.835
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 134 | 270.68
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 45DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 14 | 14.14
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 12 | 10.8
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 21 | 69.09
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 UEQT OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 14.85
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 4.3
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/48.3X5.08 | SA234WPB |  | NO |  | 5 | 3.85
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 15 | 2.85
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 EPSTY-D D1=24.7(SITE) | SA106GRB |  | M |  | 25 | 81
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 40 | 17.2
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NB50 OILHOSEASPERIS635 L=15 M WITH END | Rubber Hose |  | NO |  | 2 | 50
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT END CLOSURE OD88.9X5.49 | SA515GR70 |  | NO |  | 8 | 8.32
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT FACED FLANGE NB80 CL 150 SA105 | SA515GR70 | 4-80-340-73230 | NO |  | 4 | 36
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | STUD M16 X 2 X 160 SA193B7 | SA193B7 |  | NO |  | 10 | 2.24
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NUT -M16 -2H | A194GR2H |  | NO |  | 20 | 0.6
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 15 | 2.7
5 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 21.3 X 4.78 L=10M | SA106GRB |  | M |  | 10 | 19.5
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 88.9X5.49 EPD-79.0 AT SHOP | SA106GRB |  | M |  | 580 | 6554
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 - EP-D24.7(SITE L=40M | SA106GRB |  | M |  | 40 | 129.6
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD60.3X5.54 L=35M EP STY-D49.3(SITE | SA106GRB |  | M |  | 35 | 261.835
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 134 | 270.68
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 45DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 14 | 14.14
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 12 | 10.8
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 21 | 69.09
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 UEQT OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 14.85
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 4.3
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/48.3X5.08 | SA234WPB |  | NO |  | 5 | 3.85
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 15 | 2.85
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 EPSTY-D D1=24.7(SITE) | SA106GRB |  | M |  | 25 | 81
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 40 | 17.2
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NB50 OILHOSEASPERIS635 L=15 M WITH END | Rubber Hose |  | NO |  | 2 | 50
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT END CLOSURE OD88.9X5.49 | SA515GR70 |  | NO |  | 8 | 8.32
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT FACED FLANGE NB80 CL 150 SA105 | SA515GR70 | 4-80-340-73230 | NO |  | 4 | 36
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | STUD M16 X 2 X 160 SA193B7 | SA193B7 |  | NO |  | 10 | 2.24
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NUT -M16 -2H | A194GR2H |  | NO |  | 20 | 0.6
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 15 | 2.7
5 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 21.3 X 4.78 L=10M | SA106GRB |  | M |  | 10 | 19.5
5 Total | [10 empty] | 37919.15
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 90 | 561.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 120 | 358.8
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 7
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 15.25
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 2
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 24
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 1
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 220 | 1372.8
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 27.45
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 3
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB 50/40 IS1239 | IS1239 G&T |  | NO |  | 2 | 3.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 12 | 53.64
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 40 | 119.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 1.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 19.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 70 | 35
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 40 | 12
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 40 | 60
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 25 | 74.75
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 1.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 19.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 3
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 525 | 7717.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 360
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 45DEG BEND NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 28
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 48
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/150 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/100 G&T | As per drawing | 2-80-614-A0308 | NO | A | 4
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 4 | 40.284
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 4 | 8.984
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 27.879
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 30
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 22 | 88
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 4 | 41.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 10 | 28
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 299
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 45 | 9
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 54
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 42.155
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 130 | 169
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 98 | 410.13
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 180 | 40.32
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 40 | 18.72
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/25 | As per drawing | 2-80-616-10294 | NO | A | 5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/15 | As per drawing | 2-80-616-10294 | NO | A | 10
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB200 IS1239 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB200 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 60 | 179.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 120 | 24
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | EQTEE NB25 IS1239 GAL | IS1239 G&T |  | NO |  | 60 | 0.3
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 60 | 24
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 60 | 87.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 60 | 6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/25 | As per drawing | 2-80-614-A0308 | NO | A | 8
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 8 | 53.712
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 8 | 1.52
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 52 | 156
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 42.155
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 358 | 2233.92
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1575 | 4709.25
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 125 | 182.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 36 | 3.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 210 | 42
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 53.375
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 36 | 5.76
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 9
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 18 | 7.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 80
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 10 | 23
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 40 | 5.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | NUT -M16 -2H | A194GR2H |  | NO |  | 80 | 2.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 10 | 10
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 100 | 50
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 400 | 120
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 75 | 112.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 150
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 50 | 25
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 30 | 3
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 25 | 7.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 2
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB25 IS1239 GAL L=75MM | IS1239 G&T | 3-80-612-21071 | NO |  | 34 | 7.616
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 30 | 9
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SCREWED NIPPLE NB40 IS1239 | IS1239 G&T | 3-80-612-21072 | NO |  | 4 | 2.68
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 40 IS1239 | IS1239 G&T |  | NO |  | 15 | 12
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 250 | 5475
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 685 | 4274.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1405 | 4200.95
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 3335 | 4869.1
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 10 | 360
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 25 | 260
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 92 | 140.3
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 230 | 46
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 1020 | 102
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 27.25
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 9.504
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 0.8
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 4
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 108
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 295.085
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150/15 | As per drawing | 2-80-616-06449 | NO | A | 10
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4 L=200 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 42.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 L=65.4 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 0.94
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 60 | 72
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 365 | 146
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 32 | 16
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 10
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 4
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD NB50X4.5 | IS1239 BLACK | 4-80-612-50147 | NO |  | 50 | 46.25
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | SOCKET NB200 (GALVANISED) | IS3589-410MPA G&T | 4-80-616-71901 | NO |  | 25 | 157.65
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 65 | 97.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 175 | 87.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 360 | 108
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 840 | 84
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 200 IS1239 | IS1239 G&T |  | NO |  | 17 | 102
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 150 IS1239 | IS1239 G&T |  | NO |  | 45 | 441
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 120 | 180
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 25 IS1239 | IS1239 G&T |  | NO |  | 240 | 120
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 560 | 168
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB50 IS1239 L=150 | IS1239 G&T | 3-80-612-21073 | NO |  | 50 | 46.25
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB25 IS1239 L=150 | IS1239 G&T | 3-80-612-21071 | NO |  | 200 | 89.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB15 IS1239 L=150 | IS1239 G&T | 3-80-612-21070 | NO |  | 450 | 98.1
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25 WITH THREAD 1"BSP(M) | SA106GRB | 4-80-612-82549 | NO |  | 2 | 0.648
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 40 | 10.24
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD ISO7 RC-1-1/2"(F)(GAL) | SA105 (Galvanized) | 4-80-612-A0578 | NO |  | 65 | 91
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 525 | 7717.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 360
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 45DEG BEND NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 28
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB100 IS1239G&T | IS1239 G&T |  | NO |  | 12 | 72
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | UEQT 200/100 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 3
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 3 | 30.213
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 3 | 6.738
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 60
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 5 | 14
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/150 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 41.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 50 | 149.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/25 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 60
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/15 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 10
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB200 IS3589 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB200 IS3589 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 128 | 166.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 95 | 397.575
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 150 | 33.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 24 | 11.232
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB150 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 4 | 78.776
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB100 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 8 | 83.056
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | STUD M16 X 2 X 110 SA193B7 | SA193B7 |  | NO |  | 64 | 9.28
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 128 | 3.84
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 32 | 9.696
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M20 -2H | BPS 41319 |  | NO |  | 64 | 4.16
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 925 | 1350.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1640 | 4903.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 447
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 240 | 1497.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 86 | 13.76
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 58 | 29
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 218 | 87.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 7.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 20 | 24
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 341 | 34.1
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 418 | 83.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 53 | 80.825
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 2 | 4.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 8 | 1.12
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 16 | 0.48
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 2 | 2
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB25 CL150- G&T | IS2062 |  | NO |  | 60 | 0.3
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 240 | 19.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 480 | 12
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB25CL150(GALV) | SA105 (Galvanized) |  | NO |  | 60 | 60
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB15 CL150- G&T | IS2062 |  | NO |  | 50 | 0.25
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 200 | 16
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 400 | 10
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB15 CL150(GALV | IS2062 |  | NO |  | 50 | 45
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 70 | 35
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 420 | 126
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 50 | 75
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 330 | 165
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 15 | 7.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 230 | 23
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 180 | 54
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB15 IS1239G&T | IS1239 G&T |  | NO |  | 50 | 5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 12
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 40 IS1239 | IS1239 G&T |  | NO |  | 20 | 16
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB 40 IS1239 | IS1239 G&T |  | NO |  | 12 | 4.8
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 200 | 2940
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB50X4.5 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 525 | 3276
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB25X4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 2200 | 6578
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 5850 | 8541
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 8 | 288
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 80
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 76.25
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 420 | 84
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1250 | 125
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 75 | 22.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB 200/100 IS1239 G&T | As per drawing | 2-80-616-10294 | NO | A | 2
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.0 L=300 | IS3589-410MPA | 2-80-616-10294 | NO |  | 2 | 18.918
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-616-10294 | NO |  | 2 | 4.492
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 1 | 6
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/50 IS1239 G&T | IS1239 G&T |  | NO |  | 13 | 52
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 140
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 12
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 48
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/15 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 108
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 20
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB25/15 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 120
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 50 IS1239 G7T | IS1239 G&T |  | NO |  | 10 | 5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 15 IS1239 G&T | IS1239 G&T |  | NO |  | 200 | 20
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB50X4.05 | IS1239 BLACK | 4-80-612-50147 | NO |  | 40 | 37
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB25X3.25 | IS1239 BLACK | 4-80-612-50147 | NO |  | 250 | 111.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB15X4.50 | IS1239 BLACK | 4-80-612-50147 | NO |  | 650 | 141.7
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 65
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 135 | 67.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB25 IS1329 G&T | IS1239 G&T |  | NO |  | 550 | 165
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1470 | 147
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 146.475
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 135
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 370 | 185
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 980 | 294
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0575 | NO |  | 10 | 6.17
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0574 | NO |  | 100 | 29.7
6 | Mirzapur MTEUPPL 2x800 MW Unit 1 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1/2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0573 | NO |  | 650 | 94.25
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 90 | 561.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 120 | 358.8
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 7
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 15.25
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 2
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 24
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 1
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 170 | 1060.8
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 14 | 21.35
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 3
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB 50/40 IS1239 | IS1239 G&T |  | NO |  | 2 | 3.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 12 | 53.64
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 40 | 119.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 1.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 19.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 60 | 30
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 35 | 10.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 32 | 48
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 12.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 18 | 53.82
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 1.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 16
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 3
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 585 | 8599.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 98 | 392
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 45DEG BEND NB100IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 42
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 48
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/150 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/100 G&T | As per drawing | 2-80-614-A0308 | NO | A | 4
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 4 | 40.284
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 4 | 8.984
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 27.879
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 30
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 22 | 88
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 4 | 41.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 10 | 28
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 299
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 45 | 9
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 54
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 42.155
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 130 | 169
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 98 | 410.13
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 180 | 40.32
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 40 | 18.72
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/25 | As per drawing | 2-80-616-10294 | NO | A | 5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/15 | As per drawing | 2-80-616-10294 | NO | A | 10
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB200 IS1239 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB200 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 358 | 2233.92
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1575 | 4709.25
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 125 | 182.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 36 | 3.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 210 | 42
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 53.375
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 36 | 5.76
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 9
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 18 | 7.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 80
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 10 | 23
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 40 | 5.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | NUT -M16 -2H | A194GR2H |  | NO |  | 80 | 2.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 10 | 10
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 100 | 50
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 400 | 120
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 75 | 112.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 150
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 25 | 12.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 30 | 3
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 25 | 7.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB15 IS1239G&T | IS1239 G&T |  | NO |  | 10 | 1
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 250 | 5475
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 685 | 4274.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1405 | 4200.95
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 3335 | 4869.1
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 10 | 360
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 25 | 260
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 92 | 140.3
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 230 | 46
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 1020 | 102
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 27.25
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 9.504
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 0.8
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 4
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 108
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 295.085
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150/15 | As per drawing | 2-80-616-06449 | NO | A | 10
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4 L=200 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 42.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 L=65.4 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 0.94
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 60 | 72
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 365 | 146
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 32 | 16
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 10
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 4
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD NB50X4.5 | IS1239 BLACK | 4-80-612-50147 | NO |  | 50 | 46.25
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | SOCKET NB200 (GALVANISED) | IS3589-410MPA G&T | 4-80-616-71901 | NO |  | 25 | 157.65
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 65 | 97.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 175 | 87.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 360 | 108
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 840 | 84
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 200 IS1239 | IS1239 G&T |  | NO |  | 17 | 102
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 150 IS1239 | IS1239 G&T |  | NO |  | 45 | 441
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 120 | 180
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 25 IS1239 | IS1239 G&T |  | NO |  | 240 | 120
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 560 | 168
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB50 IS1239 L=150 | IS1239 G&T | 3-80-612-21073 | NO |  | 50 | 46.25
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB25 IS1239 L=150 | IS1239 G&T | 3-80-612-21071 | NO |  | 200 | 89.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB15 IS1239 L=150 | IS1239 G&T | 3-80-612-21070 | NO |  | 450 | 98.1
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25 WITH THREAD 1"BSP(M) | SA106GRB | 4-80-612-82549 | NO |  | 2 | 0.648
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 40 | 10.24
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD ISO7 RC-1-1/2"(F)(GAL) | SA105 (Galvanized) | 4-80-612-A0578 | NO |  | 65 | 91
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 580 | 8526
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 100 | 400
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 45DEG BEND NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 28
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB100 IS1239G&T | IS1239 G&T |  | NO |  | 15 | 90
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | UEQT 200/100 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 3
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 3 | 30.213
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 3 | 6.738
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 60
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 5 | 14
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/150 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 41.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 50 | 149.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/25 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 60
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/15 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 10
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB200 IS3589 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB200 IS3589 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 128 | 166.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 95 | 397.575
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 150 | 33.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 24 | 11.232
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB150 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 4 | 78.776
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB100 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 8 | 83.056
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | STUD M16 X 2 X 110 SA193B7 | SA193B7 |  | NO |  | 64 | 9.28
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 128 | 3.84
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 32 | 9.696
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M20 -2H | BPS 41319 |  | NO |  | 64 | 4.16
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 925 | 1350.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1640 | 4903.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 447
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 240 | 1497.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 86 | 13.76
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 58 | 29
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 218 | 87.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 7.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 20 | 24
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 341 | 34.1
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 418 | 83.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 53 | 80.825
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 2 | 4.6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 8 | 1.12
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 16 | 0.48
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 2 | 2
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB25 CL150- G&T | IS2062 |  | NO |  | 60 | 0.3
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 240 | 19.2
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 480 | 12
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB25CL150(GALV) | SA105 (Galvanized) |  | NO |  | 60 | 60
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB15 CL150- G&T | IS2062 |  | NO |  | 50 | 0.25
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 200 | 16
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 400 | 10
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB15 CL150(GALV | IS2062 |  | NO |  | 50 | 45
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 70 | 35
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 420 | 126
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 50 | 75
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 330 | 165
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 15 | 7.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 230 | 23
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 180 | 54
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB15 IS1239G&T | IS1239 G&T |  | NO |  | 50 | 5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 12
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 40 IS1239 | IS1239 G&T |  | NO |  | 20 | 16
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB 40 IS1239 | IS1239 G&T |  | NO |  | 12 | 4.8
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 200 | 2940
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB50X4.5 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 525 | 3276
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB25X4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 2200 | 6578
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 5850 | 8541
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 8 | 288
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 80
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 76.25
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 420 | 84
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1250 | 125
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 75 | 22.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB 200/100 IS1239 G&T | As per drawing | 2-80-616-10294 | NO | A | 2
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.0 L=300 | IS3589-410MPA | 2-80-616-10294 | NO |  | 2 | 18.918
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-616-10294 | NO |  | 2 | 4.492
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 1 | 6
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/50 IS1239 G&T | IS1239 G&T |  | NO |  | 13 | 52
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 140
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 12
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 48
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/15 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 108
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 20
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB25/15 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 120
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 50 IS1239 G7T | IS1239 G&T |  | NO |  | 10 | 5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 15 IS1239 G&T | IS1239 G&T |  | NO |  | 200 | 20
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB50X4.05 | IS1239 BLACK | 4-80-612-50147 | NO |  | 40 | 37
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB25X3.25 | IS1239 BLACK | 4-80-612-50147 | NO |  | 250 | 111.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB15X4.50 | IS1239 BLACK | 4-80-612-50147 | NO |  | 650 | 141.7
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 65
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 135 | 67.5
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB25 IS1329 G&T | IS1239 G&T |  | NO |  | 550 | 165
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1470 | 147
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 146.475
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 135
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 370 | 185
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 980 | 294
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0575 | NO |  | 10 | 6.17
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0574 | NO |  | 100 | 29.7
6 | Mirzapur MTEUPPL 2x800 MW Unit 2 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1/2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0573 | NO |  | 650 | 94.25
6 Total | [10 empty] | 205766.833
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 323.9X6.4 EP STY D D1-311.2 | IS3589-410MPA |  | M |  | 20 | 1001
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 273.1 X 6.4 EP STY D-D1 260.3 | IS3589-410MPA |  | M |  | 65 | 2735.85
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 219.1 X 6.4 EP STY D-D1 206.3 | IS3589-410MPA |  | M |  | 300 | 10071
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB150X5.4 EP STY D-D1-156.8 | IS1239 BLACK |  | M |  | 640 | 13568
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB100X5.4 EP STY D-D1-105.3 | IS1239 BLACK |  | M |  | 140 | 2016
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB80X4.8 EP STY D-D1-80.8 | IS1239 BLACK |  | M |  | 920 | 9292
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB50X4.5 EP STY D-D1-52.7 | IS1239 BLACK |  | M |  | 400 | 2468
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB40X 4.0 EP STY D-D1-41.5 | IS1239 BLACK |  | M |  | 310 | 1373.3
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB25X4.0 EP STY D-D1-26.9 | IS1239 BLACK |  | M |  | 725 | 2153.25
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB15X 3.2 EP STY D-D1-15.9 | IS1239 BLACK |  | M |  | 680 | 986
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 12 | 200.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 10 | 262
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 208
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 150
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 280.8
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 116.1
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 30
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 24
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 140 | 14
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 6 | 214.2
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 11
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 33
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 18
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 3.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 10.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD273X6.35/88.9X5.49 | SA234WPB |  | NO |  | 4 | 101.28
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 12 | 180
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 58
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 65 | 104
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 16.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 24
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 24
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 93.75
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 33
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 13.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 17.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 85 | 25.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 1
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 5
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 4 | 20
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 18
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | UEQT NB 150/100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 31
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/88.9X5.49 | SA234WPB |  | NO |  | 8 | 135.04
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD168.3X7.11/60.3X5.54 | SA234WPB |  | NO |  | 10 | 113.9
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 9
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 10
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 18
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 2.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 3 | 0.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 1.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/50) | As per drawing | 3-80-999-97670 | NO |  | 15 | 99.375
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/40) | As per drawing | 3-80-999-97669 | NO |  | 18 | 119.25
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/25) | As per drawing | 3-80-999-97668 | NO |  | 30 | 216.75
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/15) | As per drawing | 3-80-999-97667 | NO |  | 5 | 36.125
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB15 CL3000 | SA105 |  | NO |  | 130 | 23.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB25 CL3000 | SA105 |  | NO |  | 50 | 21.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB40 CL3000 | SA105 |  | NO |  | 25 | 18.75
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB50 CL3000 | SA105 |  | NO |  | 30 | 39.9
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=45 | SA105 |  | NO |  | 10 | 5
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=64 | SA105 |  | NO |  | 120 | 84
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB15 | SA106GRB | 3-80-463-27244 | NO |  | 430 | 104.49
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB25 | IS1239 BLACK | 3-80-463-27244 | NO |  | 95 | 42.37
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB40 | IS1239 BLACK | 3-80-463-27244 | NO |  | 18 | 11.952
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB50 | IS1239 BLACK | 3-80-463-27244 | NO |  | 64 | 59.2
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PLUG FOR THERMO COUPLE NIPPLE M33X2 (CS) | SA105 |  | NO |  | 130 | 104
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PACKING RING | IS1972 |  | NO |  | 130 | 1.3
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 310 | 17084.1
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD406.4X6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 105 | 6220.2
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD273.1X6.0 EP STY 'D' D1=261.1 | IS3589-410MPA |  | M |  | 50 | 1975
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB25X4.0 BLACK EP STY 'D' D1=26.9 | IS1239 BLACK |  | M |  | 175 | 519.75
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB50X4.5 EP ST Y D D1=52.7 | IS1239 BLACK |  | M |  | 85 | 524.45
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.0 EP STY 'D' D1=207.1 | IS3589-410MPA |  | M |  | 85 | 2680.05
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.35 EP STY 'D' D1=206.4 | SA106GRB |  | M |  | 35 | 1165.85
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB80 X 4.8 EP STY 'D' D1=80.8 SHOP | IS1239 BLACK |  | M |  | 25 | 252.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90 X 5.49 STY'D',78 SHOP | SA106GRB |  | M |  | 5 | 56.45
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90X11.13 STY'D',69.2 SHOP | SA106GRC |  | M |  | 120 | 2562
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE DIA 33.4 X 9.09 EP STY 'D' D1=17.2 | SA106GRC |  | M |  | 20 | 109
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 20 | 915.8
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 12 | 314.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 7
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 15 | 250.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL 90DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 15.48
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X11.13 | SA234WPC |  | NO |  | 12 | 45.84
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X9.09 | SA234WPC |  | NO |  | 6 | 1.98
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 30.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 2 | 4.04
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD355.6X6.35 | SA234WPB |  | NO |  | 4 | 196.56
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD406.4X9.53/219.1X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 161.44
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 112.3
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/219.1X6.35 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 54.83
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/88.9X5.49 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 3.84
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 3
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 32
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD88.9X11.13 | SA234WPC |  | NO |  | 1 | 6.21
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD88.9X11.13/60.3X11.07 | SA234WPC |  | NO |  | 2 | 11.16
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB15 | SA105 | 4-80-329-79004 | NO |  | 10 | 1.8
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB25 | SA105 | 4-80-329-79005 | NO |  | 30 | 12.9
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | TEMP.STUB M33X2 L=45 | SA105 |  | NO |  | 2 | 1
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 4 | 83.88
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 5 | 39.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED NB80/PUMP END | IS1239 |  | NO |  | 2 | 0.2
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED PUMP END/NB80 | IS1239 |  | NO |  | 2 | 0.2
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | NB25 SW END WITH 1" NPT (F), CS | SA105 | 4-80-471-84576 | NO |  | 2 | 0.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SCREW PLUG M33X2 | SA105 |  | NO |  | 2 | 0.32
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.11 SW RED NB50/25 CL9000 | SA105 |  | NO |  | 2 | 2
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SW END CAP NB 50 CL3000 | SA105 | 4-80-453-58056 | NO |  | 2 | 1.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 400 | 5760
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 200
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. LR 45DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 12
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 23.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB100 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 21.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BW CAP OD114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 5 | 5.9
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 40 | 118.8
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 20 | 8.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NIPPLE 1" PLAIN X EXT THRD L=100MM | SA106GRB | 4-80-418-A0468 | NO |  | 70 | 22.68
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NB25 RUBBER HOSE L=15M IS444 TYPE II | IS444 Type II |  | NO |  | 35 | 525
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 425 | 2622.25
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 448 | 1330.56
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 145.125
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. RED NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 24 | 9.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 96
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 224 | 44.8
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | ASME B16.5 BLIND FLANGE NB50 CL150 | SA515GR70 | 4-80-477-A0644 | NO |  | 24 | 76.8
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 96 | 13.44
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NUT -M16 -2H | A194GR2H |  | NO |  | 192 | 5.76
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FLAT FACED FLANGE NB50 CLASS 150 | SA515GR70 | 4-80-468-65420 | NO |  | 24 | 48
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 70 | 1008
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82477 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 30
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD273.1 X 6.4 EP STY 'D' D1=260.3 | IS3589-410MPA |  | M |  | 270 | 10665
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4 X 6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 160 | 9478.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 50 | 2755.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPENB25X4.0 EP STY D D1-26.9 | IS1239 BLACK |  | M |  | 475 | 1410.75
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB80X4.8 EP STY D D1-80.8 | IS1239 BLACK |  | M |  | 950 | 9595
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB40X4.0 EP STY D D1-41.5 | IS1239 BLACK |  | M |  | 80 | 354.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB50X4.5 EP STY D D1-52.7 | IS1239 BLACK |  | M |  | 160 | 987.2
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 28 | 733.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 8 | 366.32
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 27
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 180 | 684
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 48
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 58.05
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/273.1X6.35 | SA234WPB |  | NO |  | 2 | 38.42
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 2 | 41.94
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 4
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 1 | 29.11
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 1 | 60.78
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD406.4X9.53/355.6X9.53 | SA234WPB |  | NO |  | 2 | 177.66
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | WELDED UN EQ TEE NB400/NB80 | As per drawing | 3-80-471-33301 | NO | A | 2
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4X8 L=800 | IS3589-410MPA | 3-80-471-33301 | NO |  | 2 | 125.754
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 88.9X4 | IS1239 BLACK | 3-80-471-33301 | NO |  | 2 | 2.936
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 8
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 52 | 195
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 130 | 208
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 57
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 4
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED NB40/NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 3
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB15 CL3000 SA105 | SA105 |  | NO |  | 15 | 2.7
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB25 CL3000 SA105 | SA105 |  | NO |  | 20 | 8.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | TEMP.STUB M33X2(CS) L=45 | SA105 |  | NO |  | 2 | 1
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB |  | NO |  | 2 | 112.3
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PLUG FOR THREMOCOUPLE NIPPLE M33X29CS) | SA105 |  | NO |  | 2 | 1.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 RC-1-1/2 INCH(F) | SA105 | 4-80-480-82955 | NO |  | 30 | 30.45
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(F)BSPT | SA105 | 4-80-480-84585 | NO |  | 25 | 16.75
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(M)BSPT | SA105 | 4-80-480-A0580 | NO |  | 25 | 16.75
7 | Mirzapur MTEUPPL 2x800 MW Unit 1 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 R 1-1/2 INCH | SA105 | 4-80-480-A0581 | NO |  | 70 | 98
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 323.9X6.4 EP STY D D1-311.2 | IS3589-410MPA |  | M |  | 20 | 1001
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 273.1 X 6.4 EP STY D-D1 260.3 | IS3589-410MPA |  | M |  | 65 | 2735.85
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 219.1 X 6.4 EP STY D-D1 206.3 | IS3589-410MPA |  | M |  | 300 | 10071
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB150X5.4 EP STY D-D1-156.8 | IS1239 BLACK |  | M |  | 640 | 13568
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB100X5.4 EP STY D-D1-105.3 | IS1239 BLACK |  | M |  | 140 | 2016
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB80X4.8 EP STY D-D1-80.8 | IS1239 BLACK |  | M |  | 920 | 9292
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB50X4.5 EP STY D-D1-52.7 | IS1239 BLACK |  | M |  | 400 | 2468
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB40X 4.0 EP STY D-D1-41.5 | IS1239 BLACK |  | M |  | 310 | 1373.3
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB25X4.0 EP STY D-D1-26.9 | IS1239 BLACK |  | M |  | 725 | 2153.25
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB15X 3.2 EP STY D-D1-15.9 | IS1239 BLACK |  | M |  | 680 | 986
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 12 | 200.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 10 | 262
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 208
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 150
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 280.8
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 116.1
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 30
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 24
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 140 | 14
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 6 | 214.2
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 11
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 33
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 18
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 3.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 10.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD273X6.35/88.9X5.49 | SA234WPB |  | NO |  | 4 | 101.28
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 12 | 180
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 58
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 65 | 104
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 16.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 24
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 24
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 93.75
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 33
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 13.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 17.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 85 | 25.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 1
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 5
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 4 | 20
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 18
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | UEQT NB 150/100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 31
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/88.9X5.49 | SA234WPB |  | NO |  | 8 | 135.04
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD168.3X7.11/60.3X5.54 | SA234WPB |  | NO |  | 10 | 113.9
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 9
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 10
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 18
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 2.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 3 | 0.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 1.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/50) | As per drawing | 3-80-999-97670 | NO |  | 15 | 99.375
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/40) | As per drawing | 3-80-999-97669 | NO |  | 18 | 119.25
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/25) | As per drawing | 3-80-999-97668 | NO |  | 30 | 216.75
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/15) | As per drawing | 3-80-999-97667 | NO |  | 5 | 36.125
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB15 CL3000 | SA105 |  | NO |  | 130 | 23.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB25 CL3000 | SA105 |  | NO |  | 50 | 21.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB40 CL3000 | SA105 |  | NO |  | 25 | 18.75
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB50 CL3000 | SA105 |  | NO |  | 30 | 39.9
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=45 | SA105 |  | NO |  | 10 | 5
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=64 | SA105 |  | NO |  | 120 | 84
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB15 | SA106GRB | 3-80-463-27244 | NO |  | 430 | 104.49
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB25 | IS1239 BLACK | 3-80-463-27244 | NO |  | 95 | 42.37
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB40 | IS1239 BLACK | 3-80-463-27244 | NO |  | 18 | 11.952
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB50 | IS1239 BLACK | 3-80-463-27244 | NO |  | 64 | 59.2
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PLUG FOR THERMO COUPLE NIPPLE M33X2 (CS) | SA105 |  | NO |  | 130 | 104
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PACKING RING | IS1972 |  | NO |  | 130 | 1.3
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 310 | 17084.1
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD406.4X6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 105 | 6220.2
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD273.1X6.0 EP STY 'D' D1=261.1 | IS3589-410MPA |  | M |  | 50 | 1975
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB25X4.0 BLACK EP STY 'D' D1=26.9 | IS1239 BLACK |  | M |  | 175 | 519.75
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB50X4.5 EP ST Y D D1=52.7 | IS1239 BLACK |  | M |  | 85 | 524.45
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.0 EP STY 'D' D1=207.1 | IS3589-410MPA |  | M |  | 85 | 2680.05
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.35 EP STY 'D' D1=206.4 | SA106GRB |  | M |  | 35 | 1165.85
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB80 X 4.8 EP STY 'D' D1=80.8 SHOP | IS1239 BLACK |  | M |  | 25 | 252.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90 X 5.49 STY'D',78 SHOP | SA106GRB |  | M |  | 5 | 56.45
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90X11.13 STY'D',69.2 SHOP | SA106GRC |  | M |  | 120 | 2562
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE DIA 33.4 X 9.09 EP STY 'D' D1=17.2 | SA106GRC |  | M |  | 20 | 109
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 20 | 915.8
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 12 | 314.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 7
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 15 | 250.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL 90DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 15.48
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X11.13 | SA234WPC |  | NO |  | 12 | 45.84
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X9.09 | SA234WPC |  | NO |  | 6 | 1.98
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 30.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 2 | 4.04
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD355.6X6.35 | SA234WPB |  | NO |  | 4 | 196.56
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD406.4X9.53/219.1X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 161.44
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 112.3
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/219.1X6.35 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 54.83
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/88.9X5.49 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 3.84
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 3
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 32
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD88.9X11.13 | SA234WPC |  | NO |  | 1 | 6.21
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD88.9X11.13/60.3X11.07 | SA234WPC |  | NO |  | 2 | 11.16
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB15 | SA105 | 4-80-329-79004 | NO |  | 10 | 1.8
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB25 | SA105 | 4-80-329-79005 | NO |  | 30 | 12.9
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | TEMP.STUB M33X2 L=45 | SA105 |  | NO |  | 2 | 1
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 4 | 83.88
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 5 | 39.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED NB80/PUMP END | IS1239 |  | NO |  | 2 | 0.2
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED PUMP END/NB80 | IS1239 |  | NO |  | 2 | 0.2
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | NB25 SW END WITH 1" NPT (F), CS | SA105 | 4-80-471-84576 | NO |  | 2 | 0.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SCREW PLUG M33X2 | SA105 |  | NO |  | 2 | 0.32
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.11 SW RED NB50/25 CL9000 | SA105 |  | NO |  | 2 | 2
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SW END CAP NB 50 CL3000 | SA105 | 4-80-453-58056 | NO |  | 2 | 1.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 400 | 5760
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 200
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. LR 45DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 12
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 23.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB100 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 21.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BW CAP OD114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 5 | 5.9
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 40 | 118.8
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 20 | 8.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NIPPLE 1" PLAIN X EXT THRD L=100MM | SA106GRB | 4-80-418-A0468 | NO |  | 70 | 22.68
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NB25 RUBBER HOSE L=15M IS444 TYPE II | IS444 Type II |  | NO |  | 10 | 150
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 425 | 2622.25
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 448 | 1330.56
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 145.125
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. RED NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 24 | 9.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 96
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 224 | 44.8
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | ASME B16.5 BLIND FLANGE NB50 CL150 | SA515GR70 | 4-80-477-A0644 | NO |  | 24 | 76.8
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 96 | 13.44
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NUT -M16 -2H | A194GR2H |  | NO |  | 192 | 5.76
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FLAT FACED FLANGE NB50 CLASS 150 | SA515GR70 | 4-80-468-65420 | NO |  | 24 | 48
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD273.1 X 6.4 EP STY 'D' D1=260.3 | IS3589-410MPA |  | M |  | 270 | 10665
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4 X 6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 160 | 9478.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 50 | 2755.5
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPENB25X4.0 EP STY D D1-26.9 | IS1239 BLACK |  | M |  | 475 | 1410.75
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB80X4.8 EP STY D D1-80.8 | IS1239 BLACK |  | M |  | 950 | 9595
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB40X4.0 EP STY D D1-41.5 | IS1239 BLACK |  | M |  | 80 | 354.4
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB50X4.5 EP STY D D1-52.7 | IS1239 BLACK |  | M |  | 160 | 987.2
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 28 | 733.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 8 | 366.32
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 27
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 180 | 684
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 48
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 58.05
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/273.1X6.35 | SA234WPB |  | NO |  | 2 | 38.42
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 2 | 41.94
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 4
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 1 | 29.11
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 1 | 60.78
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD406.4X9.53/355.6X9.53 | SA234WPB |  | NO |  | 2 | 177.66
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | WELDED UN EQ TEE NB400/NB80 | As per drawing | 3-80-471-33301 | NO | A | 2
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4X8 L=800 | IS3589-410MPA | 3-80-471-33301 | NO |  | 2 | 125.754
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 88.9X4 | IS1239 BLACK | 3-80-471-33301 | NO |  | 2 | 2.936
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 8
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 52 | 195
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 130 | 208
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 57
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 4
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED NB40/NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 3
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB15 CL3000 SA105 | SA105 |  | NO |  | 15 | 2.7
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB25 CL3000 SA105 | SA105 |  | NO |  | 20 | 8.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | TEMP.STUB M33X2(CS) L=45 | SA105 |  | NO |  | 2 | 1
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB |  | NO |  | 2 | 112.3
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PLUG FOR THREMOCOUPLE NIPPLE M33X29CS) | SA105 |  | NO |  | 2 | 1.6
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 RC-1-1/2 INCH(F) | SA105 | 4-80-480-82955 | NO |  | 30 | 30.45
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(F)BSPT | SA105 | 4-80-480-84585 | NO |  | 25 | 16.75
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(M)BSPT | SA105 | 4-80-480-A0580 | NO |  | 25 | 16.75
7 | Mirzapur MTEUPPL 2x800 MW Unit 2 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 R 1-1/2 INCH | SA105 | 4-80-480-A0581 | NO |  | 70 | 98
7 Total | [10 empty] | 271619.014
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 20 | 50
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE DIA 114.30 X 3.05 - SA312TP304H | SA312TP304H |  | M |  | 55 | 460.35
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 98 | 291.06
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB40X 4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 80 | 354.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 202 | 1246.34
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE NB 80 HEAVY - IS1239 | IS1239 BLACK |  | M |  | 466 | 4590.1
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 88 | 1267.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 336 | 7123.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 219.1 X 6.0 IS3589-410MPA | IS3589-410MPA |  | M |  | 174 | 5486.22
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1 X 6.4 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 144 | 6060.96
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 323.9X 6.35 IS3589FE410 PA | IS3589-410MPA |  | M |  | 140 | 6962.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 355.6 X 6.4 IS3589-410MPA | IS3589-410MPA |  | M |  | 50 | 2755.5
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 406.4 X 6.0 EFW IS3589 LS/SPIRA | IS3589-410MPA |  | M |  | 7.5 | 444.3
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA457.1X6.0EFW IS3589-410MPA(LS/SPI | IS3589-410MPA |  | M |  | 170 | 11342.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 94 | 6982.32
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 102 | 9115.536
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 EFW IS3589-410MPA-LS/SPIR | IS3589-410MPA |  | M |  | 107 | 14840.9
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP304H |  | NO |  | 7 | 14
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 8 | 1.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 34 | 6.8
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 6.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 28 | 54.18
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. LR 45DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 16
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 144 | 547.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 18 | 90
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 94 | 977.6
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 46 | 768.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.92
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 24 | 399.84
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 33 | 786.06
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 4 | 71.36
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 10 | 457.9
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. UEQT NB150 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.752
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BW LR 60DEG ELL 219.1 X 8.18 SA234WPB | SA234WPB |  | NO |  | 4 | 56
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 6 | 1.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 2 | 1.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 14.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RED NB 100/80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 19.8
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 17.94
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.68
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 2 | 2.52
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 16.32
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/323.9X6.35 | SA234WPB |  | NO |  | 7 | 120.75
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/323.9X6.35 | SA234WPB |  | NO |  | 2 | 47.18
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 3 | 48.45
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X9.53/355.6X9.53 | SA234WPB |  | NO |  | 4 | 144.52
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/406.4X6.35 | SA234WPB |  | NO |  | 2 | 50.94
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD168.3X7.11/114.3X6.02 | SA234WPB |  | NO |  | 2 | 6.32
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD 114.3X3.05 | SA403WP304H |  | NO |  | 1 | 2.94
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 1 | 0.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD219.1X6.35 | SA234WPB |  | NO |  | 6 | 115.62
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD168.3X7.11 | SA234WPB |  | NO |  | 2 | 26.56
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 4 | 13.16
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 4 | 243.12
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD457.2X9.53 | SA234WPB |  | NO |  | 2 | 229.54
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 5.94
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 107.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD168.3X7.11/88.9X5.49 | SA234WPB |  | NO |  | 8 | 93.04
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD355.6X7.92/168.3X7.11 | SA234WPB |  | NO |  | 4 | 215.84
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/168.3X6.35 | SA234WPB |  | NO |  | 2 | 36.38
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 51.26
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT OD711.2X8 | As per drawing | 3-80-463-31357 | NO | A | 1
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=1200 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 166.44
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=750 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 104.025
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 508 X 6 | As per drawing | 3-80-463-A0817 | NO | A | 5
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 790.975
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA508X10 L=239 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 146.69
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 610 X 8 | As per drawing | 3-80-463-A0818 | NO | A | 6
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 908.496
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA610X10 L=298 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 264.432
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD610X6/323.9X6 | As per drawing | 3-80-463-A0820 | NO | A | 2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD610X10 L=600 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 177.552
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD323.9X8 L=186 00 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 23.174
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/355.6X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 5
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 964.7
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA355.6X8LS/SPIRAL IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 131.865
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/323.9 X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 1
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 166.63
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 323.9 X 8 IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 20.372
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB700/NB450 | As per drawing | 3-80-463-A0821 | NO | A | 5
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD711X10 IS 2062E250B | IS2062E250GRBR | 3-80-468-32127 | NO |  | 5 | 876.06
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 457X8 IS 3589 | IS3589-410MPA | 3-80-463-A0821 | NO |  | 5 | 98.765
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD508X6/OD457X6 | IS2062E250GRBR | 4-80-463-A0473 | NO |  | 4 | 197.192
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCER NB700/NB450 | IS2062E250GRBR | 4-80-463-A0474 | NO |  | 1 | 141.379
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD711.2/OD610 | IS2062E250GRBR | 4-80-463-A0475 | NO |  | 1 | 105.111
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD711.2X8/OD508X6 | IS2062E250GRBR | 4-80-463-A0478 | NO |  | 6 | 614.184
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD508X6/OD323.9X6 | IS2062E250GRBR | 4-80-463-A0479 | NO |  | 4 | 254.216
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ECC RED OD610X6/OD406.4X6 | IS2062E250GRBR | 3-80-463-A0819 | NO |  | 3 | 157.125
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 18 | 1369.44
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD457.2X9.53 | SA234WPB |  | NO |  | 8 | 604.24
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 4 | 152.08
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD508X9.53 | SA234WPB |  | NO |  | 20 | 1869.6
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 30°MITRE BEND Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0806 | NO |  | 3 | 85.344
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 711X8 (R=700) | IS2062E250GRBR | 3-80-463-A0807 | NO |  | 6 | 974.028
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 45DEG OD711.2X8 (R=700) | IS2062E250GRBR | 3-80-463-A0808 | NO |  | 2 | 162.024
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 60° OD 457 X 8 (R=686) | IS2062E250GRBR | 3-80-463-A0809 | NO |  | 2 | 133.93
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 610.0X8 (R=600) | IS2062E250GRBR | 3-80-463-A0810 | NO |  | 8 | 957.576
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | MITREBEND 45DEG Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0822 | NO |  | 2 | 85.66
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 100 | 18
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 100 | 43
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 50 CLASS 3000 | SA105 |  | NO |  | 100 | 133
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L45 | SA105 | 4-80-463-63321 | NO |  | 70 | 59.08
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L64 | SA105 | 4-80-463-23357 | NO |  | 70 | 176.96
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLUG RC 1" | SA105 | 4-80-463-23358 | NO |  | 140 | 70
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1"(NB80/50) | As per drawing | 3-80-460-28909 | NO | A | 40
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28909 | NO |  | 40 | 60.6
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK | 3-80-460-28909 | NO |  | 80 | 144
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 3-80-460-28909 | NO |  | 40 | 101.12
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 3-80-460-28909 | NO |  | 40 | 44.12
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1" (NB80/25) | As per drawing | 3-80-460-28907 | NO | A | 40
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28907 | NO |  | 40 | 60.6
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 144
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 24
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 4-80-463-23357 | NO |  | 40 | 101.12
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 4-80-463-23358 | NO |  | 40 | 44.12
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 308.5
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 38.7
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 70 | 207.9
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 5
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE NB15 IS1239 | IS1239 BLACK |  | M |  | 50 | 73.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 20 | 2.6
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 30 | 636
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1X 6.35 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 150 | 6262.5
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 62 | 5540.816
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 813 X 8 EFW-LS/SPIRAL IS3589-410MPA | IS3589-410MPA |  | M |  | 69 | 10957.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 15 | 1114.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 62.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 45DEG BEND NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 24
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 20 | 524
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 8 | 104.8
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=600) | IS3589-410MPA | 3-80-468-32248 | NO |  | 8 | 943.744
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=915) | IS2062E250GRBR | 3-80-463-A0833 | NO |  | 10 | 1780.38
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 30DEG MITRE BEND OD813X10 (R=800) | IS2062E250GRBR | 3-80-463-A0834 | NO |  | 2 | 174.898
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD813X9.53 | SA234WPB |  | NO |  | 3 | 1084.74
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD813X10 (R=800) | IS3589-410MPA | 3-80-463-27732 | NO |  | 9 | 2322.504
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 9.68
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 13.68
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BW RED 168.3X7.11/114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 8 | 32
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB350 | IS2062E250GRBR | 4-80-463-A0488 | NO |  | 6 | 375.684
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB250 | IS2062E250GRBR | 4-80-463-A0489 | NO |  | 4 | 234.112
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB800/NB600 | IS2062E250GRBR | 4-80-463-A0490 | NO |  | 3 | 275.715
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RED NB800/NBXXX HOLD | IS1239 |  | NO |  | 4 | 0.02
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB500 | As per drawing | 3-80-463-A0829 | NO | A | 1
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=1000 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 122.696
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=427 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 52.36
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB600 | As per drawing | 3-80-463-A0828 | NO | A | 1
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X12 L=1200 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 212.138
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X10 L=515 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 76.145
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 8 | 214.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT NB500/NB350 | As per drawing | 3-80-463-A0830 | NO | A | 3
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD508X8 L=700 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 207.144
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD355.6X8 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 42.744
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/250 | As per drawing | 3-80-463-A0825 | NO | A | 1
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X10;L=900 | IS2062E250GRBR | 3-80-463-A0825 | NO |  | 1 | 133.058
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD273.1X6.0;L=222 | IS3589-410MPA | 3-80-463-A0825 | NO |  | 1 | 8.769
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/500 | As per drawing | 3-80-463-A0836 | NO | A | 1
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø610X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 118.221
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø508X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 50.947
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB800/600 | As per drawing | 3-80-463-A0826 | NO | A | 4
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1000 | IS2062E250GRBR | 3-80-463-A0826 | NO |  | 4 | 947.652
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X6;L=322 | IS3589-410MPA | 3-80-463-A0826 | NO |  | 4 | 115.104
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED EQUAL TEENB800 | As per drawing | 3-80-463-A0827 | NO | A | 1
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1200 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 284.296
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=394 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 93.352
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACED FLANGE NB 500 CLASS 150 | SA515GR70 | 4-80-468-65426 | NO |  | 3 | 162
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB500 | SA515GR70 | 4-80-463-A0484 | NO |  | 3 | 383.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | STUD M30 X 3.5 X 230 SA193B7 | SA193B7 |  | NO |  | 60 | 66.24
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M30 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 120 | 27.6
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACE FLANGE NB800 | IS2062E250GRBR | 3-80-468-27258 | NO |  | 2 | 196.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB-800 | IS2062E250GRBR | 4-80-463-A0486 | NO |  | 2 | 507.46
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | STUD M36X4 - 290 SA193B7 | SA193B7 |  | NO |  | 56 | 112
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | HEX NUT M36 X 4 SA194GR2H | SA194GR2H |  | NO |  | 112 | 48.16
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 300 | 1851
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 77.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 150 | 385.8
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 20 | 3.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000 SA182F316 | SA182F316 |  | NO |  | 1 | 0.25
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 25 | 64.3
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 25 | 4
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000SA182F316 | SA182F316 |  | NO |  | 15 | 3.75
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 15 | 44.55
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SW STUB NB25 CL3000 SA479TY316L | SA479TY316L |  | NO |  | 25 | 10.75
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB300 (OP -1) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=12 Ø 404 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 21.724
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=12 40X104 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.744
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB300 (OP -2) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8 Ø404 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 13.056
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8, 40X104 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.496
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB150 (OP -3) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8 Ø 217.5 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 4.016
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8, 30X96 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.344
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB250 (OP -4) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8 Ø 334 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 9.372
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8, 40X99 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.472
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB500 ( OP -5) | As per drawing | 3-80-463-A0944 | NO | A | 2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=10 Ø 600 | IS2062E250GRBR | 3-80-463-A0944 | NO |  | 2 | 37.124
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=10, 40X115 | IS2062E250GRBR | 3-80-463-A0944 | NO |  | 2 | 0.686
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB80 ( OP -6) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=6 Ø 133 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 1.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=6, 30X93 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.25
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB80 CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 36.272
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB150 CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 78.776
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB250CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 185.412
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB300CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 8 | 531.8
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB500CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 769.3
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | STUD M16 X 2 X 110 SA193B7 | SA193B7 |  | NO |  | 8 | 1.16
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M16 -2H | A194GR2H |  | NO |  | 16 | 0.48
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 16 | 4.848
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M20 -2H | BPS 41319 |  | NO |  | 32 | 2.08
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | STUD M 24 X 3 X 220 SA193 B16 | SA193B16 |  | NO |  | 72 | 47.52
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M24 -CL6-IS1364P3 BPS 41301 | IS:1364 (P-3) |  | NO |  | 144 | 15.84
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | STUD M30 X 3.5 X 230SA193B7 | SA193B7 |  | NO |  | 40 | 44.16
8 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M30 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 80 | 18.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 20 | 50
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE DIA 114.30 X 3.05 - SA312TP304H | SA312TP304H |  | M |  | 55 | 460.35
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 98 | 291.06
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB40X 4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 80 | 354.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 202 | 1246.34
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE NB 80 HEAVY - IS1239 | IS1239 BLACK |  | M |  | 466 | 4590.1
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 88 | 1267.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 336 | 7123.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 219.1 X 6.0 IS3589-410MPA | IS3589-410MPA |  | M |  | 174 | 5486.22
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1 X 6.4 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 144 | 6060.96
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 323.9X 6.35 IS3589FE410 PA | IS3589-410MPA |  | M |  | 140 | 6962.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 355.6 X 6.4 IS3589-410MPA | IS3589-410MPA |  | M |  | 50 | 2755.5
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 406.4 X 6.0 EFW IS3589 LS/SPIRA | IS3589-410MPA |  | M |  | 7.5 | 444.3
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA457.1X6.0EFW IS3589-410MPA(LS/SPI | IS3589-410MPA |  | M |  | 170 | 11342.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 94 | 6982.32
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 102 | 9115.536
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 EFW IS3589-410MPA-LS/SPIR | IS3589-410MPA |  | M |  | 107 | 14840.9
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP304H |  | NO |  | 7 | 14
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 8 | 1.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 34 | 6.8
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 6.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 28 | 54.18
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. LR 45DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 16
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 144 | 547.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 18 | 90
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 94 | 977.6
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 46 | 768.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.92
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 24 | 399.84
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 33 | 786.06
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 4 | 71.36
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 10 | 457.9
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. UEQT NB150 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.752
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BW LR 60DEG ELL 219.1 X 8.18 SA234WPB | SA234WPB |  | NO |  | 4 | 56
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 6 | 1.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 2 | 1.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 14.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | RED NB 100/80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 19.8
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 17.94
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.68
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 2 | 2.52
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 16.32
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/323.9X6.35 | SA234WPB |  | NO |  | 7 | 120.75
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/323.9X6.35 | SA234WPB |  | NO |  | 2 | 47.18
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 3 | 48.45
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X9.53/355.6X9.53 | SA234WPB |  | NO |  | 4 | 144.52
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/406.4X6.35 | SA234WPB |  | NO |  | 2 | 50.94
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD168.3X7.11/114.3X6.02 | SA234WPB |  | NO |  | 2 | 6.32
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD 114.3X3.05 | SA403WP304H |  | NO |  | 1 | 2.94
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 1 | 0.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD219.1X6.35 | SA234WPB |  | NO |  | 6 | 115.62
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD168.3X7.11 | SA234WPB |  | NO |  | 2 | 26.56
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 4 | 13.16
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 4 | 243.12
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD457.2X9.53 | SA234WPB |  | NO |  | 2 | 229.54
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 5.94
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 107.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD168.3X7.11/88.9X5.49 | SA234WPB |  | NO |  | 8 | 93.04
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD355.6X7.92/168.3X7.11 | SA234WPB |  | NO |  | 4 | 215.84
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/168.3X6.35 | SA234WPB |  | NO |  | 2 | 36.38
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 51.26
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT OD711.2X8 | As per drawing | 3-80-463-31357 | NO | A | 1
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=1200 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 166.44
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=750 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 104.025
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 508 X 6 | As per drawing | 3-80-463-A0817 | NO | A | 5
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 790.975
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA508X10 L=239 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 146.69
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 610 X 8 | As per drawing | 3-80-463-A0818 | NO | A | 6
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 908.496
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA610X10 L=298 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 264.432
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD610X6/323.9X6 | As per drawing | 3-80-463-A0820 | NO | A | 2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD610X10 L=600 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 177.552
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD323.9X8 L=186 00 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 23.174
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/355.6X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 5
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 964.7
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA355.6X8LS/SPIRAL IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 131.865
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/323.9 X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 1
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 166.63
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 323.9 X 8 IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 20.372
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB700/NB450 | As per drawing | 3-80-463-A0821 | NO | A | 5
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD711X10 IS 2062E250B | IS2062E250GRBR | 3-80-468-32127 | NO |  | 5 | 876.06
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 457X8 IS 3589 | IS3589-410MPA | 3-80-463-A0821 | NO |  | 5 | 98.765
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD508X6/OD457X6 | IS2062E250GRBR | 4-80-463-A0473 | NO |  | 4 | 197.192
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCER NB700/NB450 | IS2062E250GRBR | 4-80-463-A0474 | NO |  | 1 | 141.379
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD711.2/OD610 | IS2062E250GRBR | 4-80-463-A0475 | NO |  | 1 | 105.111
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD711.2X8/OD508X6 | IS2062E250GRBR | 4-80-463-A0478 | NO |  | 6 | 614.184
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD508X6/OD323.9X6 | IS2062E250GRBR | 4-80-463-A0479 | NO |  | 4 | 254.216
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ECC RED OD610X6/OD406.4X6 | IS2062E250GRBR | 3-80-463-A0819 | NO |  | 3 | 157.125
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 18 | 1369.44
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD457.2X9.53 | SA234WPB |  | NO |  | 8 | 604.24
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 4 | 152.08
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD508X9.53 | SA234WPB |  | NO |  | 20 | 1869.6
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 30°MITRE BEND Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0806 | NO |  | 3 | 85.344
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 711X8 (R=700) | IS2062E250GRBR | 3-80-463-A0807 | NO |  | 6 | 974.028
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 45DEG OD711.2X8 (R=700) | IS2062E250GRBR | 3-80-463-A0808 | NO |  | 2 | 162.024
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 60° OD 457 X 8 (R=686) | IS2062E250GRBR | 3-80-463-A0809 | NO |  | 2 | 133.93
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 610.0X8 (R=600) | IS2062E250GRBR | 3-80-463-A0810 | NO |  | 8 | 957.576
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | MITREBEND 45DEG Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0822 | NO |  | 2 | 85.66
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 100 | 18
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 100 | 43
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 50 CLASS 3000 | SA105 |  | NO |  | 100 | 133
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L45 | SA105 | 4-80-463-63321 | NO |  | 70 | 59.08
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L64 | SA105 | 4-80-463-23357 | NO |  | 70 | 176.96
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLUG RC 1" | SA105 | 4-80-463-23358 | NO |  | 140 | 70
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1"(NB80/50) | As per drawing | 3-80-460-28909 | NO | A | 40
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28909 | NO |  | 40 | 60.6
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK | 3-80-460-28909 | NO |  | 80 | 144
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 3-80-460-28909 | NO |  | 40 | 101.12
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 3-80-460-28909 | NO |  | 40 | 44.12
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1" (NB80/25) | As per drawing | 3-80-460-28907 | NO | A | 40
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28907 | NO |  | 40 | 60.6
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 144
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 24
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 4-80-463-23357 | NO |  | 40 | 101.12
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 4-80-463-23358 | NO |  | 40 | 44.12
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 308.5
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 38.7
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 70 | 207.9
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 5
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE NB15 IS1239 | IS1239 BLACK |  | M |  | 50 | 73.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 20 | 2.6
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 30 | 636
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1X 6.35 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 150 | 6262.5
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 62 | 5540.816
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 813 X 8 EFW-LS/SPIRAL IS3589-410MPA | IS3589-410MPA |  | M |  | 69 | 10957.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 15 | 1114.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 62.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 45DEG BEND NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 24
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 20 | 524
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 8 | 104.8
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=600) | IS3589-410MPA | 3-80-468-32248 | NO |  | 8 | 943.744
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=915) | IS2062E250GRBR | 3-80-463-A0833 | NO |  | 10 | 1780.38
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 30DEG MITRE BEND OD813X10 (R=800) | IS2062E250GRBR | 3-80-463-A0834 | NO |  | 2 | 174.898
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD813X9.53 | SA234WPB |  | NO |  | 3 | 1084.74
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD813X10 (R=800) | IS3589-410MPA | 3-80-463-27732 | NO |  | 9 | 2322.504
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 9.68
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 13.68
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BW RED 168.3X7.11/114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 8 | 32
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB350 | IS2062E250GRBR | 4-80-463-A0488 | NO |  | 6 | 375.684
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB250 | IS2062E250GRBR | 4-80-463-A0489 | NO |  | 4 | 234.112
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB800/NB600 | IS2062E250GRBR | 4-80-463-A0490 | NO |  | 3 | 275.715
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | RED NB800/NBXXX HOLD | IS1239 |  | NO |  | 4 | 0.02
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB500 | As per drawing | 3-80-463-A0829 | NO | A | 1
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=1000 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 122.696
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=427 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 52.36
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB600 | As per drawing | 3-80-463-A0828 | NO | A | 1
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X12 L=1200 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 212.138
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X10 L=515 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 76.145
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 8 | 214.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT NB500/NB350 | As per drawing | 3-80-463-A0830 | NO | A | 3
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD508X8 L=700 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 207.144
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD355.6X8 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 42.744
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/250 | As per drawing | 3-80-463-A0825 | NO | A | 1
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X10;L=900 | IS2062E250GRBR | 3-80-463-A0825 | NO |  | 1 | 133.058
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD273.1X6.0;L=222 | IS3589-410MPA | 3-80-463-A0825 | NO |  | 1 | 8.769
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/500 | As per drawing | 3-80-463-A0836 | NO | A | 1
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø610X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 118.221
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø508X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 50.947
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB800/600 | As per drawing | 3-80-463-A0826 | NO | A | 4
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1000 | IS2062E250GRBR | 3-80-463-A0826 | NO |  | 4 | 947.652
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X6;L=322 | IS3589-410MPA | 3-80-463-A0826 | NO |  | 4 | 115.104
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED EQUAL TEENB800 | As per drawing | 3-80-463-A0827 | NO | A | 1
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1200 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 284.296
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=394 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 93.352
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACED FLANGE NB 500 CLASS 150 | SA515GR70 | 4-80-468-65426 | NO |  | 3 | 162
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB500 | SA515GR70 | 4-80-463-A0484 | NO |  | 3 | 383.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | STUD M30 X 3.5 X 230 SA193B7 | SA193B7 |  | NO |  | 60 | 66.24
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M30 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 120 | 27.6
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACE FLANGE NB800 | IS2062E250GRBR | 3-80-468-27258 | NO |  | 2 | 196.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB-800 | IS2062E250GRBR | 4-80-463-A0486 | NO |  | 2 | 507.46
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | STUD M36X4 - 290 SA193B7 | SA193B7 |  | NO |  | 56 | 112
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | HEX NUT M36 X 4 SA194GR2H | SA194GR2H |  | NO |  | 112 | 48.16
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 300 | 1851
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 77.4
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 150 | 385.8
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 20 | 3.2
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000 SA182F316 | SA182F316 |  | NO |  | 1 | 0.25
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 25 | 64.3
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 25 | 4
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000SA182F316 | SA182F316 |  | NO |  | 15 | 3.75
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 15 | 44.55
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
8 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Aux Cooling Water | Non IBR | 82463 | SW STUB NB25 CL3000 SA479TY316L | SA479TY316L |  | NO |  | 25 | 10.75
8 Total | [10 empty] | 281931.116
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | PIPE OD33.4X4.55 EP STY D D1-25.2 ATSITE | SA106GRB |  | M |  | 105 | 340.2
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 24 | 4.56
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 465 | 3478.2
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 74 | 66.6
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 209 | 677.16
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 88 | 16.72
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 4 | 5.6
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 3 | 14.79
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 7 | 2.87
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 75 | 561
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 17 | 15.3
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6AT SITE | SA106GRB |  | M |  | 145 | 833.17
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD48.3X5.08 | SA234WPB |  | NO |  | 30 | 14.4
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 180 | 450
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 25 | 3.75
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 30 | 97.2
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 5 | 0.95
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/48.3X5.54 | SA234WPB |  | NO |  | 1 | 0.51
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB50/40 CL3000 | SA105 |  | NO |  | 2 | 2
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 45 | 40.5
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6 ATSITE | SA106GRB |  | M |  | 40 | 229.84
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 1050 | 3402
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 162 | 30.78
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 3 | 2.58
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 2 | 0.74
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 2 | 2.8
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 16 | 6.88
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 3 | 0.36
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB25/10 | SA105 | 3-80-449-A0883 | NO |  | 10 | 0.4
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD60.3X5.54 SA234WPB | SA234WPB |  | NO |  | 1 | 0.33
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD48.3X3.68 SA234WPB | SA234WPB |  | NO |  | 1 | 0.17
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | SW B16.11 CAP OD33.4X4.55 SA105 | SA105 |  | NO |  | 1 | 0.005
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 10 | 3
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 10 | 32.4
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY DD1-49.5 AT SITE | SA106GRB |  | M |  | 70 | 523.6
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 14 | 12.6
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 10 | 14
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 45 | 145.8
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 60 | 150
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 12 | 1.8
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 4
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 5 | 1
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB15/10 | SA479TY304 | 3-80-449-A0883 | NO |  | 5 | 0.2
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 1000 | 3240
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 156 | 29.64
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 80 | 34.4
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 26 | 23.4
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 10 | 3.7
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 40 | 56
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 49.5
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 50 | 125
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 4 | 2
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 60.3X5.54 EPSTY D D1-49.5 ATSITE | SA106GRC |  | M |  | 50 | 374
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 8.9
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | EQT OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 0.05
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA21.3X2.77 EPATSITE STY-DD1=16.16 | SA312TP304H |  | M |  | 50 | 65
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 15 | 1.2
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD21.3X3.73EP ATSITE STY-D,D1=14.24 | SA106GRB |  | M |  | 300 | 486
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA 21.3X3.73EPATSITE STY-DD1=14.24 | SA312TP304H |  | M |  | 50 | 80.5
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 15 | 0.87
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB15X 3.2 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 100 | 145
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 4
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 25 | 36.5
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 10 | 1
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRB |  | M |  | 150 | 486
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 50 | 9.5
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 45 | 5.4
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRC |  | M |  | 110 | 356.4
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW LR 90DEG ELL 33.4X 4.55 SA234WPC | SA234WPC |  | NO |  | 40 | 0.2
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X6.35/21.3X4.55 | SA234WPC |  | NO |  | 40 | 6
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA33.4X3.38 EPATSITE STY-D,D1=27 | SA312TP304H |  | M |  | 50 | 125
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 20 | 3
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 20 | 4
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSY NB50(OP-40)&(OP-45) | As per drawing | 3-80-449-A0984 | NO | A | 4
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 L=210MM | SA106GRB | 3-80-449-A0984 | NO |  | 4 | 5.12
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø52.22 | SA240TP304 | 3-80-449-A0984 | NO |  | 4 | 0.64
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEMBLY NB25 (OP-46) | As per drawing | 3-80-449-A0985 | NO | A | 2
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 L=210MM | SA312TP316L | 3-80-449-A0985 | NO |  | 2 | 1.36
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø28.50 | SA240TP304 | 3-80-449-A0985 | NO |  | 2 | 0.086
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSY NB80(OP-51)&(OP-52) | As per drawing | 3-80-449-A0977 | NO | A | 4
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD88.9X7.42 L=210MM | SA106GRB | 3-80-449-A0977 | NO |  | 4 | 12.8
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø77.92 | SA240TP304 | 3-80-449-A0977 | NO |  | 4 | 1.408
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEY NB25(OP-47) | As per drawing | 3-80-449-A0981 | NO | A | 2
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X6.35 L=210MM | SA106GRC | 3-80-449-A0981 | NO |  | 2 | 1.78
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATET=10THK,Ø22.70 ORIFICEHOLE DIA10MM | SA240TP304 | 3-80-449-A0981 | NO |  | 2 | 0.05
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEY NB25(OP-38) | As per drawing | 3-80-452-A0965 | NO | A | 2
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X6.35 L=210MM | SA106GRB | 3-80-452-A0965 | NO |  | 2 | 1.592
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø23.80ORIFICE HOLE DIA10MM | SA240TP304 | 3-80-452-A0965 | NO |  | 2 | 0.056
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEMBLY NB25 (OP-53) | As per drawing | 3-80-449-A0981 | NO | A | 2
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X6.35 L=210MM | SA106GRB | 3-80-449-A0981 | NO |  | 2 | 1.78
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK, Ø2 2.70 ORIF HOL DIA10 | SA240TP304 | 3-80-449-A0981 | NO |  | 2 | 0.054
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 160 | 400
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 18 | 2.7
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X2.77 EP STY D D1-16.2 ATSITE | SA312TP304H |  | M |  | 160 | 208
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 20 | 1.6
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 2 | 0.8
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD21.3X2.77 | SA403WP304H |  | NO |  | 2 | 0.36
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE DIA 33.4X3.38EPSTYD D1=27.2(SITE) | SA106GRB |  | M |  | 110 | 275
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.14
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 300 | 750
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 26 | 3.9
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X3.73 EP D1-15.2 AT SITE | SA312TP304H |  | M |  | 10 | 16.1
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 5 | 0.29
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 60 | 154.32
9 | Mirzapur MTEUPPL 2x800 MW Unit 1 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 6 | 0.96
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | PIPE OD33.4X4.55 EP STY D D1-25.2 ATSITE | SA106GRB |  | M |  | 105 | 340.2
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 24 | 4.56
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 465 | 3478.2
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 74 | 66.6
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 209 | 677.16
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 88 | 16.72
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 4 | 5.6
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 3 | 14.79
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 7 | 2.87
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 75 | 561
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 17 | 15.3
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6AT SITE | SA106GRB |  | M |  | 145 | 833.17
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD48.3X5.08 | SA234WPB |  | NO |  | 30 | 14.4
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 180 | 450
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 25 | 3.75
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 30 | 97.2
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 5 | 0.95
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/48.3X5.54 | SA234WPB |  | NO |  | 1 | 0.51
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB50/40 CL3000 | SA105 |  | NO |  | 2 | 2
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 45 | 40.5
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6 ATSITE | SA106GRB |  | M |  | 40 | 229.84
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 1050 | 3402
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 162 | 30.78
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 3 | 2.58
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 2 | 0.74
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 2 | 2.8
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 16 | 6.88
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 3 | 0.36
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB25/10 | SA105 | 3-80-449-A0883 | NO |  | 10 | 0.4
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD60.3X5.54 SA234WPB | SA234WPB |  | NO |  | 1 | 0.33
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD48.3X3.68 SA234WPB | SA234WPB |  | NO |  | 1 | 0.17
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | SW B16.11 CAP OD33.4X4.55 SA105 | SA105 |  | NO |  | 1 | 0.005
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 10 | 3
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 10 | 32.4
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY DD1-49.5 AT SITE | SA106GRB |  | M |  | 10 | 74.8
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 4 | 3.6
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 1 | 1.4
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 45 | 145.8
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 60 | 150
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 12 | 1.8
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 4
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 5 | 1
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB15/10 | SA479TY304 | 3-80-449-A0883 | NO |  | 5 | 0.2
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 1000 | 3240
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 156 | 29.64
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 80 | 34.4
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 26 | 23.4
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 10 | 3.7
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 40 | 56
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 49.5
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 50 | 125
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 4 | 2
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 60.3X5.54 EPSTY D D1-49.5 ATSITE | SA106GRC |  | M |  | 50 | 374
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 8.9
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | EQT OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 0.05
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA21.3X2.77 EPATSITE STY-DD1=16.16 | SA312TP304H |  | M |  | 50 | 65
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 15 | 1.2
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD21.3X3.73EP ATSITE STY-D,D1=14.24 | SA106GRB |  | M |  | 300 | 486
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA 21.3X3.73EPATSITE STY-DD1=14.24 | SA312TP304H |  | M |  | 50 | 80.5
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 15 | 0.87
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB15X 3.2 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 100 | 145
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 4
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 25 | 36.5
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 10 | 1
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRB |  | M |  | 150 | 486
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 50 | 9.5
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 45 | 5.4
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRC |  | M |  | 110 | 356.4
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW LR 90DEG ELL 33.4X 4.55 SA234WPC | SA234WPC |  | NO |  | 40 | 0.2
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X6.35/21.3X4.55 | SA234WPC |  | NO |  | 40 | 6
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA33.4X3.38 EPATSITE STY-D,D1=27 | SA312TP304H |  | M |  | 50 | 125
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 20 | 3
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 20 | 4
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 160 | 400
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 18 | 2.7
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X2.77 EP STY D D1-16.2 ATSITE | SA312TP304H |  | M |  | 160 | 208
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 20 | 1.6
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 2 | 0.8
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD21.3X2.77 | SA403WP304H |  | NO |  | 2 | 0.36
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE DIA 33.4X3.38EPSTYD D1=27.2(SITE) | SA106GRB |  | M |  | 110 | 275
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.14
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 300 | 750
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 26 | 3.9
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X3.73 EP D1-15.2 AT SITE | SA312TP304H |  | M |  | 10 | 16.1
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 5 | 0.29
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 60 | 154.32
9 | Mirzapur MTEUPPL 2x800 MW Unit 2 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 6 | 0.96
9 Total | [10 empty] | 41640.756
Grand Total | [10 empty] | 945050.309
Note-
1. In case of Assembly items (indicated as 'A' under Assembly Indicator), exploded BOM will be indicated below the Assembly item. Weight of individual items of the Assembly shall be considered for arriving the final weight of the assembly. Individual drawings shall also be referred.
2. Bidders are required to thoroughly review the drawings before quoting.
3. in case of any mismatch between the Specification indicated against each item and corresponding Specification indicated in the drawing, Specification indicated in the drawing shall prevail.

## BOM- MEL Mahan 2x800 MW
Enquiry No 4202500017 dt 25.09.2025 Procurement of Low Pressure (LP) Piping for various Adani projects Annexure C- Detailed Piping System BOM (R01)
Schedule No | Project | Piping System | IBR / Non IBR | PGMA | Item Description | Specification | Drawing No | UOM | Assembly Indicator | Quantity | Weight (kg)
1 | MEL Mahan 2x800 MW Unit 3 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 33.4X4.55 EP AT SITE D1-25.2 | SA106GRB | 2-80-453-A0365 | M |  | 730 | 2365.2
1 | MEL Mahan 2x800 MW Unit 3 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRB | 2-80-453-A0365 | M |  | 30 | 224.4
1 | MEL Mahan 2x800 MW Unit 3 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRC | 2-80-453-A0365 | M |  | 300 | 2244
1 | MEL Mahan 2x800 MW Unit 3 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 21.3X3.73 EP AT SITE D1-14.5 | SA106GRB | 2-80-453-A0365 | M |  | 100 | 162
1 | MEL Mahan 2x800 MW Unit 3 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 100 | 38
1 | MEL Mahan 2x800 MW Unit 3 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 35 | 31.5
1 | MEL Mahan 2x800 MW Unit 3 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 34 | 10.2
1 | MEL Mahan 2x800 MW Unit 3 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 16 | 4.8
1 | MEL Mahan 2x800 MW Unit 3 | LP Piping Drains- SG Scope | IBR | 82453 | SW END CAP NB50 CL3000 SA105 | SA105 | 2-80-453-A0365 | NO |  | 4 | 1
1 | MEL Mahan 2x800 MW Unit 4 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 33.4X4.55 EP AT SITE D1-25.2 | SA106GRB | 2-80-453-A0365 | M |  | 730 | 2365.2
1 | MEL Mahan 2x800 MW Unit 4 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRB | 2-80-453-A0365 | M |  | 30 | 224.4
1 | MEL Mahan 2x800 MW Unit 4 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 60.3X5.54 EP AT SITE D1-49.0 | SA106GRC | 2-80-453-A0365 | M |  | 300 | 2244
1 | MEL Mahan 2x800 MW Unit 4 | LP Piping Drains- SG Scope | IBR | 82453 | PIPE OD 21.3X3.73 EP AT SITE D1-14.5 | SA106GRB | 2-80-453-A0365 | M |  | 100 | 162
1 | MEL Mahan 2x800 MW Unit 4 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 100 | 38
1 | MEL Mahan 2x800 MW Unit 4 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 35 | 31.5
1 | MEL Mahan 2x800 MW Unit 4 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 34 | 10.2
1 | MEL Mahan 2x800 MW Unit 4 | LP Piping Drains- SG Scope | IBR | 82453 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 | 2-80-453-A0365 | NO |  | 16 | 4.8
1 | MEL Mahan 2x800 MW Unit 4 | LP Piping Drains- SG Scope | IBR | 82453 | SW END CAP NB50 CL3000 SA105 | SA105 | 2-80-453-A0365 | NO |  | 4 | 1
1 Total | [10 empty] | 10162.2
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (CS) | As per drawing | 3-80-418-38038 | NO | A | 130
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW | SA105 | 4-80-418-85267 | NO |  | 130 | 31.2
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA105 | 4-80-418-85269 | NO |  | 130 | 46.8
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA105 | 4-80-418-85270 | NO |  | 130 | 22.88
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TUBE 21.30 X 3.73 - SA106GRB | SA106GRB |  | M |  | 280 | 453.6
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | COND. LOOP (CS) | As per drawing | 3-80-999-99256 | NO | A | 10
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | LOOP CS OD21.3X4.78 L=700 | SA106GRC | 3-80-999-99256 | NO |  | 10 | 13.7
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA105 | 4-80-418-A0470 | NO |  | 130 | 26.52
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2" (PLAINXEXTTHRD)L=100MM | SA312TP316L | 4-80-418-A0517 | NO |  | 5 | 0.81
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 6 | 9.72
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | NO |  | 10 | 3.24
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2"-1/2"PLAIN X 1/2"NPT(M) | SA106GRB | 4-80-418-A0471 | NO |  | 10 | 1.62
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 10 | 2.56
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA182F316 | 4-80-418-A0518 | NO |  | 5 | 1.48
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (SS) | As per drawing | 3-80-418-A0856 | NO | A | 3
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2" NB-SW CL3000 | SA182F316 | 4-80-418-A0519 | NO |  | 3 | 0.888
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA182F316 | 4-80-418-A0520 | NO |  | 3 | 1.332
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA182F316 | 4-80-418-A0521 | NO |  | 3 | 0.651
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-50.4 | SA106GRB |  | M |  | 150 | 1122
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 27
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD33.4X4.55 EP STY D D1-25.2 AT SIT | SA106GRB |  | M |  | 165 | 534.6
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 30 | 5.7
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 60 | 22.8
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 5 | 8.25
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 10 | 4.3
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 1 | 1.4
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-49.0 | SA106GRB |  | M |  | 60 | 448.8
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 33.4 X 4.55 - SA106GRB | SA106GRB |  | M |  | 420 | 1360.8
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 21.3 X 3.73 - SA106GRB | SA106GRB |  | M |  | 240 | 388.8
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 25 | 22.5
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 120 | 45.6
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 35 | 10.5
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB50 CL3000 | SA105 |  | NO |  | 6 | 6
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 |  | NO |  | 45 | 13.5
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB50/25 CL3000 | SA105 |  | NO |  | 16 | 36
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 70 | 21
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 1/4"NPT/NB15 | SA105 |  | NO |  | 85 | 29.325
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 3/8"NPT/NB15 | SA105 |  | NO |  | 85 | 59.5
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 50 CL150 | SA515GR70 |  | NO |  | 2 | 4
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 25 CL150 | SA515GR70 |  | NO |  | 2 | 1.8
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT HEX GRA 8.8 M16X80 | IS:1364 (P-1) |  | NO |  | 4 | 0.62
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | HEX NUT M16 | IS:1364 (P-3) |  | NO |  | 4 | 0.12
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT-M12X70 -4.6-IS1364P1 | IS:1363 (P-1) |  | NO |  | 4 | 0.308
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NUT -M12 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 8 | 0.16
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD33.4X4.55 | SA515GR70 |  | NO |  | 30 | 4.14
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD60.3X5.54 | SA515GR70 | 3-80-709-99011 | NO |  | 2 | 0.8
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD114.3 X 6.02 SA106GRB | SA106GRB |  | M |  | 8 | 128.56
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 | SA234WPB |  | NO |  | 2 | 7.68
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 1 | 4.93
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE FOROD114.3X6.02 | SA515GR70 |  | NO |  | 1 | 2.19
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/40 CL3000 | SA105 |  | NO |  | 5 | 5
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/25 CL3000 | SA105 |  | NO |  | 8 | 8
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SW STUB NB15 CL 3000 | SA479TY304 |  | NO |  | 10 | 1.8
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (CS) | As per drawing | 3-80-418-38038 | NO | A | 25
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW | SA105 | 4-80-418-85267 | NO |  | 25 | 6
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA105 | 4-80-418-85269 | NO |  | 25 | 9
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA105 | 4-80-418-85270 | NO |  | 25 | 4.4
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TUBE 21.30 X 3.73 - SA106GRB | SA106GRB |  | M |  | 50 | 81
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | COND. LOOP (CS) | As per drawing | 3-80-999-99256 | NO | A | 25
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | LOOP CS OD21.3X4.78 L=700 | SA106GRC | 3-80-999-99256 | NO |  | 25 | 34.25
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA105 | 4-80-418-A0470 | NO |  | 25 | 5.1
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2" (PLAINXEXTTHRD)L=100MM | SA312TP316L | 4-80-418-A0517 | NO |  | 25 | 4.05
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 50 | 81
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | NO |  | 25 | 8.1
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2"-1/2"PLAIN X 1/2"NPT(M) | SA106GRB | 4-80-418-A0471 | NO |  | 25 | 4.05
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 25 | 4.9
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA182F316 | 4-80-418-A0518 | NO |  | 25 | 5.1
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (SS) | As per drawing | 3-80-418-A0856 | NO | A | 25
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2" NB-SW CL3000 | SA182F316 | 4-80-418-A0519 | NO |  | 25 | 7.4
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA182F316 | 4-80-418-A0520 | NO |  | 25 | 11.1
2 | MEL Mahan 2x800 MW Unit 3 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA182F316 | 4-80-418-A0521 | NO |  | 25 | 5.425
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (CS) | As per drawing | 3-80-418-38038 | NO | A | 130
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW | SA105 | 4-80-418-85267 | NO |  | 130 | 31.2
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA105 | 4-80-418-85269 | NO |  | 130 | 46.8
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA105 | 4-80-418-85270 | NO |  | 130 | 22.88
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TUBE 21.30 X 3.73 - SA106GRB | SA106GRB |  | M |  | 280 | 453.6
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | COND. LOOP (CS) | As per drawing | 3-80-999-99256 | NO | A | 10
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | LOOP CS OD21.3X4.78 L=700 | SA106GRC | 3-80-999-99256 | NO |  | 10 | 13.7
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA105 | 4-80-418-A0470 | NO |  | 130 | 26.52
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2" (PLAINXEXTTHRD)L=100MM | SA312TP316L | 4-80-418-A0517 | NO |  | 5 | 0.81
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 6 | 9.72
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | NO |  | 10 | 3.24
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | PIPE NIPPLE 1/2"-1/2"PLAIN X 1/2"NPT(M) | SA106GRB | 4-80-418-A0471 | NO |  | 10 | 1.62
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 10 | 2.56
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2"NB-SW CL-3000 | SA182F316 | 4-80-418-A0518 | NO |  | 5 | 1.48
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | HEAD AND TAIL ASSEMBLY (SS) | As per drawing | 3-80-418-A0856 | NO | A | 3
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | FORGED COUPLING 1/2" NB-SW CL3000 | SA182F316 | 4-80-418-A0519 | NO |  | 3 | 0.888
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | TAIL PIPE | SA182F316 | 4-80-418-A0520 | NO |  | 3 | 1.332
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82418 | UNION NUT (1/2"NPT-F) | SA182F316 | 4-80-418-A0521 | NO |  | 3 | 0.651
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-50.4 | SA106GRB |  | M |  | 150 | 1122
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 27
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD33.4X4.55 EP STY D D1-25.2 AT SIT | SA106GRB |  | M |  | 165 | 534.6
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 30 | 5.7
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 60 | 22.8
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 5 | 8.25
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 10 | 4.3
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 1 | 1.4
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD60.3X5.54 EP STY D D1-49.0 | SA106GRB |  | M |  | 60 | 448.8
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 33.4 X 4.55 - SA106GRB | SA106GRB |  | M |  | 420 | 1360.8
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD 21.3 X 3.73 - SA106GRB | SA106GRB |  | M |  | 240 | 388.8
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 25 | 22.5
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 120 | 45.6
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 35 | 10.5
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB50 CL3000 | SA105 |  | NO |  | 6 | 6
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA105 |  | NO |  | 45 | 13.5
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB50/25 CL3000 | SA105 |  | NO |  | 16 | 36
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 70 | 21
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 1/4"NPT/NB15 | SA105 |  | NO |  | 85 | 29.325
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NIPPLE(CS) 3/8"NPT/NB15 | SA105 |  | NO |  | 85 | 59.5
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 50 CL150 | SA515GR70 |  | NO |  | 2 | 4
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SOW FLANGE NB 25 CL150 | SA515GR70 |  | NO |  | 2 | 1.8
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT HEX GRA 8.8 M16X80 | IS:1364 (P-1) |  | NO |  | 4 | 0.62
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | HEX NUT M16 | IS:1364 (P-3) |  | NO |  | 4 | 0.12
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | BOLT-M12X70 -4.6-IS1364P1 | IS:1363 (P-1) |  | NO |  | 4 | 0.308
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | NUT -M12 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 8 | 0.16
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD33.4X4.55 | SA515GR70 |  | NO |  | 30 | 4.14
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE OD60.3X5.54 | SA515GR70 | 3-80-709-99011 | NO |  | 2 | 0.8
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | PIPE OD114.3 X 6.02 SA106GRB | SA106GRB |  | M |  | 8 | 128.56
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 | SA234WPB |  | NO |  | 2 | 7.68
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 1 | 4.93
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | FLAT END CLOSURE FOROD114.3X6.02 | SA515GR70 |  | NO |  | 1 | 2.19
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/40 CL3000 | SA105 |  | NO |  | 5 | 5
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | ASMEB16.11 SW RED NB50/25 CL3000 | SA105 |  | NO |  | 8 | 8
2 | MEL Mahan 2x800 MW Unit 4 | Condensate for Sealing of Vacuum | Non IBR | 82407 | SW STUB NB15 CL 3000 | SA479TY304 |  | NO |  | 10 | 1.8
2 Total | [10 empty] | 10207.843
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3762 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 32.357
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1733 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.906
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3644 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 31.342
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3079 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 26.482
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4807 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 41.345
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1662 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.295
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2728 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 23.464
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3978 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.215
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2539 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 21.838
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5201 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 44.734
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=298 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.563
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=326 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.804
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=104 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 0.895
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3339 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 28.719
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1739 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.957
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4942 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 42.506
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=892 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 7.672
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=171 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.471
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=562 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.834
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=699 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.012
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=782 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.726
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=780 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 5.178
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=268 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.779
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=3368 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 22.357
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=464 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.08
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=582 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.863
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=5178 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.372
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=673 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.467
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=151 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.002
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=1319 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 8.756
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 3 | 1.29
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 17 | 34
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 45DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 5 | 5.8
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BW EQUAL TEE OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 5.88
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.9BW UNEQT 114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 2.8
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1.75
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 1.54
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 0.56
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=3000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 25.803
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD88.9X3.05L=1000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.638
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X3.05L=2000 | SA312TP304H | 1-80-412-A0533 | NO |  | 1 | 12.92
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | BOTTOM PLATE 10THKX 1500X1500 | SA515GR70 | 1-80-412-A0533 | NO |  | 1 | 176.625
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1977 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 17.004
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD60.3X5.54 L=4000 | SA106GRB | 1-80-412-A0533 | NO |  | 1 | 29.924
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=264 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.271
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2672 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 22.982
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=360 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 3.096
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=242 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.081
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 50.66
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH CARRIER PLATES | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4382 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 37.69
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3039 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 26.138
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=192 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 1.651
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2938 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 25.27
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5544 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 47.684
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1001 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 8.61
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1583 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 13.615
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 8 | 16
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X5.49 L=2500 | SA106GRB | 2-80-412-A0362 | NO |  | 1 | 28.23
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 10MMX500X50010 | SA240TP304L | 2-80-412-A0362 | NO |  | 1 | 40.35
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=2000 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 17.202
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD168.3X3.4/114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 1 | 1.59
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 12MMX150X300 | SA515GR70 | 2-80-412-A0362 | NO |  | 1 | 4.239
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 230 | 591.56
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 50 | 8
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | BW UEQT 60.3X3.91/33.4X3.38 SA403WP316L | SA403WP316L |  | NO |  | 6 | 6.12
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25 SS | SA479TY304 |  | NO |  | 10 | 4.3
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | MULTI HOLE ORIFICE PLATE ASY(NB80)-OP43 | As per drawing | 3-80-412-A0952 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05 L=150MM | SA312TP316L | 3-80-412-A0952 | NO |  | 1 | 0.969
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE T=10THK, Ø84. 6 | SA240TP304 | 3-80-412-A0952 | NO |  | 1 | 0.37
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ORIFICE PLT NB80 (OP44) | As per drawing | 3-80-412-A0954 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05 L=150MM | SA312TP316L | 3-80-412-A0954 | NO |  | 1 | 0.969
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE T=10THK, Ø84.62 | SA240TP304 | 3-80-412-A0954 | NO |  | 1 | 0.37
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | ORIFICE PLT NB100 (OP54)) | As per drawing | 3-80-412-A0955 | NO | A | 2
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 L=200MM SA312TP316L | SA312TP316L | 3-80-412-A0955 | NO |  | 2 | 3.44
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE T=12THK, Ø110.20 | SA240TP304 | 3-80-412-A0955 | NO |  | 2 | 1.39
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD60.3X5.54 EP STY D D1-50.4AT SITE | SA106GRB |  | M |  | 25 | 187
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 8 | 7.2
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-60.3X3.91 EP STY D D1-53.2AT SITE | SA312TP316L |  | M |  | 130 | 726.57
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 18 | 11.7
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 180 | 462.96
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 21 | 3.36
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | SW RED NB50/25 CL3000 SA182F316 | SA182F316 | 4-80-452-85266 | NO |  | 2 | 7.2
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L |  | NO |  | 2 | 3.5
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 60.3 X 3.91 EP STY D D1-53.2 | SA312TP304H |  | M |  | 50 | 272
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP304H |  | NO |  | 10 | 6.5
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 5 | 2.5
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 50 | 125
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD60.3X3.91/33.4X3.38 | SA403WP304L |  | NO |  | 5 | 5.1
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 65 | 923.845
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 14 | 69.58
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD168.3 X3.4 | SA403WP316L |  | NO |  | 2 | 13
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD168.3X3.4/88.9X3.05 | SA403WP316L |  | NO |  | 2 | 11.48
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 1 | 1.43
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 88.90 X 3.05 - SA312TP316L | SA312TP316L |  | M |  | 4 | 26.552
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L |  | NO |  | 2 | 2.32
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 RED OD168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 2 | 3.18
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | SOW FLANGE NB150 CL150 (RF) (SS316L) | SA182F316L |  | NO |  | 4 | 28
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 20 | 6.06
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | NUT -M20 -2H | BPS 41319 |  | NO |  | 40 | 2.6
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 75 | 1065.975
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 6 | 29.82
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 4 | 23.64
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 36 | 309.636
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 14 | 28
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD168.3X3.4/88.9X3.05 | SA403WP316L |  | NO |  | 1 | 5.74
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 1 | 1.43
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 88.90 X 3.05 - SA312TP316L | SA312TP316L |  | M |  | 4 | 26.552
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L |  | NO |  | 2 | 2.32
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 88.90 X 3.05 - SA312TP316L | SA312TP316L |  | M |  | 45 | 298.71
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L |  | NO |  | 10 | 11.6
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD88.9X3.05 | SA403WP316L |  | NO |  | 2 | 3.76
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD273.1 X 4.19 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 26 | 742.352
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD273.1X4.19 | SA403WP316L |  | NO |  | 2 | 33.26
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | BW EQT OD273.0X4.19 SA403WP316L | SA403WP316L |  | NO |  | 2 | 37.2
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | BW UEQT 273X4.19/219.1X3.76 SA403WP316L | SA403WP316L |  | NO |  | 2 | 36.328
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE D219.1 X 3.76 X6000 - SA312TP316L | SA312TP316L |  | M |  | 14 | 287.35
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X3.76 | SA403WP316L |  | NO |  | 2 | 19.14
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ECC RED219.1X3.76/168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 2 | 5.6
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 27 | 383.751
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 6 | 29.82
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 273.1X4.19/168.3X3.4 | SA403WP316L |  | NO |  | 4 | 69.76
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 ECCRED OD168.3X3.4/141.3X3.4 | SA403WP316L |  | NO |  | 4 | 7.16
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD141.3X3.4 L=6000 SA312TP316L | SA312TP316L |  | M |  | 6 | 69.222
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | 90 DEG LR ELBOW OD 141.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 4 | 15.2
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD273X4.19 SA403WP316L | SA403WP316L |  | NO |  | 2 | 8.12
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | BW SR 90DEG ELL OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 2 | 2
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 284.26
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 4 | 19.88
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 172.02
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 4 | 8
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L |  | NO |  | 50 | 21.5
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | SW STUB NB15 SS | SA182F316 | 4-80-473-A0623 | NO |  | 30 | 5.4
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 33.4 X 4.55SA312TP316L | SA312TP316L |  | M |  | 45 | 145.8
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 21.3 X 3.73 SA312TP316L | SA312TP316L |  | M |  | 5 | 8.1
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA403WP316L |  | NO |  | 28 | 5.32
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 60.3 X 3.91 SA312TP316L | SA312TP316L |  | M |  | 20 | 111.78
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | SW STUB NB 50 SS CL:3000-SA182F316 | SA182F316 |  | NO |  | 5 | 4.6
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X6000 - SA312TP316L | SA312TP316L |  | M |  | 270 | 3837.51
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 12 | 59.64
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD168.3 X3.4 | SA403WP316L |  | NO |  | 2 | 13
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 2 | 11.82
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 172.02
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 6 | 12
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD 273.00 X 6.35 X 6000 - SA106GRB | SA106GRB |  | M |  | 270 | 11275.2
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 14 | 366.8
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 2 | 58.22
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 10 | 4.3
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | M |  | 25 | 81
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 18 | 3.42
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | FLAT END CLOSURE OD273X6.35 | SA515GR70 |  | NO |  | 2 | 34.92
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD168.3 X 3.4 X6000 - SA312TP316L | SA312TP316L |  | M |  | 250 | 3553.25
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD168.3X3.4 | SA403WP316L |  | NO |  | 12 | 59.64
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD 168.3X3.4/114.3X3.05 | SA403WP316L |  | NO |  | 2 | 11.82
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD114.3 X 3.05 X 6000 - SA312TP316L | SA312TP316L |  | M |  | 20 | 172.02
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L |  | NO |  | 4 | 8
3 | MEL Mahan 2x800 MW Unit 3 | Demineralised Water System (SS) | Non IBR | 82473 | BW PIPE CAP OD168.3X3.4 SA403WP316L | SA403WP316L |  | NO |  | 2 | 2.86
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3762 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 32.357
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1733 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.906
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3644 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 31.342
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3079 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 26.482
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4807 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 41.345
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1662 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.295
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2728 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 23.464
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3978 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.215
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2539 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 21.838
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5201 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 44.734
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=298 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.563
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=326 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 2.804
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=104 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 0.895
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3339 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 28.719
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1739 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 14.957
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4942 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 42.506
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=892 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 7.672
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=171 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.471
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1192 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 10.252
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=562 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.834
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=699 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.012
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=782 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.726
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=780 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 5.178
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=268 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.779
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=3368 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 22.357
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=464 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.08
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=582 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 3.863
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 1 | 0.43
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=5178 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 34.372
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=673 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 4.467
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=151 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 1.002
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.93X3.05 WITH STUB | As per drawing | 1-80-412-A0533 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD88.9X3.05L=1319 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 8.756
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.11 SW STUB NB25,CL:3000 | SA479TY316L | 1-80-412-A0533 | NO |  | 3 | 1.29
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 17 | 34
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 45DEG ELBOW OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 5 | 5.8
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BW EQUAL TEE OD114.3X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 5.88
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASME B16.9BW UNEQT 114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 2.8
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 1.75
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD114.3X3.05/88.9X3.05 | SA403WP316L | 1-80-412-A0533 | NO |  | 2 | 1.54
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD88.9X3.05/60.3X3.91 | SA403WP316L | 1-80-412-A0533 | NO |  | 1 | 0.56
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=3000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 25.803
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD88.9X3.05L=1000 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 6.638
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X3.05L=2000 | SA312TP304H | 1-80-412-A0533 | NO |  | 1 | 12.92
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | BOTTOM PLATE 10THKX 1500X1500 | SA515GR70 | 1-80-412-A0533 | NO |  | 1 | 176.625
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1977 | SA312TP316L | 1-80-412-A0533 | NO |  | 1 | 17.004
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD60.3X5.54 L=4000 | SA106GRB | 1-80-412-A0533 | NO |  | 1 | 29.924
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=264 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.271
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2672 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 22.982
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=360 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 3.096
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=242 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 2.081
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 50.66
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH CARRIER PLATES | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5980 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 51.434
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=4382 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 37.69
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=3039 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 26.138
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=192 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 1.651
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=2938 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 25.27
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05 WITH STUB | As per drawing | 2-80-412-A0362 | NO | A | 1
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=5544 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 47.684
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25,CL:300 0 | SA479TY316L | 2-80-412-A0362 | NO |  | 1 | 0.43
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1001 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 8.61
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE OD114.3X3.05L=1583 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 13.615
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 8 | 16
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | SUPPORT PIPE OD88.9X5.49 L=2500 | SA106GRB | 2-80-412-A0362 | NO |  | 1 | 28.23
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 10MMX500X50010 | SA240TP304L | 2-80-412-A0362 | NO |  | 1 | 40.35
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE PIPE OD114.3X3.05L=2000 | SA312TP316L | 2-80-412-A0362 | NO |  | 1 | 17.202
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 RED OD168.3X3.4/114.3X3.05 | SA403WP316L | 2-80-412-A0362 | NO |  | 1 | 1.59
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PLATE 12MMX150X300 | SA515GR70 | 2-80-412-A0362 | NO |  | 1 | 4.239
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | SPARE CARRIER PLATE 8MM 50X60 | SA240TP316L | 2-80-412-A0362 | NO |  | 4 | 0.776
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 230 | 591.56
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 50 | 8
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | BW UEQT 60.3X3.91/33.4X3.38 SA403WP316L | SA403WP316L |  | NO |  | 6 | 6.12
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82412 | SW STUB NB25 SS | SA479TY304 |  | NO |  | 10 | 4.3
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE OD60.3X5.54 EP STY D D1-50.4AT SITE | SA106GRB |  | M |  | 25 | 187
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 8 | 7.2
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-60.3X3.91 EP STY D D1-53.2AT SITE | SA312TP316L |  | M |  | 130 | 726.57
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 18 | 11.7
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 180 | 462.96
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 21 | 3.36
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82473 | SW RED NB50/25 CL3000 SA182F316 | SA182F316 | 4-80-452-85266 | NO |  | 2 | 7.2
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD88.9X3.05/60.3X3.91 | SA403WP316L |  | NO |  | 2 | 3.5
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 60.3 X 3.91 EP STY D D1-53.2 | SA312TP304H |  | M |  | 50 | 272
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP304H |  | NO |  | 10 | 6.5
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 5 | 2.5
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82473 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 50 | 125
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
3 | MEL Mahan 2x800 MW Unit 4 | Demineralised Water System (SS) | Non IBR | 82473 | ASMEB16.9 UEQT OD60.3X3.91/33.4X3.38 | SA403WP304L |  | NO |  | 5 | 5.1
3 Total | [10 empty] | 34697.769
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1016 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 807.859
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PLATE 2500X2500X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 1 | 785
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT PIPE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=208 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 165.415
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=698 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 555.018
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 30DEG OD2032X16(R=0.75D)L=819 | SA515GR70 | 3-80-363-31709 | NO |  | 1 | 651.236
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 90DEG (R=0.75D) L=2457 | SA515GR70 | 3-80-363-31710 | NO |  | 2 | 3907.416
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | IMPULSE PIPE OD21.3X3.73 L=2750 | SA106GRB | 1-80-363-A0539 | NO |  | 4 | 17.82
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SPARE PIPE OD323.9X9.53 L=1000 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 73.88
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BLIND FLANGE ASSY. NB500 CL150 | SA515GR70 | 3-80-362-11781 | NO |  | 2 | 252
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STUD M30X200 | SA193B16 | 1-80-363-A0539 | NO |  | 44 | 37.4
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | HEX. NUT M30 | A194GR2H | 1-80-363-A0539 | NO |  | 88 | 20.24
4 | MEL Mahan 2x800 MW Unit 3 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | GASKET, T=3 800X8 00 | NON-ASBESTOS | 1-80-363-A0539 | NO |  | 2 | 7.284
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1016 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 807.859
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PLATE 2500X2500X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 1 | 785
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT PIPE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2476 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 1968.906
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & MANHOLE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=2649 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2106.438
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 130.216
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 63.302
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 49.454
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD 508X12.7 L=250 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 38.775
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SOW. FLANGE NB500 CL.150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 1 | 54
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=208 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 165.415
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=698 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 555.018
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH SUPPORT & STUBS | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=3442 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 2736.906
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 607X427X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 260.432
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 840X400X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 126.604
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 450X350X20 | SA515GR70 | 1-80-363-A0539 | NO |  | 4 | 98.908
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BRANCH PIPE OD323.9X9.53 L=200 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 14.77
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | TEMPERATURE STUB RC 1" L=45 | SA105 | 4-80-463-63321 | NO |  | 4 | 3.536
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SCREW PLUG R 1" | SA105 | 4-80-400-58724 | NO |  | 4 | 0.8
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | ASME B16.11 CL3000 SW STUB NB15(CS) | SA105 | 1-80-363-A0539 | NO |  | 5 | 0.9
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16 WITH LUG PLATE | As per drawing | 1-80-363-A0539 | NO | A | 1
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PIPE OD2032X16L=1062 | SA515GR70 | 3-80-363-A0860 | NO |  | 1 | 844.534
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BOTTOM PLATE 750X474X25 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 139.534
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | PAD PLATE 717X375X12 | SA515GR70 | 1-80-363-A0539 | NO |  | 2 | 50.656
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STIFFNER PLATE 740X275X16 | SA515GR70 | 1-80-363-A0539 | NO |  | 8 | 204.48
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 30DEG OD2032X16(R=0.75D)L=819 | SA515GR70 | 3-80-363-31709 | NO |  | 1 | 651.236
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | MITRE BEND 90DEG (R=0.75D) L=2457 | SA515GR70 | 3-80-363-31710 | NO |  | 2 | 3907.416
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | IMPULSE PIPE OD21.3X3.73 L=2750 | SA106GRB | 1-80-363-A0539 | NO |  | 4 | 17.82
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | SPARE PIPE OD323.9X9.53 L=1000 | SA106GRB | 1-80-363-A0539 | NO |  | 1 | 73.88
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | BLIND FLANGE ASSY. NB500 CL150 | SA515GR70 | 3-80-362-11781 | NO |  | 2 | 252
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | STUD M30X200 | SA193B16 | 1-80-363-A0539 | NO |  | 44 | 37.4
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | HEX. NUT M30 | A194GR2H | 1-80-363-A0539 | NO |  | 88 | 20.24
4 | MEL Mahan 2x800 MW Unit 4 | Exhaust Steam from Prime Movers- TG Scope | Non IBR | 82363 | GASKET, T=3 800X8 00 | NON-ASBESTOS | 1-80-363-A0539 | NO |  | 2 | 7.284
4 Total | [10 empty] | 51105.628
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | PIPE OD 273.00 X 6.35 X 6000 - SA106GRB | SA106GRB |  | M |  | 90 | 3758.4
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 14 | 366.8
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 1 | 29.11
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 5 | 2.15
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | PIPE 33.40 X 4.55 - SA106GRB | SA106GRB |  | M |  | 6 | 19.44
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82408 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 4 | 0.76
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 88.9X5.49 EPD-79.0 AT SHOP | SA106GRB |  | M |  | 580 | 6554
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 - EP-D24.7(SITE L=40M | SA106GRB |  | M |  | 40 | 129.6
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD60.3X5.54 L=35M EP STY-D49.3(SITE | SA106GRB |  | M |  | 35 | 261.835
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 134 | 270.68
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 45DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 14 | 14.14
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 12 | 10.8
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 21 | 69.09
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 UEQT OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 14.85
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 4.3
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/48.3X5.08 | SA234WPB |  | NO |  | 5 | 3.85
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 15 | 2.85
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 EPSTY-D D1=24.7(SITE) | SA106GRB |  | M |  | 25 | 81
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 40 | 17.2
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NB50 OILHOSEASPERIS635 L=15 M WITH END | Rubber Hose |  | NO |  | 2 | 50
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT END CLOSURE OD88.9X5.49 | SA515GR70 |  | NO |  | 8 | 8.32
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT FACED FLANGE NB80 CL 150 SA105 | SA515GR70 | 4-80-340-73230 | NO |  | 4 | 36
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | STUD M16 X 2 X 160 SA193B7 | SA193B7 |  | NO |  | 10 | 2.24
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NUT -M16 -2H | A194GR2H |  | NO |  | 20 | 0.6
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 15 | 2.7
5 | MEL Mahan 2x800 MW Unit 3 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 21.3 X 4.78 L=10M | SA106GRB |  | M |  | 10 | 19.5
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 88.9X5.49 EPD-79.0 AT SHOP | SA106GRB |  | M |  | 580 | 6554
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 - EP-D24.7(SITE L=40M | SA106GRB |  | M |  | 40 | 129.6
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD60.3X5.54 L=35M EP STY-D49.3(SITE | SA106GRB |  | M |  | 35 | 261.835
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 134 | 270.68
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 45DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 14 | 14.14
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 12 | 10.8
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 21 | 69.09
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 UEQT OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 14.85
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 5 | 4.3
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 RED OD88.9X5.49/48.3X5.08 | SA234WPB |  | NO |  | 5 | 3.85
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 15 | 2.85
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE 33.40 X 4.55 EPSTY-D D1=24.7(SITE) | SA106GRB |  | M |  | 25 | 81
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 40 | 17.2
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NB50 OILHOSEASPERIS635 L=15 M WITH END | Rubber Hose |  | NO |  | 2 | 50
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT END CLOSURE OD88.9X5.49 | SA515GR70 |  | NO |  | 8 | 8.32
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | FLAT FACED FLANGE NB80 CL 150 SA105 | SA515GR70 | 4-80-340-73230 | NO |  | 4 | 36
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | STUD M16 X 2 X 160 SA193B7 | SA193B7 |  | NO |  | 10 | 2.24
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | NUT -M16 -2H | A194GR2H |  | NO |  | 20 | 0.6
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 15 | 2.7
5 | MEL Mahan 2x800 MW Unit 4 | Fuel / Lube Oil Supply & Return Piping | Non IBR | 82673 | PIPE OD 21.3 X 4.78 L=10M | SA106GRB |  | M |  | 10 | 19.5
5 Total | [10 empty] | 19291.37
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 90 | 561.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 120 | 358.8
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 7
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 15.25
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 2
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 24
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 1
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 220 | 1372.8
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 27.45
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 3
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB 50/40 IS1239 | IS1239 G&T |  | NO |  | 2 | 3.4
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 12 | 53.64
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 40 | 119.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 1.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 19.2
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 70 | 35
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 40 | 12
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 40 | 60
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 25 | 74.75
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 1.2
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 19.2
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 3
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 525 | 7717.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 360
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 45DEG BEND NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 28
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 48
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/150 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/100 G&T | As per drawing | 2-80-614-A0308 | NO | A | 4
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 4 | 40.284
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 4 | 8.984
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 27.879
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 30
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 22 | 88
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 4 | 41.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 10 | 28
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 299
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 45 | 9
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 54
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 42.155
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 130 | 169
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 98 | 410.13
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 180 | 40.32
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 40 | 18.72
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/25 | As per drawing | 2-80-616-10294 | NO | A | 5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/15 | As per drawing | 2-80-616-10294 | NO | A | 10
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB200 IS1239 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB200 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 60 | 179.4
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 120 | 24
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | EQTEE NB25 IS1239 GAL | IS1239 G&T |  | NO |  | 60 | 0.3
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 60 | 24
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 60 | 87.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 60 | 6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/25 | As per drawing | 2-80-614-A0308 | NO | A | 8
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 8 | 53.712
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 8 | 1.52
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 52 | 156
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 42.155
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 358 | 2233.92
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1575 | 4709.25
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 125 | 182.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 36 | 3.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 210 | 42
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 53.375
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 36 | 5.76
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 9
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 18 | 7.2
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 80
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 10 | 23
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 40 | 5.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | NUT -M16 -2H | A194GR2H |  | NO |  | 80 | 2.4
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 10 | 10
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 100 | 50
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 400 | 120
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 75 | 112.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 150
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 50 | 25
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 30 | 3
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 25 | 7.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 2
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB25 IS1239 GAL L=75MM | IS1239 G&T | 3-80-612-21071 | NO |  | 34 | 7.616
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 30 | 9
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SCREWED NIPPLE NB40 IS1239 | IS1239 G&T | 3-80-612-21072 | NO |  | 4 | 2.68
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 40 IS1239 | IS1239 G&T |  | NO |  | 15 | 12
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 250 | 5475
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 685 | 4274.4
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1405 | 4200.95
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 3335 | 4869.1
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 10 | 360
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 25 | 260
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 92 | 140.3
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 230 | 46
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 1020 | 102
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 27.25
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 9.504
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 0.8
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 4
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 108
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 295.085
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150/15 | As per drawing | 2-80-616-06449 | NO | A | 10
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4 L=200 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 42.4
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 L=65.4 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 0.94
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 60 | 72
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 365 | 146
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 32 | 16
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 10
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 4
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD NB50X4.5 | IS1239 BLACK | 4-80-612-50147 | NO |  | 50 | 46.25
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | SOCKET NB200 (GALVANISED) | IS3589-410MPA G&T | 4-80-616-71901 | NO |  | 25 | 157.65
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 65 | 97.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 175 | 87.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 360 | 108
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 840 | 84
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 200 IS1239 | IS1239 G&T |  | NO |  | 17 | 102
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 150 IS1239 | IS1239 G&T |  | NO |  | 45 | 441
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 120 | 180
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 25 IS1239 | IS1239 G&T |  | NO |  | 240 | 120
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 560 | 168
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB50 IS1239 L=150 | IS1239 G&T | 3-80-612-21073 | NO |  | 50 | 46.25
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB25 IS1239 L=150 | IS1239 G&T | 3-80-612-21071 | NO |  | 200 | 89.2
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB15 IS1239 L=150 | IS1239 G&T | 3-80-612-21070 | NO |  | 450 | 98.1
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25 WITH THREAD 1"BSP(M) | SA106GRB | 4-80-612-82549 | NO |  | 2 | 0.648
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 40 | 10.24
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD ISO7 RC-1-1/2"(F)(GAL) | SA105 (Galvanized) | 4-80-612-A0578 | NO |  | 65 | 91
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 525 | 7717.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 360
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 45DEG BEND NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 28
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB100 IS1239G&T | IS1239 G&T |  | NO |  | 12 | 72
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | UEQT 200/100 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 3
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 3 | 30.213
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 3 | 6.738
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 60
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 5 | 14
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/150 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 41.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 50 | 149.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/25 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 60
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/15 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 10
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB200 IS3589 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB200 IS3589 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 128 | 166.4
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 95 | 397.575
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 150 | 33.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 24 | 11.232
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB150 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 4 | 78.776
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB100 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 8 | 83.056
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | STUD M16 X 2 X 110 SA193B7 | SA193B7 |  | NO |  | 64 | 9.28
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 128 | 3.84
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 32 | 9.696
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M20 -2H | BPS 41319 |  | NO |  | 64 | 4.16
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 925 | 1350.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1640 | 4903.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 447
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 240 | 1497.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 86 | 13.76
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 58 | 29
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 218 | 87.2
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 7.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 20 | 24
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 341 | 34.1
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 418 | 83.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 53 | 80.825
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 2 | 4.6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 8 | 1.12
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 16 | 0.48
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 2 | 2
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB25 CL150- G&T | IS2062 |  | NO |  | 60 | 0.3
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 240 | 19.2
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 480 | 12
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB25CL150(GALV) | SA105 (Galvanized) |  | NO |  | 60 | 60
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB15 CL150- G&T | IS2062 |  | NO |  | 50 | 0.25
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 200 | 16
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 400 | 10
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB15 CL150(GALV | IS2062 |  | NO |  | 50 | 45
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 70 | 35
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 420 | 126
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 50 | 75
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 330 | 165
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 15 | 7.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 230 | 23
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 180 | 54
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB15 IS1239G&T | IS1239 G&T |  | NO |  | 50 | 5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 12
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 40 IS1239 | IS1239 G&T |  | NO |  | 20 | 16
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB 40 IS1239 | IS1239 G&T |  | NO |  | 12 | 4.8
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 200 | 2940
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB50X4.5 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 525 | 3276
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB25X4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 2200 | 6578
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 5850 | 8541
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 8 | 288
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 80
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 76.25
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 420 | 84
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1250 | 125
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 75 | 22.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB 200/100 IS1239 G&T | As per drawing | 2-80-616-10294 | NO | A | 2
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.0 L=300 | IS3589-410MPA | 2-80-616-10294 | NO |  | 2 | 18.918
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-616-10294 | NO |  | 2 | 4.492
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 1 | 6
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/50 IS1239 G&T | IS1239 G&T |  | NO |  | 13 | 52
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 140
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 12
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 48
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/15 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 108
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 20
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB25/15 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 120
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 50 IS1239 G7T | IS1239 G&T |  | NO |  | 10 | 5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 15 IS1239 G&T | IS1239 G&T |  | NO |  | 200 | 20
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB50X4.05 | IS1239 BLACK | 4-80-612-50147 | NO |  | 40 | 37
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB25X3.25 | IS1239 BLACK | 4-80-612-50147 | NO |  | 250 | 111.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB15X4.50 | IS1239 BLACK | 4-80-612-50147 | NO |  | 650 | 141.7
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 65
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 135 | 67.5
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB25 IS1329 G&T | IS1239 G&T |  | NO |  | 550 | 165
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1470 | 147
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 146.475
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 135
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 370 | 185
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 980 | 294
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0575 | NO |  | 10 | 6.17
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0574 | NO |  | 100 | 29.7
6 | MEL Mahan 2x800 MW Unit 3 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1/2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0573 | NO |  | 650 | 94.25
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 90 | 561.6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 120 | 358.8
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 7
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 15.25
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 2
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 24
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 1
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 170 | 1060.8
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 14 | 21.35
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 3
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB 50/40 IS1239 | IS1239 G&T |  | NO |  | 2 | 3.4
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 12 | 53.64
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 40 | 119.6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 1.6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 19.2
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 60 | 30
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 35 | 10.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 32 | 48
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 12.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 18 | 53.82
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 1.2
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 16
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82478 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 6 | 3
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 585 | 8599.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 98 | 392
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 45DEG BEND NB100IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 42
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 48
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/150 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | UEQT 200/100 G&T | As per drawing | 2-80-614-A0308 | NO | A | 4
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 4 | 40.284
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 4 | 8.984
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 27.879
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 10 | 30
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 22 | 88
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 4 | 41.6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 10 | 28
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 299
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 45 | 9
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 15
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 54
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 42.155
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 130 | 169
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 98 | 410.13
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 180 | 40.32
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 40 | 18.72
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/25 | As per drawing | 2-80-616-10294 | NO | A | 5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 200/15 | As per drawing | 2-80-616-10294 | NO | A | 10
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB200 IS1239 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB200 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 358 | 2233.92
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1575 | 4709.25
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 125 | 182.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 36 | 3.6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 210 | 42
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 53.375
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 36 | 5.76
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 18 | 9
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 18 | 7.2
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 80
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 10 | 23
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 40 | 5.6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | NUT -M16 -2H | A194GR2H |  | NO |  | 80 | 2.4
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 10 | 10
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 100 | 50
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 400 | 120
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 75 | 112.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 150
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 25 | 12.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 30 | 3
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 25 | 7.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82610 | G&T PLUG NB15 IS1239G&T | IS1239 G&T |  | NO |  | 10 | 1
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 250 | 5475
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 685 | 4274.4
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1405 | 4200.95
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 3335 | 4869.1
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 10 | 360
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB150 IS1239 | IS1239 G&T |  | NO |  | 25 | 260
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 92 | 140.3
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 230 | 46
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 1020 | 102
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB150 / 100 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 27.25
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 9.504
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 1.6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB50 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 2 | 0.8
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 4
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 12 | 108
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 295.085
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB150/15 | As per drawing | 2-80-616-06449 | NO | A | 10
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB150X5.4 L=200 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 42.4
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB15X3.2 L=65.4 | IS1239 BLACK | 2-80-616-06449 | NO |  | 10 | 0.94
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 60 | 72
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 365 | 146
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 3 | 30.33
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 32 | 16
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 10
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 10.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PLUG NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 4
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD NB50X4.5 | IS1239 BLACK | 4-80-612-50147 | NO |  | 50 | 46.25
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | SOCKET NB200 (GALVANISED) | IS3589-410MPA G&T | 4-80-616-71901 | NO |  | 25 | 157.65
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 65 | 97.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 175 | 87.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 360 | 108
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 840 | 84
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 200 IS1239 | IS1239 G&T |  | NO |  | 17 | 102
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 150 IS1239 | IS1239 G&T |  | NO |  | 45 | 441
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 120 | 180
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 25 IS1239 | IS1239 G&T |  | NO |  | 240 | 120
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 560 | 168
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB50 IS1239 L=150 | IS1239 G&T | 3-80-612-21073 | NO |  | 50 | 46.25
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB25 IS1239 L=150 | IS1239 G&T | 3-80-612-21071 | NO |  | 200 | 89.2
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | G&T NIPPLE NB15 IS1239 L=150 | IS1239 G&T | 3-80-612-21070 | NO |  | 450 | 98.1
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE NB25 WITH THREAD 1"BSP(M) | SA106GRB | 4-80-612-82549 | NO |  | 2 | 0.648
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | FORGED CAP 1/2" (NPT-F) | SA105 | 4-80-418-85268 | NO |  | 40 | 10.24
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82612 | PIPE WITH THREAD ISO7 RC-1-1/2"(F)(GAL) | SA105 (Galvanized) | 4-80-612-A0578 | NO |  | 65 | 91
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 100X5.4SCREW&SOCKETED IS1239 GA | IS1239 G&T |  | M |  | 580 | 8526
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 100 | 400
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 45DEG BEND NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 28
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE DIA 219.1 X 6.4IS3589-410-GALV | IS3589-410MPA G&T | 4-80-614-A0536 | M |  | 120 | 4028.4
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | 90DEG PIPEBEND R=400OD219.1X6.4L=828-GAL | IS3589-410MPA G&T | 3-80-614-A0783 | NO |  | 4 | 111.184
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB100 IS1239G&T | IS1239 G&T |  | NO |  | 15 | 90
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | UEQT 200/100 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 3
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=300 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 3 | 30.213
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 3 | 6.738
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 60
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 100/15 IS1239 | IS1239 G&T |  | NO |  | 5 | 14
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/150 IS3589 G&T | As per drawing | 2-80-614-A0308 | NO | A | 2
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=500 | IS3589-410MPA | 2-80-614-A0308 | NO |  | 2 | 33.57
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB150X5.4 L=225 | IS1239 BLACK | 2-80-614-A0308 | NO |  | 2 | 9.54
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 41.6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 150X5.4SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 10 | 219
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 50 | 149.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/25 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 5 | 33.57
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE NB25X4.0 L=64 | IS1239 BLACK | 2-80-616-10294 | NO |  | 5 | 0.95
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 60
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB100 / 50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 20
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 200/15 IS3589 G&T | As per drawing | 2-80-616-10294 | NO | A | 10
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPE OD219.1X6.4 L=200 | IS3589-410MPA | 2-80-616-10294 | NO |  | 10 | 67.14
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB15X 3.2 IS1239BL L=54 | IS1239 BLACK | 2-80-616-10294 | NO |  | 10 | 3.33
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB200 IS3589 G&T | IS3589-410MPA G&T | 4-80-610-A0428 | NO |  | 24 | 161.136
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB200 IS3589 G&T | IS1239 G&T |  | NO |  | 18 | 108
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 128 | 166.4
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 100 IS1239 | IS1239 G&T |  | NO |  | 95 | 397.575
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB15 IS1239 GAL | IS1239 G&T | 3-80-612-21070 | NO |  | 340 | 37.4
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB25 IS1239 GAL | IS1239 G&T | 3-80-612-21071 | NO |  | 150 | 33.6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | SCREWED NIPPLE NB50 IS1239 GAL | IS1239 G&T | 3-80-612-21073 | NO |  | 24 | 11.232
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 150 IS1239 | IS1239 G&T |  | NO |  | 6 | 9
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB150 IS1239 G&T | IS1239 G&T |  | NO |  | 4 | 39.2
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB150 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 4 | 78.776
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FLAT FACED FLANGE SCREWED NB100 (GAL) | IS2062E250GRBR | 3-80-614-A0784 | NO |  | 8 | 83.056
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | STUD M16 X 2 X 110 SA193B7 | SA193B7 |  | NO |  | 64 | 9.28
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 128 | 3.84
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 32 | 9.696
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M20 -2H | BPS 41319 |  | NO |  | 64 | 4.16
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 925 | 1350.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 25X4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 1640 | 4903.6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 40X 4.0 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 100 | 447
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | PIPENB 50X4.50SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 240 | 1497.6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB25 / 15 IS1239 G&T | IS1239 G&T |  | NO |  | 86 | 13.76
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 58 | 29
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 25/15 IS1239 | IS1239 G&T |  | NO |  | 218 | 87.2
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T RED NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 20
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 5 | 7.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB50 / 25 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 32
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UEQT NB 50/15 IS1239 | IS1239 G&T |  | NO |  | 20 | 24
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 341 | 34.1
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 418 | 83.6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 15 | 6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 53 | 80.825
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLINDFLANGE NB50CL150 GALV | SA105 (Galvanized) |  | NO |  | 2 | 4.6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 8 | 1.12
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M16 -2H | A194GR2H |  | NO |  | 16 | 0.48
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB50CL150(GALV) | SA105 (Galvanized) |  | NO |  | 2 | 2
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB25 CL150- G&T | IS2062 |  | NO |  | 60 | 0.3
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 240 | 19.2
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 480 | 12
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB25CL150(GALV) | SA105 (Galvanized) |  | NO |  | 60 | 60
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASME B16.5 RF BLIND FLANGE NB15 CL150- G&T | IS2062 |  | NO |  | 50 | 0.25
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | FT STUD-M14X80 -B7 | SA193B7 |  | NO |  | 200 | 16
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | NUT -M14 2H | IS:1363 (P-3) |  | NO |  | 400 | 10
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | ASMEB16.5 RF FLANGE SCRD NB15 CL150(GALV | IS2062 |  | NO |  | 50 | 45
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 50 IS1239 | IS1239 G&T |  | NO |  | 70 | 35
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 25 IS1239 | IS1239 G&T |  | NO |  | 420 | 126
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 50 IS1239 | IS1239 G&T |  | NO |  | 50 | 75
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 330 | 165
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB50 IS1239G&T | IS1239 G&T |  | NO |  | 15 | 7.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB25 IS1239G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB 15 IS1239 | IS1239 G&T |  | NO |  | 230 | 23
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 15 IS1239 | IS1239 G&T |  | NO |  | 180 | 54
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB15 IS1239G&T | IS1239 G&T |  | NO |  | 50 | 5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T SOCKET NB40 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 12
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T UNION NB 40 IS1239 | IS1239 G&T |  | NO |  | 20 | 16
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82614 | G&T PLUG NB 40 IS1239 | IS1239 G&T |  | NO |  | 12 | 4.8
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.4 GALVANISED AND THREADED | IS3589-410MPA G&T | 4-80-616-71909 | M |  | 100 | 3153
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 200 | 2940
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB50X4.5 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 525 | 3276
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB25X4 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 2200 | 6578
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB15X3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 5850 | 8541
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | 90DEG PIPE BEND R=600 OD 219.1X6 L=1142-GAL | IS3589-410MPA G&T | 3-80-616-27716 | NO |  | 8 | 288
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 20 | 80
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 76.25
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 420 | 84
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T 90DEG ELL NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1250 | 125
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | ASMEB16.11 SW RED NB25/15 CL3000 | SA105 |  | NO |  | 75 | 22.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB 200/100 IS1239 G&T | As per drawing | 2-80-616-10294 | NO | A | 2
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE OD219.1X6.0 L=300 | IS3589-410MPA | 2-80-616-10294 | NO |  | 2 | 18.918
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NB100X5.4 L=156 | IS1239 BLACK | 2-80-616-10294 | NO |  | 2 | 4.492
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 1 | 6
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/50 IS1239 G&T | IS1239 G&T |  | NO |  | 13 | 52
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/25 IS1239 G&T | IS1239 G&T |  | NO |  | 25 | 75
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB100/15 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 140
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 8 | 12
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/25 IS1239 G&T | IS1239 G&T |  | NO |  | 30 | 48
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB50/15 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 108
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 40 | 20
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UEQT NB25/15 IS1239 G&T | IS1239 G&T |  | NO |  | 300 | 120
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T EQT NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 100 | 30
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 50 IS1239 G7T | IS1239 G&T |  | NO |  | 10 | 5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 25 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 15
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T PLUG NB 15 IS1239 G&T | IS1239 G&T |  | NO |  | 200 | 20
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB50X4.05 | IS1239 BLACK | 4-80-612-50147 | NO |  | 40 | 37
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB25X3.25 | IS1239 BLACK | 4-80-612-50147 | NO |  | 250 | 111.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE WITH THREAD NB15X4.50 | IS1239 BLACK | 4-80-612-50147 | NO |  | 650 | 141.7
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 50 | 65
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 135 | 67.5
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB25 IS1329 G&T | IS1239 G&T |  | NO |  | 550 | 165
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T SOCKET NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 1470 | 147
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB100 IS1239 G&T | IS1239 G&T |  | NO |  | 35 | 146.475
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB50 IS1239 G&T | IS1239 G&T |  | NO |  | 90 | 135
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB25 IS1239 G&T | IS1239 G&T |  | NO |  | 370 | 185
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | G&T UNION NB15 IS1239 G&T | IS1239 G&T |  | NO |  | 980 | 294
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0575 | NO |  | 10 | 6.17
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0574 | NO |  | 100 | 29.7
6 | MEL Mahan 2x800 MW Unit 4 | Service Air- Comp Suct & Dis to Receiver | Non IBR | 82616 | PIPE NIPPLE 1/2" NPT(M)/THREAD IS554 | IS1239 BLACK | 4-80-616-A0573 | NO |  | 650 | 94.25
6 Total | [10 empty] | 205766.833
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 323.9X6.4 EP STY D D1-311.2 | IS3589-410MPA |  | M |  | 20 | 1001
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 273.1 X 6.4 EP STY D-D1 260.3 | IS3589-410MPA |  | M |  | 65 | 2735.85
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 219.1 X 6.4 EP STY D-D1 206.3 | IS3589-410MPA |  | M |  | 300 | 10071
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB150X5.4 EP STY D-D1-156.8 | IS1239 BLACK |  | M |  | 640 | 13568
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB100X5.4 EP STY D-D1-105.3 | IS1239 BLACK |  | M |  | 140 | 2016
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB80X4.8 EP STY D-D1-80.8 | IS1239 BLACK |  | M |  | 920 | 9292
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB50X4.5 EP STY D-D1-52.7 | IS1239 BLACK |  | M |  | 400 | 2468
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB40X 4.0 EP STY D-D1-41.5 | IS1239 BLACK |  | M |  | 310 | 1373.3
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB25X4.0 EP STY D-D1-26.9 | IS1239 BLACK |  | M |  | 725 | 2153.25
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB15X 3.2 EP STY D-D1-15.9 | IS1239 BLACK |  | M |  | 680 | 986
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 12 | 200.4
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 10 | 262
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 208
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 150
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 280.8
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 116.1
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 30
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 24
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 140 | 14
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 6 | 214.2
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 11
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 33
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 18
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 3.6
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 10.5
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD273X6.35/88.9X5.49 | SA234WPB |  | NO |  | 4 | 101.28
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 12 | 180
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 58
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 65 | 104
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 16.5
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 24
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 24
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 93.75
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 33
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 13.5
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 17.5
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 85 | 25.5
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 1
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 5
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 4 | 20
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 18
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | UEQT NB 150/100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 31
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/88.9X5.49 | SA234WPB |  | NO |  | 8 | 135.04
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD168.3X7.11/60.3X5.54 | SA234WPB |  | NO |  | 10 | 113.9
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 9
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 10
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 18
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 2.5
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 3 | 0.6
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 1.5
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/50) | As per drawing | 3-80-999-97670 | NO |  | 15 | 99.375
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/40) | As per drawing | 3-80-999-97669 | NO |  | 18 | 119.25
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/25) | As per drawing | 3-80-999-97668 | NO |  | 30 | 216.75
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/15) | As per drawing | 3-80-999-97667 | NO |  | 5 | 36.125
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB15 CL3000 | SA105 |  | NO |  | 130 | 23.4
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB25 CL3000 | SA105 |  | NO |  | 50 | 21.5
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB40 CL3000 | SA105 |  | NO |  | 25 | 18.75
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB50 CL3000 | SA105 |  | NO |  | 30 | 39.9
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=45 | SA105 |  | NO |  | 10 | 5
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=64 | SA105 |  | NO |  | 120 | 84
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB15 | SA106GRB | 3-80-463-27244 | NO |  | 430 | 104.49
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB25 | IS1239 BLACK | 3-80-463-27244 | NO |  | 95 | 42.37
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB40 | IS1239 BLACK | 3-80-463-27244 | NO |  | 18 | 11.952
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB50 | IS1239 BLACK | 3-80-463-27244 | NO |  | 64 | 59.2
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PLUG FOR THERMO COUPLE NIPPLE M33X2 (CS) | SA105 |  | NO |  | 130 | 104
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PACKING RING | IS1972 |  | NO |  | 130 | 1.3
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 310 | 17084.1
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD406.4X6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 105 | 6220.2
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD273.1X6.0 EP STY 'D' D1=261.1 | IS3589-410MPA |  | M |  | 50 | 1975
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB25X4.0 BLACK EP STY 'D' D1=26.9 | IS1239 BLACK |  | M |  | 175 | 519.75
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB50X4.5 EP ST Y D D1=52.7 | IS1239 BLACK |  | M |  | 85 | 524.45
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.0 EP STY 'D' D1=207.1 | IS3589-410MPA |  | M |  | 85 | 2680.05
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.35 EP STY 'D' D1=206.4 | SA106GRB |  | M |  | 35 | 1165.85
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB80 X 4.8 EP STY 'D' D1=80.8 SHOP | IS1239 BLACK |  | M |  | 25 | 252.5
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90 X 5.49 STY'D',78 SHOP | SA106GRB |  | M |  | 5 | 56.45
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90X11.13 STY'D',69.2 SHOP | SA106GRC |  | M |  | 120 | 2562
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE DIA 33.4 X 9.09 EP STY 'D' D1=17.2 | SA106GRC |  | M |  | 20 | 109
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 20 | 915.8
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 12 | 314.4
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 7
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 15 | 250.5
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL 90DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 15.48
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X11.13 | SA234WPC |  | NO |  | 12 | 45.84
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X9.09 | SA234WPC |  | NO |  | 6 | 1.98
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 30.4
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 2 | 4.04
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD355.6X6.35 | SA234WPB |  | NO |  | 4 | 196.56
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD406.4X9.53/219.1X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 161.44
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 112.3
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/219.1X6.35 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 54.83
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/88.9X5.49 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 3.84
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 3
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 32
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD88.9X11.13 | SA234WPC |  | NO |  | 1 | 6.21
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD88.9X11.13/60.3X11.07 | SA234WPC |  | NO |  | 2 | 11.16
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB15 | SA105 | 4-80-329-79004 | NO |  | 10 | 1.8
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB25 | SA105 | 4-80-329-79005 | NO |  | 30 | 12.9
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | TEMP.STUB M33X2 L=45 | SA105 |  | NO |  | 2 | 1
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 4 | 83.88
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 5 | 39.5
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED NB80/PUMP END | IS1239 |  | NO |  | 2 | 0.2
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED PUMP END/NB80 | IS1239 |  | NO |  | 2 | 0.2
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | NB25 SW END WITH 1" NPT (F), CS | SA105 | 4-80-471-84576 | NO |  | 2 | 0.4
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SCREW PLUG M33X2 | SA105 |  | NO |  | 2 | 0.32
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.11 SW RED NB50/25 CL9000 | SA105 |  | NO |  | 2 | 2
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SW END CAP NB 50 CL3000 | SA105 | 4-80-453-58056 | NO |  | 2 | 1.4
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 400 | 5760
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 200
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. LR 45DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 12
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 23.4
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB100 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 21.6
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BW CAP OD114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 5 | 5.9
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 40 | 118.8
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 20 | 8.6
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NIPPLE 1" PLAIN X EXT THRD L=100MM | SA106GRB | 4-80-418-A0468 | NO |  | 70 | 22.68
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NB25 RUBBER HOSE L=15M IS444 TYPE II | IS444 Type II |  | NO |  | 35 | 525
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 425 | 2622.25
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 448 | 1330.56
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 145.125
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. RED NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 24 | 9.6
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 96
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.4
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 224 | 44.8
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | ASME B16.5 BLIND FLANGE NB50 CL150 | SA515GR70 | 4-80-477-A0644 | NO |  | 24 | 76.8
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 96 | 13.44
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NUT -M16 -2H | A194GR2H |  | NO |  | 192 | 5.76
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FLAT FACED FLANGE NB50 CLASS 150 | SA515GR70 | 4-80-468-65420 | NO |  | 24 | 48
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 70 | 1008
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82477 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 30
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD273.1 X 6.4 EP STY 'D' D1=260.3 | IS3589-410MPA |  | M |  | 270 | 10665
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4 X 6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 160 | 9478.4
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 50 | 2755.5
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPENB25X4.0 EP STY D D1-26.9 | IS1239 BLACK |  | M |  | 475 | 1410.75
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB80X4.8 EP STY D D1-80.8 | IS1239 BLACK |  | M |  | 950 | 9595
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB40X4.0 EP STY D D1-41.5 | IS1239 BLACK |  | M |  | 80 | 354.4
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB50X4.5 EP STY D D1-52.7 | IS1239 BLACK |  | M |  | 160 | 987.2
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 28 | 733.6
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 8 | 366.32
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 27
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 180 | 684
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 48
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 58.05
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/273.1X6.35 | SA234WPB |  | NO |  | 2 | 38.42
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 2 | 41.94
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.6
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 4
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 1 | 29.11
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 1 | 60.78
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD406.4X9.53/355.6X9.53 | SA234WPB |  | NO |  | 2 | 177.66
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | WELDED UN EQ TEE NB400/NB80 | As per drawing | 3-80-471-33301 | NO | A | 2
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4X8 L=800 | IS3589-410MPA | 3-80-471-33301 | NO |  | 2 | 125.754
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 88.9X4 | IS1239 BLACK | 3-80-471-33301 | NO |  | 2 | 2.936
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 8
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 52 | 195
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 130 | 208
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 57
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 4
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED NB40/NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 3
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB15 CL3000 SA105 | SA105 |  | NO |  | 15 | 2.7
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB25 CL3000 SA105 | SA105 |  | NO |  | 20 | 8.6
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | TEMP.STUB M33X2(CS) L=45 | SA105 |  | NO |  | 2 | 1
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB |  | NO |  | 2 | 112.3
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PLUG FOR THREMOCOUPLE NIPPLE M33X29CS) | SA105 |  | NO |  | 2 | 1.6
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 RC-1-1/2 INCH(F) | SA105 | 4-80-480-82955 | NO |  | 30 | 30.45
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(F)BSPT | SA105 | 4-80-480-84585 | NO |  | 25 | 16.75
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(M)BSPT | SA105 | 4-80-480-A0580 | NO |  | 25 | 16.75
7 | MEL Mahan 2x800 MW Unit 3 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 R 1-1/2 INCH | SA105 | 4-80-480-A0581 | NO |  | 70 | 98
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 323.9X6.4 EP STY D D1-311.2 | IS3589-410MPA |  | M |  | 20 | 1001
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 273.1 X 6.4 EP STY D-D1 260.3 | IS3589-410MPA |  | M |  | 65 | 2735.85
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE 219.1 X 6.4 EP STY D-D1 206.3 | IS3589-410MPA |  | M |  | 300 | 10071
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB150X5.4 EP STY D-D1-156.8 | IS1239 BLACK |  | M |  | 640 | 13568
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB100X5.4 EP STY D-D1-105.3 | IS1239 BLACK |  | M |  | 140 | 2016
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB80X4.8 EP STY D-D1-80.8 | IS1239 BLACK |  | M |  | 920 | 9292
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB50X4.5 EP STY D-D1-52.7 | IS1239 BLACK |  | M |  | 400 | 2468
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB40X 4.0 EP STY D-D1-41.5 | IS1239 BLACK |  | M |  | 310 | 1373.3
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB25X4.0 EP STY D-D1-26.9 | IS1239 BLACK |  | M |  | 725 | 2153.25
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PIPE NB15X 3.2 EP STY D-D1-15.9 | IS1239 BLACK |  | M |  | 680 | 986
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 12 | 200.4
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 10 | 262
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 208
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 150
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 280.8
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 116.1
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 30
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 24
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 140 | 14
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 BWLR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 6 | 214.2
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 11
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 33
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 18
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 3.6
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 10.5
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD273X6.35/88.9X5.49 | SA234WPB |  | NO |  | 4 | 101.28
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 12 | 180
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB100 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 58
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 65 | 104
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 16.5
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 24
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 24
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 93.75
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 33
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 13.5
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 17.5
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. EQT NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 85 | 25.5
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 1
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 5
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB150 / 80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 4 | 20
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 18
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | UEQT NB 150/100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 31
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/88.9X5.49 | SA234WPB |  | NO |  | 8 | 135.04
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ASMEB16.9 UEQT OD168.3X7.11/60.3X5.54 | SA234WPB |  | NO |  | 10 | 113.9
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 9
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. UEQT NB50 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 5 | 10
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | BL. RED NB40 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 18
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 2.5
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 3 | 0.6
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | RED PUMP END/NB80 | IS1239 |  | NO |  | 5 | 1.5
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/50) | As per drawing | 3-80-999-97670 | NO |  | 15 | 99.375
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/40) | As per drawing | 3-80-999-97669 | NO |  | 18 | 119.25
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/25) | As per drawing | 3-80-999-97668 | NO |  | 30 | 216.75
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ADOPTOR WITH TEMP.STUB M33X2 (NB80/15) | As per drawing | 3-80-999-97667 | NO |  | 5 | 36.125
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB15 CL3000 | SA105 |  | NO |  | 130 | 23.4
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB25 CL3000 | SA105 |  | NO |  | 50 | 21.5
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB40 CL3000 | SA105 |  | NO |  | 25 | 18.75
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | SW PRESSURE STUB NB50 CL3000 | SA105 |  | NO |  | 30 | 39.9
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=45 | SA105 |  | NO |  | 10 | 5
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | TEMP.STUB M33X2 (CS)L=64 | SA105 |  | NO |  | 120 | 84
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB15 | SA106GRB | 3-80-463-27244 | NO |  | 430 | 104.49
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB25 | IS1239 BLACK | 3-80-463-27244 | NO |  | 95 | 42.37
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB40 | IS1239 BLACK | 3-80-463-27244 | NO |  | 18 | 11.952
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | ONE SIDE SCREWED NIPPLE NB50 | IS1239 BLACK | 3-80-463-27244 | NO |  | 64 | 59.2
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PLUG FOR THERMO COUPLE NIPPLE M33X2 (CS) | SA105 |  | NO |  | 130 | 104
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82460 | PACKING RING | IS1972 |  | NO |  | 130 | 1.3
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 310 | 17084.1
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD406.4X6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 105 | 6220.2
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD273.1X6.0 EP STY 'D' D1=261.1 | IS3589-410MPA |  | M |  | 50 | 1975
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB25X4.0 BLACK EP STY 'D' D1=26.9 | IS1239 BLACK |  | M |  | 175 | 519.75
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB50X4.5 EP ST Y D D1=52.7 | IS1239 BLACK |  | M |  | 85 | 524.45
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.0 EP STY 'D' D1=207.1 | IS3589-410MPA |  | M |  | 85 | 2680.05
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD219.1X6.35 EP STY 'D' D1=206.4 | SA106GRB |  | M |  | 35 | 1165.85
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE NB80 X 4.8 EP STY 'D' D1=80.8 SHOP | IS1239 BLACK |  | M |  | 25 | 252.5
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90 X 5.49 STY'D',78 SHOP | SA106GRB |  | M |  | 5 | 56.45
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE OD88.90X11.13 STY'D',69.2 SHOP | SA106GRC |  | M |  | 120 | 2562
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | PIPE DIA 33.4 X 9.09 EP STY 'D' D1=17.2 | SA106GRC |  | M |  | 20 | 109
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 20 | 915.8
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 12 | 314.4
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 35 | 7
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 15 | 250.5
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL 90DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 15.48
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X11.13 | SA234WPC |  | NO |  | 12 | 45.84
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X9.09 | SA234WPC |  | NO |  | 6 | 1.98
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 30.4
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BWLR 90DEG ELBOW OD88.9X5.49 | SA234WPB |  | NO |  | 2 | 4.04
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD355.6X6.35 | SA234WPB |  | NO |  | 4 | 196.56
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD406.4X9.53/219.1X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 161.44
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB | 3-80-477-33125 | NO |  | 2 | 112.3
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD355.6X7.92/219.1X6.35 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 54.83
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/88.9X5.49 | SA234WPB | 3-80-463-36006 | NO |  | 1 | 3.84
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 3
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 32
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 BW EQUAL TEE OD88.9X11.13 | SA234WPC |  | NO |  | 1 | 6.21
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 UEQT OD88.9X11.13/60.3X11.07 | SA234WPC |  | NO |  | 2 | 11.16
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB15 | SA105 | 4-80-329-79004 | NO |  | 10 | 1.8
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASME B16.11 SW STUB NB25 | SA105 | 4-80-329-79005 | NO |  | 30 | 12.9
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | TEMP.STUB M33X2 L=45 | SA105 |  | NO |  | 2 | 1
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 4 | 83.88
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 5 | 39.5
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED NB80/PUMP END | IS1239 |  | NO |  | 2 | 0.2
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | RED PUMP END/NB80 | IS1239 |  | NO |  | 2 | 0.2
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | NB25 SW END WITH 1" NPT (F), CS | SA105 | 4-80-471-84576 | NO |  | 2 | 0.4
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SCREW PLUG M33X2 | SA105 |  | NO |  | 2 | 0.32
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | ASMEB16.11 SW RED NB50/25 CL9000 | SA105 |  | NO |  | 2 | 2
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82471 | SW END CAP NB 50 CL3000 | SA105 | 4-80-453-58056 | NO |  | 2 | 1.4
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 400 | 5760
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 200
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. LR 45DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 12
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 23.4
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB100 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 21.6
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BW CAP OD114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 5 | 5.9
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 40 | 118.8
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | SW STUB NB 25 CL 30000 | SA105 |  | NO |  | 20 | 8.6
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NIPPLE 1" PLAIN X EXT THRD L=100MM | SA106GRB | 4-80-418-A0468 | NO |  | 70 | 22.68
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NB25 RUBBER HOSE L=15M IS444 TYPE II | IS444 Type II |  | NO |  | 10 | 150
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 425 | 2622.25
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 448 | 1330.56
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 75 | 145.125
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. RED NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 24 | 9.6
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. UEQT NB50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 60 | 96
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. EQT NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.4
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 224 | 44.8
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | ASME B16.5 BLIND FLANGE NB50 CL150 | SA515GR70 | 4-80-477-A0644 | NO |  | 24 | 76.8
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FT STUD-M16X100 -B7 | SA193B7 |  | NO |  | 96 | 13.44
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | NUT -M16 -2H | A194GR2H |  | NO |  | 192 | 5.76
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82477 | FLAT FACED FLANGE NB50 CLASS 150 | SA515GR70 | 4-80-468-65420 | NO |  | 24 | 48
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD273.1 X 6.4 EP STY 'D' D1=260.3 | IS3589-410MPA |  | M |  | 270 | 10665
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4 X 6.0 EP STY 'D' D1=394.4 | IS3589-410MPA |  | M |  | 160 | 9478.4
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD355.6X6.4 EP STY 'D' D1=342.8 | IS3589-410MPA |  | M |  | 50 | 2755.5
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPENB25X4.0 EP STY D D1-26.9 | IS1239 BLACK |  | M |  | 475 | 1410.75
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB80X4.8 EP STY D D1-80.8 | IS1239 BLACK |  | M |  | 950 | 9595
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB40X4.0 EP STY D D1-41.5 | IS1239 BLACK |  | M |  | 80 | 354.4
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE NB50X4.5 EP STY D D1-52.7 | IS1239 BLACK |  | M |  | 160 | 987.2
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 28 | 733.6
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD406.4X6.35 | SA234WPB |  | NO |  | 8 | 480.24
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 8 | 366.32
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 135 | 27
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | 90 DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 180 | 684
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 120 | 48
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 58.05
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/273.1X6.35 | SA234WPB |  | NO |  | 2 | 38.42
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD406.4X6.35/355.6X6.35 | SA234WPB |  | NO |  | 2 | 41.94
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 32.3
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.6
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. RED NB25 / 15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 4
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD273X6.35 | SA234WPB |  | NO |  | 1 | 29.11
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 1 | 60.78
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD406.4X9.53/355.6X9.53 | SA234WPB |  | NO |  | 2 | 177.66
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | WELDED UN EQ TEE NB400/NB80 | As per drawing | 3-80-471-33301 | NO | A | 2
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 406.4X8 L=800 | IS3589-410MPA | 3-80-471-33301 | NO |  | 2 | 125.754
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE OD 88.9X4 | IS1239 BLACK | 3-80-471-33301 | NO |  | 2 | 2.936
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. EQT NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 8
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.EQT NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 52 | 195
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 130 | 208
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL. UEQT NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 30 | 57
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED50 / 25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 4
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | BL.RED NB40/NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 3
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB15 CL3000 SA105 | SA105 |  | NO |  | 15 | 2.7
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | SW STUB CS NB25 CL3000 SA105 | SA105 |  | NO |  | 20 | 8.6
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | TEMP.STUB M33X2(CS) L=45 | SA105 |  | NO |  | 2 | 1
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | ASMEB16.9 UEQT OD355.6X7.92/273X6.35 | SA234WPB |  | NO |  | 2 | 112.3
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PLUG FOR THREMOCOUPLE NIPPLE M33X29CS) | SA105 |  | NO |  | 2 | 1.6
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | COPPER PACKING RING M33X2 IS1972 | IS1972 |  | NO |  | 2 | 0.02
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 RC-1-1/2 INCH(F) | SA105 | 4-80-480-82955 | NO |  | 30 | 30.45
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(F)BSPT | SA105 | 4-80-480-84585 | NO |  | 25 | 16.75
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | NB25 SW WITH ½"(M)BSPT | SA105 | 4-80-480-A0580 | NO |  | 25 | 16.75
7 | MEL Mahan 2x800 MW Unit 4 | SG Aux Cooling Water Unit System | Non IBR | 82480 | PIPE WITH THREAD ISO7 R 1-1/2 INCH | SA105 | 4-80-480-A0581 | NO |  | 70 | 98
7 Total | [10 empty] | 271619.014
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 20 | 50
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE DIA 114.30 X 3.05 - SA312TP304H | SA312TP304H |  | M |  | 55 | 460.35
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 98 | 291.06
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB40X 4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 80 | 354.4
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 202 | 1246.34
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE NB 80 HEAVY - IS1239 | IS1239 BLACK |  | M |  | 466 | 4590.1
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 88 | 1267.2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 336 | 7123.2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 219.1 X 6.0 IS3589-410MPA | IS3589-410MPA |  | M |  | 174 | 5486.22
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1 X 6.4 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 144 | 6060.96
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 323.9X 6.35 IS3589FE410 PA | IS3589-410MPA |  | M |  | 140 | 6962.2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 355.6 X 6.4 IS3589-410MPA | IS3589-410MPA |  | M |  | 50 | 2755.5
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 406.4 X 6.0 EFW IS3589 LS/SPIRA | IS3589-410MPA |  | M |  | 7.5 | 444.3
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA457.1X6.0EFW IS3589-410MPA(LS/SPI | IS3589-410MPA |  | M |  | 170 | 11342.4
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 94 | 6982.32
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 102 | 9115.536
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 EFW IS3589-410MPA-LS/SPIR | IS3589-410MPA |  | M |  | 107 | 14840.9
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP304H |  | NO |  | 7 | 14
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 8 | 1.2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 34 | 6.8
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 6.4
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 28 | 54.18
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BL. LR 45DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 16
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 144 | 547.2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 18 | 90
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 94 | 977.6
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 46 | 768.2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.92
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 24 | 399.84
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 33 | 786.06
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 4 | 71.36
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 10 | 457.9
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BL. UEQT NB150 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.752
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BW LR 60DEG ELL 219.1 X 8.18 SA234WPB | SA234WPB |  | NO |  | 4 | 56
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 6 | 1.2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 2 | 1.2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 14.4
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | RED NB 100/80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 19.8
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 17.94
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.68
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 2 | 2.52
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 16.32
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/323.9X6.35 | SA234WPB |  | NO |  | 7 | 120.75
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/323.9X6.35 | SA234WPB |  | NO |  | 2 | 47.18
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 3 | 48.45
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X9.53/355.6X9.53 | SA234WPB |  | NO |  | 4 | 144.52
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/406.4X6.35 | SA234WPB |  | NO |  | 2 | 50.94
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD168.3X7.11/114.3X6.02 | SA234WPB |  | NO |  | 2 | 6.32
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD 114.3X3.05 | SA403WP304H |  | NO |  | 1 | 2.94
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 1 | 0.4
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD219.1X6.35 | SA234WPB |  | NO |  | 6 | 115.62
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD168.3X7.11 | SA234WPB |  | NO |  | 2 | 26.56
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 4 | 13.16
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 4 | 243.12
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD457.2X9.53 | SA234WPB |  | NO |  | 2 | 229.54
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 5.94
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 107.2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD168.3X7.11/88.9X5.49 | SA234WPB |  | NO |  | 8 | 93.04
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD355.6X7.92/168.3X7.11 | SA234WPB |  | NO |  | 4 | 215.84
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/168.3X6.35 | SA234WPB |  | NO |  | 2 | 36.38
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 51.26
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT OD711.2X8 | As per drawing | 3-80-463-31357 | NO | A | 1
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=1200 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 166.44
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=750 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 104.025
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 508 X 6 | As per drawing | 3-80-463-A0817 | NO | A | 5
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 790.975
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA508X10 L=239 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 146.69
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 610 X 8 | As per drawing | 3-80-463-A0818 | NO | A | 6
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 908.496
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA610X10 L=298 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 264.432
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD610X6/323.9X6 | As per drawing | 3-80-463-A0820 | NO | A | 2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD610X10 L=600 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 177.552
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD323.9X8 L=186 00 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 23.174
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/355.6X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 5
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 964.7
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA355.6X8LS/SPIRAL IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 131.865
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/323.9 X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 1
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 166.63
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 323.9 X 8 IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 20.372
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB700/NB450 | As per drawing | 3-80-463-A0821 | NO | A | 5
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD711X10 IS 2062E250B | IS2062E250GRBR | 3-80-468-32127 | NO |  | 5 | 876.06
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 457X8 IS 3589 | IS3589-410MPA | 3-80-463-A0821 | NO |  | 5 | 98.765
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD508X6/OD457X6 | IS2062E250GRBR | 4-80-463-A0473 | NO |  | 4 | 197.192
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCER NB700/NB450 | IS2062E250GRBR | 4-80-463-A0474 | NO |  | 1 | 141.379
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD711.2/OD610 | IS2062E250GRBR | 4-80-463-A0475 | NO |  | 1 | 105.111
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD711.2X8/OD508X6 | IS2062E250GRBR | 4-80-463-A0478 | NO |  | 6 | 614.184
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD508X6/OD323.9X6 | IS2062E250GRBR | 4-80-463-A0479 | NO |  | 4 | 254.216
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ECC RED OD610X6/OD406.4X6 | IS2062E250GRBR | 3-80-463-A0819 | NO |  | 3 | 157.125
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 18 | 1369.44
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD457.2X9.53 | SA234WPB |  | NO |  | 8 | 604.24
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 4 | 152.08
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD508X9.53 | SA234WPB |  | NO |  | 20 | 1869.6
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | 30°MITRE BEND Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0806 | NO |  | 3 | 85.344
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 711X8 (R=700) | IS2062E250GRBR | 3-80-463-A0807 | NO |  | 6 | 974.028
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 45DEG OD711.2X8 (R=700) | IS2062E250GRBR | 3-80-463-A0808 | NO |  | 2 | 162.024
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 60° OD 457 X 8 (R=686) | IS2062E250GRBR | 3-80-463-A0809 | NO |  | 2 | 133.93
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 610.0X8 (R=600) | IS2062E250GRBR | 3-80-463-A0810 | NO |  | 8 | 957.576
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | MITREBEND 45DEG Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0822 | NO |  | 2 | 85.66
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 100 | 18
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 100 | 43
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 50 CLASS 3000 | SA105 |  | NO |  | 100 | 133
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L45 | SA105 | 4-80-463-63321 | NO |  | 70 | 59.08
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L64 | SA105 | 4-80-463-23357 | NO |  | 70 | 176.96
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLUG RC 1" | SA105 | 4-80-463-23358 | NO |  | 140 | 70
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1"(NB80/50) | As per drawing | 3-80-460-28909 | NO | A | 40
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28909 | NO |  | 40 | 60.6
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK | 3-80-460-28909 | NO |  | 80 | 144
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 3-80-460-28909 | NO |  | 40 | 101.12
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 3-80-460-28909 | NO |  | 40 | 44.12
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1" (NB80/25) | As per drawing | 3-80-460-28907 | NO | A | 40
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28907 | NO |  | 40 | 60.6
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 144
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 24
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 4-80-463-23357 | NO |  | 40 | 101.12
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 4-80-463-23358 | NO |  | 40 | 44.12
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 308.5
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 38.7
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 70 | 207.9
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 5
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE NB15 IS1239 | IS1239 BLACK |  | M |  | 50 | 73.4
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 20 | 2.6
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 30 | 636
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1X 6.35 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 150 | 6262.5
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 62 | 5540.816
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 813 X 8 EFW-LS/SPIRAL IS3589-410MPA | IS3589-410MPA |  | M |  | 69 | 10957.2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 15 | 1114.2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 62.4
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | 45DEG BEND NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 24
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 20 | 524
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 8 | 104.8
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=600) | IS3589-410MPA | 3-80-468-32248 | NO |  | 8 | 943.744
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=915) | IS2062E250GRBR | 3-80-463-A0833 | NO |  | 10 | 1780.38
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | 30DEG MITRE BEND OD813X10 (R=800) | IS2062E250GRBR | 3-80-463-A0834 | NO |  | 2 | 174.898
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD813X9.53 | SA234WPB |  | NO |  | 3 | 1084.74
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD813X10 (R=800) | IS3589-410MPA | 3-80-463-27732 | NO |  | 9 | 2322.504
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 9.68
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 13.68
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BW RED 168.3X7.11/114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 8 | 32
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB350 | IS2062E250GRBR | 4-80-463-A0488 | NO |  | 6 | 375.684
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB250 | IS2062E250GRBR | 4-80-463-A0489 | NO |  | 4 | 234.112
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB800/NB600 | IS2062E250GRBR | 4-80-463-A0490 | NO |  | 3 | 275.715
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | RED NB800/NBXXX HOLD | IS1239 |  | NO |  | 4 | 0.02
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB500 | As per drawing | 3-80-463-A0829 | NO | A | 1
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=1000 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 122.696
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=427 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 52.36
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB600 | As per drawing | 3-80-463-A0828 | NO | A | 1
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X12 L=1200 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 212.138
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X10 L=515 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 76.145
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 8 | 214.4
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT NB500/NB350 | As per drawing | 3-80-463-A0830 | NO | A | 3
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD508X8 L=700 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 207.144
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD355.6X8 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 42.744
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/250 | As per drawing | 3-80-463-A0825 | NO | A | 1
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X10;L=900 | IS2062E250GRBR | 3-80-463-A0825 | NO |  | 1 | 133.058
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD273.1X6.0;L=222 | IS3589-410MPA | 3-80-463-A0825 | NO |  | 1 | 8.769
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/500 | As per drawing | 3-80-463-A0836 | NO | A | 1
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø610X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 118.221
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø508X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 50.947
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB800/600 | As per drawing | 3-80-463-A0826 | NO | A | 4
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1000 | IS2062E250GRBR | 3-80-463-A0826 | NO |  | 4 | 947.652
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X6;L=322 | IS3589-410MPA | 3-80-463-A0826 | NO |  | 4 | 115.104
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED EQUAL TEENB800 | As per drawing | 3-80-463-A0827 | NO | A | 1
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1200 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 284.296
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=394 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 93.352
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACED FLANGE NB 500 CLASS 150 | SA515GR70 | 4-80-468-65426 | NO |  | 3 | 162
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB500 | SA515GR70 | 4-80-463-A0484 | NO |  | 3 | 383.4
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | STUD M30 X 3.5 X 230 SA193B7 | SA193B7 |  | NO |  | 60 | 66.24
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M30 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 120 | 27.6
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACE FLANGE NB800 | IS2062E250GRBR | 3-80-468-27258 | NO |  | 2 | 196.2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB-800 | IS2062E250GRBR | 4-80-463-A0486 | NO |  | 2 | 507.46
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | STUD M36X4 - 290 SA193B7 | SA193B7 |  | NO |  | 56 | 112
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | HEX NUT M36 X 4 SA194GR2H | SA194GR2H |  | NO |  | 112 | 48.16
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 300 | 1851
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 77.4
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 150 | 385.8
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 20 | 3.2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000 SA182F316 | SA182F316 |  | NO |  | 1 | 0.25
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 25 | 64.3
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 25 | 4
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000SA182F316 | SA182F316 |  | NO |  | 15 | 3.75
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 15 | 44.55
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | SW STUB NB25 CL3000 SA479TY316L | SA479TY316L |  | NO |  | 25 | 10.75
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB300 (OP -1) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=12 Ø 404 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 21.724
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=12 40X104 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.744
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB300 (OP -2) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8 Ø404 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 13.056
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8, 40X104 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.496
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB150 (OP -3) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8 Ø 217.5 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 4.016
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8, 30X96 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.344
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB250 (OP -4) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8 Ø 334 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 9.372
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=8, 40X99 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.472
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB500 ( OP -5) | As per drawing | 3-80-463-A0944 | NO | A | 2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=10 Ø 600 | IS2062E250GRBR | 3-80-463-A0944 | NO |  | 2 | 37.124
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=10, 40X115 | IS2062E250GRBR | 3-80-463-A0944 | NO |  | 2 | 0.686
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | RESTRICTION ORIFICE NB80 ( OP -6) | As per drawing | 2-80-463-A0447 | NO | A | 2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=6 Ø 133 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 1.2
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | PLATE T=6, 30X93 | IS2062E250GRBR | 2-80-463-A0447 | NO |  | 2 | 0.25
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB80 CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 36.272
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB150 CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 78.776
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB250CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 185.412
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB300CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 8 | 531.8
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | SOW FLANGE NB500CL150 | IS2062E250GRBR | 3-80-999-99059 | NO |  | 4 | 769.3
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | STUD M16 X 2 X 110 SA193B7 | SA193B7 |  | NO |  | 8 | 1.16
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M16 -2H | A194GR2H |  | NO |  | 16 | 0.48
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | FT STUD-M20X140 -B7 | SA193B7 |  | NO |  | 16 | 4.848
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M20 -2H | BPS 41319 |  | NO |  | 32 | 2.08
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | STUD M 24 X 3 X 220 SA193 B16 | SA193B16 |  | NO |  | 72 | 47.52
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M24 -CL6-IS1364P3 BPS 41301 | IS:1364 (P-3) |  | NO |  | 144 | 15.84
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | STUD M30 X 3.5 X 230SA193B7 | SA193B7 |  | NO |  | 40 | 44.16
8 | MEL Mahan 2x800 MW Unit 3 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M30 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 80 | 18.4
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 33.4 X 3.38 SA312TP304H | SA312TP304H |  | M |  | 20 | 50
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE DIA 114.30 X 3.05 - SA312TP304H | SA312TP304H |  | M |  | 55 | 460.35
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 98 | 291.06
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB40X 4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 80 | 354.4
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 202 | 1246.34
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ERW PIPE NB 80 HEAVY - IS1239 | IS1239 BLACK |  | M |  | 466 | 4590.1
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB100X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 88 | 1267.2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 336 | 7123.2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 219.1 X 6.0 IS3589-410MPA | IS3589-410MPA |  | M |  | 174 | 5486.22
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1 X 6.4 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 144 | 6060.96
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 323.9X 6.35 IS3589FE410 PA | IS3589-410MPA |  | M |  | 140 | 6962.2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 355.6 X 6.4 IS3589-410MPA | IS3589-410MPA |  | M |  | 50 | 2755.5
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 406.4 X 6.0 EFW IS3589 LS/SPIRA | IS3589-410MPA |  | M |  | 7.5 | 444.3
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA457.1X6.0EFW IS3589-410MPA(LS/SPI | IS3589-410MPA |  | M |  | 170 | 11342.4
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 94 | 6982.32
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 102 | 9115.536
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 EFW IS3589-410MPA-LS/SPIR | IS3589-410MPA |  | M |  | 107 | 14840.9
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X3.05 | SA403WP304H |  | NO |  | 7 | 14
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 8 | 1.2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 34 | 6.8
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB40 IS1239 BLACK | IS1239 BLACK |  | NO |  | 16 | 6.4
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 28 | 54.18
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BL. LR 45DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 16
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 144 | 547.2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB100 IS1239 BLACK | IS1239 BLACK |  | NO |  | 18 | 90
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 94 | 977.6
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 46 | 768.2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD219.1X6.35 | SA234WPB |  | NO |  | 4 | 31.92
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 24 | 399.84
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 33 | 786.06
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD323.9X6.35 | SA234WPB |  | NO |  | 4 | 71.36
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD355.6X6.35 | SA234WPB |  | NO |  | 10 | 457.9
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BL. UEQT NB150 / 65 IS1239 BLACK | IS1239 BLACK |  | NO |  | 2 | 4.752
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BW LR 60DEG ELL 219.1 X 8.18 SA234WPB | SA234WPB |  | NO |  | 4 | 56
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB25 CL3000 | SA105 |  | NO |  | 6 | 1.2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 45DEG ELBOW NB50 CL3000 | SA105 |  | NO |  | 2 | 1.2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 8 | 14.4
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | RED NB 100/80 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 19.8
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 17.94
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.68
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 2 | 2.52
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/273X6.35 | SA234WPB |  | NO |  | 2 | 18.84
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD323.9X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 16.32
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/323.9X6.35 | SA234WPB |  | NO |  | 7 | 120.75
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/323.9X6.35 | SA234WPB |  | NO |  | 2 | 47.18
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273.1X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 15.8
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD355.6X6.35/273X6.35 | SA234WPB |  | NO |  | 3 | 48.45
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X9.53/355.6X9.53 | SA234WPB |  | NO |  | 4 | 144.52
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD457.2X6.35/406.4X6.35 | SA234WPB |  | NO |  | 2 | 50.94
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 8.28
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 19.36
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD168.3X7.11/114.3X6.02 | SA234WPB |  | NO |  | 2 | 6.32
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD 114.3X3.05 | SA403WP304H |  | NO |  | 1 | 2.94
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 1 | 0.4
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD219.1X6.35 | SA234WPB |  | NO |  | 6 | 115.62
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD168.3X7.11 | SA234WPB |  | NO |  | 2 | 26.56
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD88.9X5.49 | SA234WPB |  | NO |  | 4 | 13.16
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD406.4X6.35 | SA234WPB |  | NO |  | 4 | 243.12
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BW EQUAL TEE OD457.2X9.53 | SA234WPB |  | NO |  | 2 | 229.54
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD48.3X5.08/33.4X4.55 | SA234WPB |  | NO |  | 6 | 5.94
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 4 | 107.2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD168.3X7.11/88.9X5.49 | SA234WPB |  | NO |  | 8 | 93.04
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD355.6X7.92/168.3X7.11 | SA234WPB |  | NO |  | 4 | 215.84
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 34.36
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD219.1X6.35/168.3X6.35 | SA234WPB |  | NO |  | 2 | 36.38
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273X6.35/114.3X6.02 | SA234WPB |  | NO |  | 2 | 51.26
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD323.9X6.35/219.1X6.35 | SA234WPB |  | NO |  | 2 | 74.94
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT OD711.2X8 | As per drawing | 3-80-463-31357 | NO | A | 1
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=1200 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 166.44
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 711.2 X 8 L=750 | IS3589-410MPA | 3-80-463-31357 | NO |  | 1 | 104.025
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 508 X 6 | As per drawing | 3-80-463-A0817 | NO | A | 5
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 790.975
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA508X10 L=239 | IS3589-410MPA | 3-80-463-A0817 | NO |  | 5 | 146.69
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711.2X 8/ 610 X 8 | As per drawing | 3-80-463-A0818 | NO | A | 6
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10 L=1000 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 908.496
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA610X10 L=298 | IS3589-410MPA | 3-80-463-A0818 | NO |  | 6 | 264.432
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD610X6/323.9X6 | As per drawing | 3-80-463-A0820 | NO | A | 2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD610X10 L=600 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 177.552
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD323.9X8 L=186 00 | IS3589-410MPA | 3-80-463-A0820 | NO |  | 2 | 23.174
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/355.6X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 5
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 964.7
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPEDIA355.6X8LS/SPIRAL IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 5 | 131.865
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT OD711X10/323.9 X8 IS3589 | As per drawing | 2-80-463-A0319 | NO | A | 1
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPEOD711.2X10(SPIRAL/LS) IS3589-410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 166.63
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE DIA 323.9 X 8 IS 3589 FE410MPA | IS3589-410MPA | 2-80-463-A0319 | NO |  | 1 | 20.372
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB700/NB450 | As per drawing | 3-80-463-A0821 | NO | A | 5
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD711X10 IS 2062E250B | IS2062E250GRBR | 3-80-468-32127 | NO |  | 5 | 876.06
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD 457X8 IS 3589 | IS3589-410MPA | 3-80-463-A0821 | NO |  | 5 | 98.765
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD508X6/OD457X6 | IS2062E250GRBR | 4-80-463-A0473 | NO |  | 4 | 197.192
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCER NB700/NB450 | IS2062E250GRBR | 4-80-463-A0474 | NO |  | 1 | 141.379
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PLATE FORMED REDUCEROD711.2/OD610 | IS2062E250GRBR | 4-80-463-A0475 | NO |  | 1 | 105.111
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD711.2X8/OD508X6 | IS2062E250GRBR | 4-80-463-A0478 | NO |  | 6 | 614.184
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PF REDUCER OD508X6/OD323.9X6 | IS2062E250GRBR | 4-80-463-A0479 | NO |  | 4 | 254.216
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ECC RED OD610X6/OD406.4X6 | IS2062E250GRBR | 3-80-463-A0819 | NO |  | 3 | 157.125
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 18 | 1369.44
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD457.2X9.53 | SA234WPB |  | NO |  | 8 | 604.24
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD457.2X6.35 | SA234WPB |  | NO |  | 4 | 152.08
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWSR 90DEG ELBOW OD508X9.53 | SA234WPB |  | NO |  | 20 | 1869.6
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | 30°MITRE BEND Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0806 | NO |  | 3 | 85.344
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 711X8 (R=700) | IS2062E250GRBR | 3-80-463-A0807 | NO |  | 6 | 974.028
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 45DEG OD711.2X8 (R=700) | IS2062E250GRBR | 3-80-463-A0808 | NO |  | 2 | 162.024
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 60° OD 457 X 8 (R=686) | IS2062E250GRBR | 3-80-463-A0809 | NO |  | 2 | 133.93
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | MITRE BEND 90° OD 610.0X8 (R=600) | IS2062E250GRBR | 3-80-463-A0810 | NO |  | 8 | 957.576
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | MITREBEND 45DEG Ø508X8(R=500) | IS2062E250GRBR | 3-80-463-A0822 | NO |  | 2 | 85.66
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 15 CL 3000(CS) | SA105 |  | NO |  | 100 | 18
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 25 CLASS 3000 | SA105 |  | NO |  | 100 | 43
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | SW PRESSURE STUB NB 50 CLASS 3000 | SA105 |  | NO |  | 100 | 133
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L45 | SA105 | 4-80-463-63321 | NO |  | 70 | 59.08
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | TEMP STUB RC 1" L64 | SA105 | 4-80-463-23357 | NO |  | 70 | 176.96
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PLUG RC 1" | SA105 | 4-80-463-23358 | NO |  | 140 | 70
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1"(NB80/50) | As per drawing | 3-80-460-28909 | NO | A | 40
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28909 | NO |  | 40 | 60.6
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 50 IS1239 BLACK | IS1239 BLACK | 3-80-460-28909 | NO |  | 80 | 144
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 3-80-460-28909 | NO |  | 40 | 101.12
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 3-80-460-28909 | NO |  | 40 | 44.12
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ADAPTER WITH TEMP. STUB RC-1" (NB80/25) | As per drawing | 3-80-460-28907 | NO | A | 40
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB80X 4.8 , L=150 | IS1239 BLACK | 3-80-460-28907 | NO |  | 40 | 60.6
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB80 / 40 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 144
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BL. RED NB40 / 25 IS1239 BLACK | IS1239 BLACK | 3-80-460-28907 | NO |  | 80 | 24
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | TEMP.STUB RC-1" L=64 | SA105 | 4-80-463-23357 | NO |  | 40 | 101.12
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PLUG R-1" | SA105 | 4-80-463-23358 | NO |  | 40 | 44.12
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 308.5
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 20 | 38.7
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 70 | 207.9
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 25 | 5
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE NB15 IS1239 | IS1239 BLACK |  | M |  | 50 | 73.4
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 20 | 2.6
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB150X5.4BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 30 | 636
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 273.1X 6.35 IS3589-410MPA-LS/SPIRAL | IS3589-410MPA |  | M |  | 150 | 6262.5
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD-610X6 IS3589-410MPA | IS3589-410MPA |  | M |  | 62 | 5540.816
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 813 X 8 EFW-LS/SPIRAL IS3589-410MPA | IS3589-410MPA |  | M |  | 69 | 10957.2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE 508.0X6.0EFW IS3589-410MPA(LS/SPIRA | IS3589-410MPA |  | M |  | 15 | 1114.2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG ELL NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 62.4
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | 45DEG BEND NB150 IS1239 BLACK | IS1239 BLACK |  | NO |  | 6 | 24
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 20 | 524
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 45DEG ELBOW OD273X6.35 | SA234WPB |  | NO |  | 8 | 104.8
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=600) | IS3589-410MPA | 3-80-468-32248 | NO |  | 8 | 943.744
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD610X8 (R=915) | IS2062E250GRBR | 3-80-463-A0833 | NO |  | 10 | 1780.38
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | 30DEG MITRE BEND OD813X10 (R=800) | IS2062E250GRBR | 3-80-463-A0834 | NO |  | 2 | 174.898
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD813X9.53 | SA234WPB |  | NO |  | 3 | 1084.74
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | 90DEG MITRE BEND OD813X10 (R=800) | IS3589-410MPA | 3-80-463-27732 | NO |  | 9 | 2322.504
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD219.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 9.68
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 RED OD273X6.35/168.3X7.11 | SA234WPB |  | NO |  | 2 | 13.68
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BW RED 168.3X7.11/114.3X6.02 SA234WPB | SA234WPB |  | NO |  | 8 | 32
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB350 | IS2062E250GRBR | 4-80-463-A0488 | NO |  | 6 | 375.684
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB600/NB250 | IS2062E250GRBR | 4-80-463-A0489 | NO |  | 4 | 234.112
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PF RED NB800/NB600 | IS2062E250GRBR | 4-80-463-A0490 | NO |  | 3 | 275.715
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | RED NB800/NBXXX HOLD | IS1239 |  | NO |  | 4 | 0.02
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB500 | As per drawing | 3-80-463-A0829 | NO | A | 1
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=1000 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 122.696
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD508X10 L=427 | IS2062E250GRBR | 3-80-463-A0829 | NO |  | 1 | 52.36
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FAB EQT NB600 | As per drawing | 3-80-463-A0828 | NO | A | 1
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X12 L=1200 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 212.138
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PF PIPE OD610X10 L=515 | IS2062E250GRBR | 3-80-463-A0828 | NO |  | 1 | 76.145
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 UEQT OD273.1X6.35/168.3X7.11 | SA234WPB |  | NO |  | 8 | 214.4
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FAB UNEQT NB500/NB350 | As per drawing | 3-80-463-A0830 | NO | A | 3
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD508X8 L=700 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 207.144
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD355.6X8 | IS3589-410MPA | 3-80-463-A0830 | NO |  | 3 | 42.744
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/250 | As per drawing | 3-80-463-A0825 | NO | A | 1
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X10;L=900 | IS2062E250GRBR | 3-80-463-A0825 | NO |  | 1 | 133.058
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD273.1X6.0;L=222 | IS3589-410MPA | 3-80-463-A0825 | NO |  | 1 | 8.769
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB600/500 | As per drawing | 3-80-463-A0836 | NO | A | 1
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø610X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 118.221
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | P.F. PIPE Ø508X10 | IS2062E250GRBR | 3-80-463-A0836 | NO |  | 1 | 50.947
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED UNEQUAL TEE NB800/600 | As per drawing | 3-80-463-A0826 | NO | A | 4
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1000 | IS2062E250GRBR | 3-80-463-A0826 | NO |  | 4 | 947.652
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD610X6;L=322 | IS3589-410MPA | 3-80-463-A0826 | NO |  | 4 | 115.104
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FABRICATED EQUAL TEENB800 | As per drawing | 3-80-463-A0827 | NO | A | 1
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=1200 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 284.296
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE OD813X12;L=394 | IS2062E250GRBR | 3-80-463-A0827 | NO |  | 1 | 93.352
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACED FLANGE NB 500 CLASS 150 | SA515GR70 | 4-80-468-65426 | NO |  | 3 | 162
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB500 | SA515GR70 | 4-80-463-A0484 | NO |  | 3 | 383.4
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | NON-ASBESTOS JOINTING SHEET 3.0MM | NON-ASBESTOS |  | M2 |  | 5 | 28.45
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | STUD M30 X 3.5 X 230 SA193B7 | SA193B7 |  | NO |  | 60 | 66.24
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | NUT -M30 -CL4-IS1363 | IS:1363 (P-3) |  | NO |  | 120 | 27.6
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | FLAT FACE FLANGE NB800 | IS2062E250GRBR | 3-80-468-27258 | NO |  | 2 | 196.2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BLIND FLANGE NB-800 | IS2062E250GRBR | 4-80-463-A0486 | NO |  | 2 | 507.46
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | STUD M36X4 - 290 SA193B7 | SA193B7 |  | NO |  | 56 | 112
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | HEX NUT M36 X 4 SA194GR2H | SA194GR2H |  | NO |  | 112 | 48.16
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 50 | 148.5
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB50X4.50BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 300 | 1851
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 10 | 2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB50 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 77.4
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 150 | 385.8
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 20 | 3.2
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000 SA182F316 | SA182F316 |  | NO |  | 1 | 0.25
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-60.3X3.91X6000-SA312TP316L | SA312TP316L |  | M |  | 100 | 558.9
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X3.91 | SA403WP316L |  | NO |  | 30 | 19.5
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPE-33.4X3.38X6000-SA312TP316L | SA312TP316L |  | M |  | 25 | 64.3
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 25 | 4
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | SW EQT NB 25 CL 3000SA182F316 | SA182F316 |  | NO |  | 15 | 3.75
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | PIPENB25X4.0 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 15 | 44.55
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | BL. 90 DEG ELL NB25 IS1239 BLACK | IS1239 BLACK |  | NO |  | 15 | 3
8 | MEL Mahan 2x800 MW Unit 4 | TG Aux Cooling Water | Non IBR | 82463 | SW STUB NB25 CL3000 SA479TY316L | SA479TY316L |  | NO |  | 25 | 10.75
8 Total | [10 empty] | 281931.116
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | PIPE OD33.4X4.55 EP STY D D1-25.2 ATSITE | SA106GRB |  | M |  | 105 | 340.2
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 24 | 4.56
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 465 | 3478.2
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 74 | 66.6
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 209 | 677.16
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 88 | 16.72
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 4 | 5.6
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 3 | 14.79
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 7 | 2.87
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 75 | 561
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 17 | 15.3
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6AT SITE | SA106GRB |  | M |  | 145 | 833.17
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD48.3X5.08 | SA234WPB |  | NO |  | 30 | 14.4
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 180 | 450
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 25 | 3.75
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 30 | 97.2
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 5 | 0.95
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/48.3X5.54 | SA234WPB |  | NO |  | 1 | 0.51
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB50/40 CL3000 | SA105 |  | NO |  | 2 | 2
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 45 | 40.5
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6 ATSITE | SA106GRB |  | M |  | 40 | 229.84
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 1050 | 3402
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 162 | 30.78
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 3 | 2.58
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 2 | 0.74
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 2 | 2.8
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 16 | 6.88
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 3 | 0.36
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB25/10 | SA105 | 3-80-449-A0883 | NO |  | 10 | 0.4
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD60.3X5.54 SA234WPB | SA234WPB |  | NO |  | 1 | 0.33
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD48.3X3.68 SA234WPB | SA234WPB |  | NO |  | 1 | 0.17
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | SW B16.11 CAP OD33.4X4.55 SA105 | SA105 |  | NO |  | 1 | 0.005
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 10 | 3
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 10 | 32.4
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY DD1-49.5 AT SITE | SA106GRB |  | M |  | 70 | 523.6
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 14 | 12.6
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 10 | 14
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 45 | 145.8
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 60 | 150
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 12 | 1.8
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 4
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 5 | 1
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB15/10 | SA479TY304 | 3-80-449-A0883 | NO |  | 5 | 0.2
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 1000 | 3240
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 156 | 29.64
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 80 | 34.4
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 26 | 23.4
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 10 | 3.7
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 40 | 56
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 49.5
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 50 | 125
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 4 | 2
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 60.3X5.54 EPSTY D D1-49.5 ATSITE | SA106GRC |  | M |  | 50 | 374
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 8.9
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | EQT OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 0.05
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA21.3X2.77 EPATSITE STY-DD1=16.16 | SA312TP304H |  | M |  | 50 | 65
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 15 | 1.2
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD21.3X3.73EP ATSITE STY-D,D1=14.24 | SA106GRB |  | M |  | 300 | 486
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA 21.3X3.73EPATSITE STY-DD1=14.24 | SA312TP304H |  | M |  | 50 | 80.5
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 15 | 0.87
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB15X 3.2 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 100 | 145
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 4
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 25 | 36.5
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 10 | 1
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRB |  | M |  | 150 | 486
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 50 | 9.5
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 45 | 5.4
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRC |  | M |  | 110 | 356.4
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW LR 90DEG ELL 33.4X 4.55 SA234WPC | SA234WPC |  | NO |  | 40 | 0.2
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X6.35/21.3X4.55 | SA234WPC |  | NO |  | 40 | 6
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA33.4X3.38 EPATSITE STY-D,D1=27 | SA312TP304H |  | M |  | 50 | 125
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 20 | 3
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 20 | 4
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSY NB50(OP-40)&(OP-45) | As per drawing | 3-80-449-A0984 | NO | A | 4
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 L=210MM | SA106GRB | 3-80-449-A0984 | NO |  | 4 | 5.12
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø52.22 | SA240TP304 | 3-80-449-A0984 | NO |  | 4 | 0.64
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEMBLY NB25 (OP-46) | As per drawing | 3-80-449-A0985 | NO | A | 2
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 L=210MM | SA312TP316L | 3-80-449-A0985 | NO |  | 2 | 1.36
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø28.50 | SA240TP304 | 3-80-449-A0985 | NO |  | 2 | 0.086
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSY NB80(OP-51)&(OP-52) | As per drawing | 3-80-449-A0977 | NO | A | 4
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD88.9X7.42 L=210MM | SA106GRB | 3-80-449-A0977 | NO |  | 4 | 12.8
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø77.92 | SA240TP304 | 3-80-449-A0977 | NO |  | 4 | 1.408
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEY NB25(OP-47) | As per drawing | 3-80-449-A0981 | NO | A | 2
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X6.35 L=210MM | SA106GRC | 3-80-449-A0981 | NO |  | 2 | 1.78
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATET=10THK,Ø22.70 ORIFICEHOLE DIA10MM | SA240TP304 | 3-80-449-A0981 | NO |  | 2 | 0.05
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEY NB25(OP-38) | As per drawing | 3-80-452-A0965 | NO | A | 2
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X6.35 L=210MM | SA106GRB | 3-80-452-A0965 | NO |  | 2 | 1.592
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK,Ø23.80ORIFICE HOLE DIA10MM | SA240TP304 | 3-80-452-A0965 | NO |  | 2 | 0.056
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ORIFICE PLATE ASSEMBLY NB25 (OP-53) | As per drawing | 3-80-449-A0981 | NO | A | 2
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X6.35 L=210MM | SA106GRB | 3-80-449-A0981 | NO |  | 2 | 1.78
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PLATE T=10THK, Ø2 2.70 ORIF HOL DIA10 | SA240TP304 | 3-80-449-A0981 | NO |  | 2 | 0.054
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 160 | 400
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 18 | 2.7
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X2.77 EP STY D D1-16.2 ATSITE | SA312TP304H |  | M |  | 160 | 208
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 20 | 1.6
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 2 | 0.8
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD21.3X2.77 | SA403WP304H |  | NO |  | 2 | 0.36
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE DIA 33.4X3.38EPSTYD D1=27.2(SITE) | SA106GRB |  | M |  | 110 | 275
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.14
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 300 | 750
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 26 | 3.9
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X3.73 EP D1-15.2 AT SITE | SA312TP304H |  | M |  | 10 | 16.1
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 5 | 0.29
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 60 | 154.32
9 | MEL Mahan 2x800 MW Unit 3 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 6 | 0.96
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | PIPE OD33.4X4.55 EP STY D D1-25.2 ATSITE | SA106GRB |  | M |  | 105 | 340.2
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82381 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 24 | 4.56
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 465 | 3478.2
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 74 | 66.6
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 209 | 677.16
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 88 | 16.72
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 4 | 5.6
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/60.3X5.54 | SA234WPB |  | NO |  | 3 | 14.79
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD114.3X6.02/88.9X5.49 | SA234WPB |  | NO |  | 2 | 10.46
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/33.4X4.55 | SA234WPB |  | NO |  | 2 | 1.36
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 7 | 2.87
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5 ATSITE | SA106GRB |  | M |  | 75 | 561
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 17 | 15.3
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6AT SITE | SA106GRB |  | M |  | 145 | 833.17
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD48.3X5.08 | SA234WPB |  | NO |  | 30 | 14.4
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 180 | 450
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 25 | 3.75
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 30 | 97.2
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 5 | 0.95
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X5.54/48.3X5.54 | SA234WPB |  | NO |  | 1 | 0.51
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB50/40 CL3000 | SA105 |  | NO |  | 2 | 2
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 45 | 40.5
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD48.3X5.08 EP STY D D1-38.6 ATSITE | SA106GRB |  | M |  | 40 | 229.84
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7 ATSITE | SA106GRB |  | M |  | 1050 | 3402
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 162 | 30.78
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD88.9X5.49/60.3X5.54 | SA234WPB |  | NO |  | 3 | 2.58
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 2 | 0.74
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 2 | 2.8
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 16 | 6.88
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 3 | 0.36
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB25/10 | SA105 | 3-80-449-A0883 | NO |  | 10 | 0.4
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD60.3X5.54 SA234WPB | SA234WPB |  | NO |  | 1 | 0.33
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW CAP OD48.3X3.68 SA234WPB | SA234WPB |  | NO |  | 1 | 0.17
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | SW B16.11 CAP OD33.4X4.55 SA105 | SA105 |  | NO |  | 1 | 0.005
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW UEQT NB25/15 CL3000 | SA105 |  | NO |  | 10 | 3
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 10 | 32.4
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY DD1-49.5 AT SITE | SA106GRB |  | M |  | 10 | 74.8
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 4 | 3.6
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 1 | 1.4
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 45 | 145.8
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 20 | 3.8
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 60 | 150
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 12 | 1.8
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 4
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 5 | 1
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | MACHINED REDUCER NB15/10 | SA479TY304 | 3-80-449-A0883 | NO |  | 5 | 0.2
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X4.55 EP STY D D1-24.7AT SITE | SA106GRB |  | M |  | 1000 | 3240
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 156 | 29.64
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD33.4X4.55 | SA234WPB |  | NO |  | 80 | 34.4
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD60.3X5.54 EP STY D D1-49.5AT SITE | SA106GRB |  | M |  | 150 | 1122
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPB |  | NO |  | 26 | 23.4
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD60.3X4.55/33.4X4.55 | SA234WPB |  | NO |  | 10 | 3.7
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 UEQT OD60.3X5.54/33.4X4.55 | SA234WPB |  | NO |  | 40 | 56
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BW EQUAL TEE OD60.3X5.54 | SA234WPB |  | NO |  | 30 | 49.5
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD33.4X3.38 EP STY D D1-27 AT SITE | SA312TP304H |  | M |  | 50 | 125
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 10 | 1.5
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW EQUAL TEE NB25 CL3000 | SA182F304H |  | NO |  | 4 | 2
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 60.3X5.54 EPSTY D D1-49.5 ATSITE | SA106GRC |  | M |  | 50 | 374
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 8.9
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | EQT OD60.3X5.54 | SA234WPC |  | NO |  | 10 | 0.05
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA21.3X2.77 EPATSITE STY-DD1=16.16 | SA312TP304H |  | M |  | 50 | 65
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 15 | 1.2
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD21.3X3.73EP ATSITE STY-D,D1=14.24 | SA106GRB |  | M |  | 300 | 486
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SWLR 90DEG ELBOW NB15 CL3000 | SA105 |  | NO |  | 100 | 13
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA 21.3X3.73EPATSITE STY-DD1=14.24 | SA312TP304H |  | M |  | 50 | 80.5
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 15 | 0.87
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB15X 3.2 BLHEAVYPLAINEND IS1239 BL | IS1239 BLACK |  | M |  | 100 | 145
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BL. 90 DEG ELL NB15 IS1239 BLACK | IS1239 BLACK |  | NO |  | 40 | 4
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPENB 15X 3.2 SCREW&SOCKETED IS1239 GAL | IS1239 G&T |  | M |  | 25 | 36.5
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | G&T 90DEG ELL NB15 IS1239 | IS1239 G&T |  | NO |  | 10 | 1
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRB |  | M |  | 150 | 486
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 50 | 9.5
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X4.55/21.3X3.73 | SA234WPB |  | NO |  | 45 | 5.4
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE OD 33.4X4.55 EPATSITE STY-D,D1=24.7 | SA106GRC |  | M |  | 110 | 356.4
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | BW LR 90DEG ELL 33.4X 4.55 SA234WPC | SA234WPC |  | NO |  | 40 | 0.2
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 RED OD33.4X6.35/21.3X4.55 | SA234WPC |  | NO |  | 40 | 6
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | PIPE DIA33.4X3.38 EPATSITE STY-D,D1=27 | SA312TP304H |  | M |  | 50 | 125
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 20 | 3
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82449 | ASMEB16.11 SW RED NB25/15 CL3000 | SA182F304H |  | NO |  | 20 | 4
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 160 | 400
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 18 | 2.7
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X2.77 EP STY D D1-16.2 ATSITE | SA312TP304H |  | M |  | 160 | 208
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X2.77 | SA403WP304H |  | NO |  | 20 | 1.6
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD33.4X3.38 | SA403WP304H |  | NO |  | 2 | 0.8
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BW EQUAL TEE OD21.3X2.77 | SA403WP304H |  | NO |  | 2 | 0.36
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE DIA 33.4X3.38EPSTYD D1=27.2(SITE) | SA106GRB |  | M |  | 110 | 275
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X4.55 | SA234WPB |  | NO |  | 6 | 1.14
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP304H |  | M |  | 300 | 750
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP304H |  | NO |  | 26 | 3.9
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE OD21.3X3.73 EP D1-15.2 AT SITE | SA312TP304H |  | M |  | 10 | 16.1
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD21.3X3.73 | SA403WP304H |  | NO |  | 5 | 0.29
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | PIPE-33.4X3.38 EP STY D D1-27.2AT SITE | SA312TP316L |  | M |  | 60 | 154.32
9 | MEL Mahan 2x800 MW Unit 4 | TG Cycle Piping Drains & Vents | Non IBR | 82601 | ASMEB16.9 BWLR 90DEG ELBOW OD33.4X3.38 | SA403WP316L |  | NO |  | 6 | 0.96
9 Total | [10 empty] | 41640.756
Grand Total | [10 empty] | 926422.529
Note-
1. In case of Assembly items (indicated as 'A' under Assembly Indicator), exploded BOM will be indicated below the Assembly item. Weight of individual items of the Assembly shall be considered for arriving the final weight of the assembly. Individual drawings shall also be referred.
2. Bidders are required to thoroughly review the drawings before quoting.
3. in case of any mismatch between the Specification indicated against each item and corresponding Specification indicated in the drawing, Specification indicated in the drawing shall prevail.