## Annexure I
BOQ for Erection Testing & Commissioning (ETC) Works for 400kV Switchyard at Banaskantha Rev 01
Customer : POWERGRID CORPORATION OF INDIA LTD.
Project : 400kV S/S Banaskantha
Note: | This BOQ covers only ETC work for 400kV Banaskantha Switchyard excluding unloading and storage .Unloading and storage of all the material required for 765kV & 400kV Switchyard at Banaskantha shall be covered in a separate BOQ (Annexure III). Bidder shall quote only for ETC work in this BOQ, prices for unloading, storage and shifting of material should be filled seperately in Annexure III.
S.No. | Voltage Class (kV) | Type | Description | Unit | Total Qty | Unit Price | Total Price
MAIN EQUIPMENTS
400kV REACTOR
1.1 | 400 kV | 125MVAR | 125 MVAr, 3-Ph, Reactor alongwith Marshalling Kiosk, terminal connectors, accessories, with oil. Work includes erection of all auxiliaries, viz turrets, bushings, terminal connectors, nitrogen purging, dry air circulation, filling of oil, oil filteration, Oil testing, laying of cable from Reactor auxiliaries to MK etc as required to complete the installation of reactor. | Nos. | 1 |  | 0
1.2 |  |  | Dragging charges of above mentioned Reactor (1 No.) upto plinth | m | 50 |  | 0
| 400kV EQUIPMENT | [5 empty] | 0
2 | 400 kV |  | 400KV SF6, 3 Phase Circuit Breaker alongwith lattice type GI supporting structure, terminal connectors, Breaker Control Cabinets, ladder and interpole cabling , SF6 cylinders complete in all respect (Supervision of Erection, Testing and commissioning will be done by supplier. Supplier will bring Timing kit and Gas leak detector only. Necessary manpower support, tools, tackles and testing kit to be in scope of ETC contractor). |  |  |  | 0
2.1 |  | CB | with PIR & with CSD | Nos. | 1 |  | 0
2.2 |  | CB | without PIR & with CSD | Nos. | 5 |  | 0
2.3 |  | CB | without PIR & without CSD | Nos. | 2 |  | 0
2.4 |  | Cable | Special cabling between CB and Relay Panel in SPR for CSD | m | 600 |  | 0
0
3 | 400 kV | HDB (Electrically ganged) | 3 Ph, Isolator,3150/2000A, motor operated complete with 9 nos. of400kV support insulators & terminal connectors without support structure |  |  |  | 0
3.1 |  |  | - with one earth switch (motor/ manual operated) | Nos. | 18 |  | 0
3.2 |  |  | - with two earth switch (motor/ manual operated) | Nos. | 2 |  | 0
0
0
4 | 400 kV | HDB (Electrically ganged) | 1 Ph, Isolator, 3150A, motor operated complete with 3 nos. of 400kV support insulators & terminal connectors without support structure |  |  |  | 0
4.1 |  |  | - without earth switch | Nos. | 5 |  | 0
4.2 |  |  | - with one earth switch (motor operated) | Nos. | 7 |  | 0
0
5 | 400 kV |  | 1 Ph, Current Transformer complete with terminal connectors without support structure. | Nos. | 24 |  | 0
0
6 | 400kV | 0.5mH | Wave Trap pedestal mounted including 3 Nos. 400kV Post Insulators and Terminal connectors without structure | Nos. | 2 |  | 0
0
7 | 400 kV | Solidcore with corona ring | Post Insulators complete with corona ring & terminal connectors without support structure | Nos. | 67 |  | 0
0
8 | 336 kV |  | 1 Phase, Gapless type Metal Oxide Surge Arrester complete with surge counter, leakage current meter, insulating base, connecting cable and terminal connectors without support structure | Nos. | 16 |  | 0
0
9 | 400 kV |  | 1 Ph, CVT complete with terminal connector without support structure. | Nos. | 12 |  | 0
0
| 145 kV Equipments | [5 empty] | 0
10 | 145 kV | Single phase | SF6, 1 Phase Circuit Breaker alongwith lattice type GI supporting structure, terminal connectors, Breaker Control Cabinets, ladder and interpole cabling. (Supervision of Erection, Testing and commissioning will be done by supplier. Supplier will bring Timing kit and Gas leak detector only. Necessary manpower support, tools, tackles and testing kit to be in scope of ETC contractor). | Nos. | 2 |  | 0
11 | 145 kV | Solidcore | Post Insulators complete with terminal connectors without support structure | Nos. | 4 |  | 0
0
| 11kV Equipments | [5 empty] | 0
12 | 11 kV | HDB (Pedestal mounted or double pole structure) | 3 Ph, Isolator, manual operated complete with 9 nos. of support insulators & terminal connectors without support structure |  |  |  | 0
|  |  | - without earth switch | Nos. | 1 |  | 0
13 | 11kv | Surge Arrestor | 1 Phase, Gapless type Metal Oxide Surge Arrester complete with surge counter, leakage current meter, insulating base, connecting cable and terminal connectors but without suppot structure | Nos. | 3 |  | 0
14 | 11 kV | HGF | 1 Phase Horn Gap Fuse along with post insulators without support structure | Nos. | 3 |  | 0
15 | 11 kV | Solidcore | Post Insulators complete with terminal connectors without support structure | Nos. | 3 |  | 0
0
0
16 | CONTROL AND RELAY PANEL | [5 empty] | 0
|  |  | 400 kV Control & Relay Panels |  |  |  | 0
|  |  | Supervision of testing and commissioning of relays in scope of panel supplier. Necessary manpower support, tools, tackles and testing equipment to be in scope of ETC contractor |  |  |  | 0
16.01 |  |  | 400kV Circuit Breaker Relay Panel with Auto reclose | Set | 5 |  | 0
16.02 |  |  | 400kV Circuit Breaker Relay Panel without Auto reclose | Set | 3 |  | 0
16.03 |  |  | 400kV Line Protection Panel | Set | 2 |  | 0
16.04 |  |  | 400kV Reactor Protection Panel | Set | 1 |  | 0
16.05 |  |  | 400kV Bus Bar Protection Panel(Duplicate Bus bar protection) | Set | 1 |  | 0
16.06 |  |  | Common Equipment's : Time synchronization Equipment - GPS Clock, Display, Antenna with wiring. | Nos. | 1 |  | 0
16.07 |  |  | Panel mounted BCU for controlling & monitoring of Auxiliary System | Set | 1 |  | 0
16.08 |  |  | Station HMI (including necessary softwares ) | Set | 2 |  | 0
16.09 |  |  | Industrial Grade Station Server(Main / Standby with necessary softwares) | Set | 4 |  | 0
16.1 |  |  | Disturbance Recorder Work Station ( including necessary softwares) | Set | 1 |  | 0
16.11 |  |  | A4/A3 type colour Laser printer | No. | 3 |  | 0
16.12 |  |  | Dot matrix printer | No. | 2 |  | 0
16.13 |  |  | Inverter -working on station battery back-up. | No. | 1 |  | 0
| FO CABLE LAYING - Contractor's supplied GI Pipe | [5 empty] | 0
16.14 |  |  | SAS : Armoured Fibre Optic system Cable for SAS and Busbar protection ( to be laid in GI Pipe) ( Scope - Laying of the cables in the 25NB GI PIPE), SUPPLY OF GI PIPE (Powergrid accepted) shall also be in contractor's scope
16.14.1 |  | Supply included in bidders scope | Supply and Laying of 25 mm GI pipes( light grade) conduits alongwith socket, bend and joint on trench rack support . Cutting, threading, fixing of clamps sockets/ bends/joints where required etc. complete. Supply of required clamp for fixing GI conduits on Cable rack shall be in ETC contractor scope. (Payment will be made for the as erected pipe length). GI conduits shall be used for laying of fiber optic cables /sensor cables. | M | 1500 |  | 0
16.14.2 |  |  | Armoured FO cable along with connectors for SAS & Busbar Protection. The laying of network/optical cables cables shall be in the contractor scope. However, Optical cable will be laid under SAS supplier's supervision. Splicing and Termination shall be in SAS supplier's scope.). FO cable shall be laid in 25mm dia. GI pipes . | M | 2000 |  | 0
0
| PLCC SYSTEM | [5 empty] | 0
17 |  |  | PLCC for 765/400KV BANASKATA STATION |  |  |  | 0
17.1 |  |  | Coupling device(Phase to Phase) | Nos. | 6 |  | 0
17.2 |  |  | PLCC Panel-Carrier equipment (for speech + protection and speech +data) (Analogue type ) | Nos. | 10 |  | 0
17.3 |  |  | PLCC Panel-Digital Protection coupler | Nos. | 8 |  | 0
17.4 |  |  | 4 wire telephone instrument( Along with telephone wiring ) | Nos. | 4 |  | 0
17.5 |  |  | 5 Pair Telephone Cables, armoured ,0.5 sq. mm annealed copper conductor and petroleum jelly filled with polyethene outer jackets | m | 2000 |  | 0
17.6 |  |  | HF Cable | m | 1400 |  | 0
0
18 |  |  | PLCC for 765KV CHITTORGARH SUBSTATION END |  |  |  | 0
18.1 |  |  | Coupling device(Phase to Phase) | Nos. | 2 |  | 0
18.2 |  |  | PLCC Panel-Carrier equipment (for speech + protection and speech +data) (Analogue type ) | Nos. | 3 |  | 0
18.3 |  |  | PLCC Panel-Digital Protection coupler | Nos. | 2 |  | 0
18.4 |  |  | 4 wire telephone instrument( Along with telephone wiring ) | Nos. | 1 |  | 0
18.5 |  |  | 5 Pair Telephone Cables, armoured ,0.5 sq. mm annealed copper conductor and petroleum jelly filled with polyethene outer jackets | m | 300 |  | 0
18.6 |  |  | HF Cable | m | 300 |  | 0
0
0
0
19 | Tele communication Equipment | [5 empty] | 0
19.1 |  |  | Equipment Cabinets for SDH & PDH equipments | Nos | 4 |  | 0
19.2 |  |  | NMS ( For SDH Equipment & Multiplexer) ( Handling & Storage only) | Set | 2 |  | 0
0
20 | LT AC & DC SWITCHBOARDS | [5 empty] | 0
20.1 |  |  | 415V Main switchboard | Set | 1 |  | 0
20.2 |  |  | 415V ACDB | Set | 1 |  | 0
20.3 |  |  | 415V MLDB (alongwith 2 nos. 300 kVA lighting transformer) | Set | 1 |  | 0
20.4 |  |  | 415V Emergency Lighting Board (alongwith 1 no. 100 kVA, lighting transformer) | Set | 1 |  | 0
20.5 |  |  | 220V DCDB | Sets | 2 |  | 0
20.6 |  |  | 48V DCDB | Sets | 2 |  | 0
0
21 | BATTERY AND BATTERY CHARGER | Battery Bank and Battery charger |  |  |  |  | 0
21.1 | 220 V | VRLA Battery Bank | Battery Bank including all accessories such as racks, interconnecting cables, connectors etc. | Sets | 2 |  | 0
21.2 | 48 V | VRLA Battery Bank | Battery Bank including all accessories such as racks, interconnecting cables, connectors etc. | Sets | 2 |  | 0
21.3 | 220 V | Battery charger | Battery Charger (Float cum Boost ) | Sets | 2 |  | 0
21.4 | 48 V | Battery charger | Battery Charger (Float cum Boost ) | Sets | 2 |  | 0
0
0
| LT TRANSFORMER | LT Transformer |  |  |  |  | 0
22 | 11kV/ 415V | Outdoor/800kVA | LT Auxilairy Oil filled Transformers. Work includes erection at plingth, erection of all auxiliaries, viz bushings, terminal connectors, filling of oil, oil filtration, oil testing, testing & Commissioning etc. | Nos. | 1 |  | 0
23 | STRINGING HARDWARE | [5 empty] | 0
23.1 | 400 kV | Double Tension | 400kV Double tension insulator string comprising 2x25 discs with subconductor spacing 450mm suitable for QUAD ACSR BERSIMIS / MOOSE conductor with / without turn Buckle | set | 96 |  | 0
23.5 | 400 kV | Double Tension | 400kV Double tension insulator string comprising 2x25 discs with subconductor spacing 450mm suitable for TWIN ACSR BERSIMIS / MOOSE conductor with / without turn Buckle | set | 12 |  | 0
23.3 | 400 kV | Single Suspension | 400kV Single suspension insulator string comprising 1x25 discs with subconductor spacing 450mm suitable for QUAD ACSR BERSIMIS / MOOSE conductor with straight / drop clamp | set | 27 |  | 0
23.4 | 400 kV | Single Suspension | 400kV Single suspension insulator string comprising 1x25 discs with subconductor spacing 450mm suitable for TWIN ACSR BERSIMIS / MOOSE conductor with straight / drop clamp | set | 15 |  | 0
0
24 | BUS MATERIAL | [5 empty] | 0
| Inclusive of fixing various types of clamps, connectors, spacers, corona rings, sleeves, aluminum welding, fixing of socket and bends, | [5 empty] | 0
24.1 | - | ACSR Bersimis | Conductor complete with Tee connectors for droppers to equipment connections, PG clamps for busbar jumpering, Twin/Quad bundle spacers etc to complete. | Km | 14 |  | 0
24.2 |  | 4.5" | Al Tube (ETC of Al.Tube includes Aluminium welding and bending to be included. Welding sleeve tube will be supplied by BHEL.) | kM | 0.75 |  | 0
24.3 | - | 7/9 SWG Sield Wire | GI Stranded Shield wire including tension clamp, PG clamp and clamping on structure for down conductor, fixing/bolting with earth strip etc to complete. | Km | 2 |  | 0
25 | Marshalling Kiosks & Junction Boxes | [5 empty] | 0
25.1 |  |  | Bay Marshalling Kiosks ( Outdoor, Floor mounted on cable trench) | Nos. | 5 |  | 0
25.2 |  |  | CT Junction Box (on CT structure) | Nos. | 8 |  | 0
25.3 |  |  | CVT Junction Box (on CVT structure/ on foundation) | Nos. | 4 |  | 0
0
0
| CABLE LAYING WORKS | [5 empty] | 0
|  |  | A. Cabling including laying, tagging , dressing, ferruling, lugging, ,soldering, tapping, jointing, crimping, termination, and drilling/ cutting holes in cable gland plates- laying can be either on trays, supports, underground, buried in ground or through GI/PVC pipe over/under ground, through wall etc. All erection materials viz. ferrules, copper lugs, cable ties / straps, Al. tags, markers, GI / PVC wall sleeves with rubber / nylon bushes and flexible steel conduits shall be supplied by bidder. Glands shall be quoted seprately. |  |  |  | 0
26 |  |  | Control cables |  |  |  | 0
26.1 |  | PVC | 2Cx2.5 sqmm Cu | Km | 25 |  | 0
26.2 |  | PVC | 5Cx2.5 sqmm Cu | Km | 14 |  | 0
26.3 |  | PVC | 7Cx2.5 sqmm Cu | Km | 2.8 |  | 0
26.4 |  | PVC | 10Cx2.5 sqmm Cu | Km | 5.5 |  | 0
26.5 |  | PVC | 14Cx2.5 sqmm Cu | Km | 4.8 |  | 0
26.6 |  | PVC | 19Cx2.5 sqmm Cu | Km | 4 |  | 0
0
0
27 |  |  | Auxiliary Power cables |  |  |  | 0
27.1 |  | PVC | 2Cx6 sqmm Al/Cu | Km | 5 |  | 0
27.2 |  | PVC | 4Cx6 sqmm Al/Cu | Km | 2.2 |  | 0
27.3 |  | PVC | 4Cx16 sqmm Al/Cu | Km | 20 |  | 0
27.4 |  | PVC | 3.5Cx35 sqmm Al/Cu | Km | 3.5 |  | 0
27.5 |  | PVC | 3.5Cx70 sqmm Al/Cu | Km | 10 |  | 0
27.6 |  | PVC | 1Cx150 sqmm Al/Cu | Km | 0.5 |  | 0
27.7 |  | XLPE | 3.5Cx300 sqmm Al/Cu | Km | 1.8 |  | 0
27.8 |  | XLPE | 1Cx630 sqmm Al/Cu | Km | 1.6 |  | 0
0
| CABLE GLAND |  | CONTRACTOR'S SUPPLY |  |  |  | 0
28 |  |  | Supply & installation - Tin/ Nickel, Nichel/chromium - Plated (coating thickness not less than 10 microns) Powergrid approved / Sunil & Co. / Arup/ Comet / QPIE make brass cable glands, double compression heavy-duty type complete with necessary armour clamp & tapered washer etc for the following cables (Bidder's Scope is to supply and fixing) Qty may vary by ±50% |  |  |  | 0
28.01 |  | PVC/ XLPE | 2Cx2.5 sqmm Cu | Nos. | 150 |  | 0
28.02 |  | PVC/ XLPE | 5Cx2.5 sqmm Cu | Nos. | 500 |  | 0
28.03 |  | PVC/ XLPE | 7Cx2.5 sqmm Cu | Nos. | 200 |  | 0
28.04 |  | PVC/ XLPE | 10Cx2.5 sqmm Cu | Nos. | 100 |  | 0
28.05 |  | PVC/ XLPE | 14Cx2.5 sqmm Cu | Nos. | 350 |  | 0
28.06 |  | PVC/ XLPE | 19Cx2.5 sqmm Cu | Nos. | 150 |  | 0
28.07 |  | PVC/ XLPE | 2Cx6 sqmm Al/Cu | Nos. | 100 |  | 0
28.08 |  | PVC/ XLPE | 4Cx6 sqmm Al/Cu | Nos. | 16 |  | 0
28.09 |  | PVC/ XLPE | 4Cx16 sqmm Al/Cu | Nos. | 200 |  | 0
28.1 |  | PVC/ XLPE | 3.5Cx35 sqmm Al/Cu | Nos. | 20 |  | 0
28.11 |  | PVC/ XLPE | 3.5Cx70 sqmm Al/Cu | Nos. | 56 |  | 0
28.12 |  | PVC/ XLPE | 1Cx150 sqmm Al/Cu | Nos. | 10 |  | 0
28.13 |  | PVC/ XLPE | 3.5Cx300 sqmm Al/Cu | Nos. | 16 |  | 0
28.14 |  | PVC/ XLPE | 1Cx630 sqmm Al/Cu | Nos. | 7 |  | 0
0
| HT CABLE | [5 empty] | 0
29 |  | 11kV, XLPE | 11kV ,single core, XLPE HT cables along with lugs, cable glands to be laid in burried trench , all civil activities such as excavation, supply and laying of sand, bricks etc. shall be in contractor's scope. Termination kit/staright joint shall be provided by BHEL . All other material like lugs, glands, tripod clamps etc. shall be arranged by contractor (Termination of cable shall be done by termination supplier) | Mtrs | 2000 |  | 0
0
30 | STEEL STRUCTURES | [5 empty] | 0
0
30.1 |  |  | Galvanised steel Lattice Structures including hardwares for Towers, beams & equipment support | MT | 440 |  | 0
30.2 |  |  | Galvanised steel Pipe Structures including hardwares for equipment support | MT | 150 |  | 0
30.3 |  |  | Double pole lattice structure | MT | 4 |  | 0
0
0
0
| Cable Trench Materials | [5 empty] | 0
31 |  |  | Cable Rack work includes welding and fabrication of cable racks of mild steel angles( 50x50x6 mm suplied by BHEL) & painted racks (paint suply in scope of bidder) on inserts of trench walls in trenches in switchyard and control room. Cable rack assembly will be of 2/3/4 tier. | MT | 20 |  | 0
32 |  |  | Laying of 100/110NB PVC pipe at a depth of 300mm including excavation, backfilling, making and repairing of walls in trenches, cutting, threading, fixing of sockets/ bends where required etc. complete. Both ends of PVC pipe shall be closed . (Payment will be made for the as erected pipe length) | Meter | 3000 |  | 0
33 |  |  | Laying of 50/65 NB PVC pipe at a depth of 300mm including excavation, backfilling, making and repairing of walls in trenches, cutting, threading, fixing of sockets/ bends where required etc. complete. Both ends of PVC pipe shall be closed . (Payment will be made for the as erected pipe length) | Meter | 3000 |  | 0
0
34 |  |  | Laying of Cable trays: including bends, tees, elbow, reducers, stiffeners coupler plates, bolting to racks, structure etc. to complete. Scope of minor fabrication is also involved. |  |  |  | 0
34.1 |  |  | 100 to 150 mm wide, 2.5 M long Perforated type | Meter | 300 |  | 0
34.2 |  |  | 100 to 750 mm wide, 2.5 M long Ladder type | Meter | 150 |  | 0
0
| Earthing work | [5 empty] | 0
35 |  |  | Earthing material- The earthing includes earthing of all switchyard equipment, towers, pipe structure, cable trenches, fence, pipe electrode for LA, CVT, neutral of transformer & at interconnections of other grids, Control room equipments using necessary Connectors for earthing flats. Earthing clamping shall be carried out by ETC contractor. GS strip including cutting, bending, welding with 40 mm dia MS rod riser/earth strip, applying zinc rich paint, clamping to structure/building wall etc. to complete. Hardware required for connecting flat on pads of structure & equipment included in scope. The Earthing of equipments, Auxiliary Earthmats under Iso/ ES/ CB MOM boxes shall be carried out as per Powergrid standard earthing drawing. |  |  |  | 0
35.1 |  |  | 75 x 12 mm GI Flat | kM | 3 |  | 0
35.2 |  |  | 50 x 6 mm GI Flat | kM | 2 |  | 0
35.3 |  |  | 50 x 6 mm MS Flat | kM | 2 |  | 0
35.4 |  |  | 40NB Pipe electrode | Nos. | 4 |  | 0
35.5 |  |  | 40mm dia MS Rod for equipment risers | MT | 12 |  | 0
0
36 |  | SUPPLY INCLUDED | SUPPLY AND INSTALLATION OF ISMC 100, ISMC 50 for Panel Supports | MT | 1 |  | 0
|  |  | Total Amount (Rs.) |  |  |  | 0
Following also forms the scope of ETC work in addition to above, but not limited to this.
Note
1 | Erection, Installation, pre-commissioning test and commissioning tests (As per BHEL FQP) are included in the scope.
2 | Annexure- 2 (Switchyard Erection guidelines) shall be followed for ETC work.
3 | All the drawings and documents as per Annexure-1 shall be followed for ETC work.
4 | Minor Civil works such as modification of civil foundations, making holes in the trenches/ control room building, grouting, fixing of trench material will be in the scope of ETC contractor.
5 | Removal of gravel, if gravelling is done, for connection of Equipment earthing strip to the existing mat (wherever earthing mat is already laid), and after completion of earthing , contractor should place the gravel to bring it in original shape.
6 | The quantities given in items mentioned above may undergo a change to any extent.
7 | Quoted rates are deemed to be inclusive of miscellaneous works viz erection of clamps and connectors.
8 | All paint , welding electrodes & other consumable by contract supplies shall be part of ETC works. Paint /welding electrode make etc. is subject to BHEL/CUSTOMER site incharge approval.
9 | Equipment erection (say Isolator ) means complete erection, metallics, post insulator, connectors (expansion/rigid tubular for Al.Tube / single/double/quadraple conductor), connection to the next in line (if connected to overhead busbar or droppers) including PG clamps/Tee connectors etc. This will be clear from the enclosed electrical layout drawings.
10 | Equipment and tower erection would include supply and erection of miscellanneous items , viz Phase colour discs , labels painting of equipments , phase colour painting , phase marking , bay identification board , danger plates , rubber mats , device number marking on the equipment, keyboard etc as per site requirements. Supply & Mounting of phase color discs & Danger plates shall be as per IS-2551; 1982 & IS 5; 1978.
11 | Welding of Aluminium tubes ( supply of welding sleeve excluded) as per Annexure-3 is in ETC contractor's scope and joints shall be tested by radiography. Welding and Bending machines and any other equipment will be in ETC Contractor scope.
12 | Completete ETC package is under the scope of bidder. All TNP including oil filterating machine, cranes etc. required to complete the job shall be provided by bidder only.
13 | Testing istruments (dully calibrated) have to be arranged by ETC Contractor at it's own cost ( List is only provided for information , if any other instrument not mentioned below but required for sucessful completion of ETC work shall be in ETC contractor's scope) , (However OMICRON or equivalent kit for Numerical relay testing shall be arranged by BHEL.)
13.01 | DCRM (OPERATIONAL ANALYZER )
13.02 | Contact Resistance Measurement kit (CRM)
13.03 | Capacitance and Tan delta measurement Kit
13.04 | Dew Point Measurement kit
13.05 | 5kV/1kV Megger
13.06 | Primary current Injection Kit
13.07 | Secondary current/Voltgae Injection kit
13.08 | 1Ph Variac
13.09 | Multimeters
13.1 | Clamp on meter
13.11 | Relay test kit