## Annexure-II
BOQ for Erection Testing & Commissioning (ETC) Works for 400kV Switchyard at Sankhari Rev 01
Customer : POWERGRID CORPORATION OF INDIA LTD.
Project : 400kV S/S Sankhari
Note: | This BOQ covers only ETC work for 400kV Switchyard at Sankhari in Gujarat excluding unloading and storage .Unloading and storage of all the material shall be covered in separate BOQ (Annexure IV). Bidder shall quote only for ETC work in this BOQ, prices for unloading, storage and shifting of material should be filled seperately in Annexure IV.
S.No. | Voltage Class | Type | Description | Unit | Total Qty | Unit Price | Total Price
MAIN EQUIPMENTS
400kV EQUIPMENTS
1 | 400 kV |  | 400KV SF6, 3 Phase Circuit Breaker alongwith lattice type GI supporting structure, terminal connectors, Breaker Control Cabinets, ladder and interpole cabling , SF6 cylinders complete in all respect (Supervision of Erection, Testing and commissioning will be done by supplier. Supplier will bring Timing kit and Gas leak detector only. Necessary manpower support, tools, tackles and testing kit to be in scope of ETC contractor).
1.1 |  | CB | without PIR & without CSD | Nos. | 2 |  | 0
0
2 | 400 kV | HCB | 3 Ph, Isolator, 2000A, motor operated complete with 6 nos. of400kV support insulators & terminal connectors without support structure |  |  |  | 0
2.1. |  |  | - with one earth switch (motor/ manual operated) | Nos. | 2 |  | 0
0
3 | 400 kV | Pantograph | 3 Ph, Isolator, 2000A, motor operated complete with 400kV support insulator, operating rod insulator & terminal connectors without support structure |  |  |  | 0
3.1 |  |  | - without earth switch (motor/ manual operated) | Nos. | 4 |  | 0
3.2 |  |  | - with one earth switch (motor/ manual operated) | Nos. | 2 |  | 0
0
4 | 400 kV | 3000 A | 1 Ph, Current Transformer complete with terminal connectors without support structure. | Nos. | 6 |  | 0
0
5 | 400 kV |  | 1 Ph, CVT complete with terminal connector without support structure. | Nos. | 6 |  | 0
0
6 | 400kV | 0.5mH | Wave Trap pedestal mounted including 3 Nos. 400kV Post Insulators and Terminal connectors without structure | Nos. | 2 |  | 0
0
7 | 400 kV | BPI | Post Insulators complete with corona ring & terminal connectors without support structure | Nos. | 48 |  | 0
0
8 | 336 kV |  | 1 Phase, Gapless type Metal Oxide Surge Arrester complete with surge counter, leakage current meter, insulating base, connecting cable and terminal connectors without support structure | Nos. | 6 |  | 0
0
0
9 | Control and Relay Panels | [5 empty] | 0
0
|  |  | 400 kV Control & Relay Panels |  |  |  | 0
|  |  | Testing and commissioning of relays in scope of panel supplier. Necessary manpower support, tools, tackles and testing equipment to be in scope of ETC contractor |  |  |  | 0
9.1 |  |  | 400kV Circuit Breaker Relay Panel with Auto reclose | Set | 2 |  | 0
9.2 |  |  | 400kV Line Protection Panel | Set | 2 |  | 0
9.3 |  |  | 400kV Bus Bar Protection Panel | No | 1 |  | 0
9.4 |  |  | Time synchronization equipment | Lot | 1 |  | 0
| FO CABLE LAYING |  | Contractor's supplied 30mm HDPE Pipe |  |  |  | 0
9.5 |  |  | SAS : Armoured Fibre Optic system Cable for SAS and Busbar protection ( to be laid in HDPE Pipe) ( Scope - Laying of the cables in the 30mm HDPE PIPE), SUPPLY OF HDPE PIPE (Getco/Powergrid accepted) shall also be in contractor's scope
9.5.1 |  | Supply included in bidders scope | Supply and Laying of 30 mm HDPE pipes conduits alongwith socket, bend and mounting on trench wall / rack support . Installation of the same in complete aspect. Supply of required clamp for fixing of the HDPE pipe on Cable trench wall / rack shall be in ETC contractor scope. (Payment will be made for the as erected pipe length). HDPE Pipe shall be used for laying of fiber optic cables /sensor cables. | M | 500 |  | 0
9.5.2 |  |  | Armoured FO cable along with connectors for SAS & Busbar Protection. The laying of network/optical cables cables shall be in the contractor scope. However, Optical cable will be laid under SAS supplier's supervision. Splicing and Termination shall be in SAS supplier's scope.). FO cable shall be laid in 30 mm HDPE pipes . | M | 500 |  | 0
| PLCC | [5 empty] | 0
10 |  |  | PLCC for 400KV SANKHARI STATION |  |  |  | 0
10.1 |  |  | Coupling device(Phase to Phase) | Nos. | 1 |  | 0
10.2 |  |  | PLCC Panel-Carrier equipment (for speech + protection and speech +data) (Analogue type ) | Nos. | 2 |  | 0
10.3 |  |  | PLCC Panel-Digital Protection coupler | Nos. | 2 |  | 0
10.4 |  |  | 4 wire telephone instrument( Along with telephone wiring ) | Nos. | 1 |  | 0
10.5 |  |  | 5 Pair Telephone Cables, armoured ,0.5 sq. mm annealed copper conductor and petroleum jelly filled with polyethene outer jackets | m | 700 |  | 0
10.6 |  |  | HF Cable laying | m | 100 |  | 0
0
11 | MKJB CTJB CVT JB |  | Marshalling Kiosks & CT / CVT Junction Boxes |  |  |  | 0
11.1 |  |  | Bay Marshalling Kiosks ( Outdoor, Floor mounted on cable trench) | Nos. | 2 |  | 0
11.2 |  |  | CT Junction Box (on CT structure) | Nos. | 2 |  | 0
11.3 |  |  | CVT Junction Box (on CVT structure/ on foundation) | Nos. | 2 |  | 0
0
0
12 | STEEL STRUCTURES | [5 empty] | 0
0
12.1 |  |  | Galvanised steel Lattice Structures including hardwares for Towers, beams & equipment support | MT | 32 |  | 0
12.2 |  |  | Galvanised steel Pipe Structures including hardwares for equipment support | MT | 40 |  | 0
0
13 |  |  | LT AC & DC SWITCHBOARDS |  |  |  | 0
13.1 |  |  | 415V ACDB (having 2. Nos incomer feeder and 12 nos. outgoing feeders) | Set | 1 |  | 0
13.2 |  |  | 220V DCDB (having 4 no. incomer feeder and 12 no. outgoing feeders | Set | 2 |  | 0
0
14 | Cable Trench Materials | [5 empty] | 0
14.1 |  |  | Cable Rack work includes welding and fabrication of cable racks of mild steel angles( 50x50x6 mm suplied by BHEL) & painted racks (paint suply in scope of bidder) on inserts of trench walls in trenches in switchyard and control room. Cable rack assembly will be of 2/3/4 tier. | MT | 1 |  | 0
14.2 |  |  | Laying of 100/110NB PVC pipe at a depth of 300mm including excavation, backfilling, making and repairing of walls in trenches, cutting, threading, fixing of sockets/ bends where required etc. complete. Both ends of PVC pipe shall be closed . (Payment will be made for the as erected pipe length) | Meter | 750 |  | 0
14.3 |  |  | Laying of 50/65 NB PVC pipe at a depth of 300mm including excavation, backfilling, making and repairing of walls in trenches, cutting, threading, fixing of sockets/ bends where required etc. complete. Both ends of PVC pipe shall be closed . (Payment will be made for the as erected pipe length) | Meter | 750 |  | 0
|  |  | Laying of Cable trays: including bends, tees, elbow, reducers, stiffeners coupler plates, bolting to racks, structure etc. to complete. Scope of minor fabrication is also involved. |  |  |  | 0
14.4 |  |  | 100 to 150 mm wide, 2.5 M long Perforated type | Meter | 75 |  | 0
14.5 |  |  | 100 to 750 mm wide, 2.5 M long Ladder type | Meter | 40 |  | 0
0
| Earthing work | [5 empty] | 0
15 |  |  | Earthing material- The earthing includes earthing of all switchyard equipment, towers, pipe structure, cable trenches, fence, pipe electrode for LA, CVT, neutral of transformer & at interconnections of other grids, Control room equipments using necessary Connectors for earthing flats. Earthing clamping shall be carried out by ETC contractor. GS strip including cutting, bending, welding with 40 mm dia MS rod riser/earth strip, applying zinc rich paint, clamping to structure/building wall etc. to complete. Hardware required for connecting flat on pads of structure & equipment included in scope. The Earthing of equipments, Auxiliary Earthmats under Iso/ ES/ CB MOM boxes shall be carried out as per Powergrid standard earthing drawing. |  |  |  | 0
15.1 |  |  | 75 x 12 mm GI Flat | kM | 0.75 |  | 0
15.2 |  |  | 50 x 6 mm GI Flat | kM | 0.5 |  | 0
15.3 |  |  | 50 x 6 mm MS Flat | kM | 0.5 |  | 0
15.4 |  |  | 40mm dia MS Rod for equipment risers | MT | 3 |  | 0
0
16 | BUS MATERIAL | [5 empty] | 0
| Inclusive of fixing various types of clamps & connectors including fire wedge type, spacers, corona rings, sleeves, aluminum welding, fixing of socket and bends, refer note 1. | [5 empty] | 0
16.1 | 400 kV | Double Tension | 400kV Double tension insulator string comprising 2x25 discs with subconductor spacing 450mm suitable for QUAD ACSR BERSIMIS / MOOSE conductor with / without turn Buckle | set | 12 |  | 0
16.2 | 400 kV | Double Tension | 400kV Double tension insulator string comprising 2x25 discs with subconductor spacing 450mm suitable forTWIN HIGH AMPACITY ALUMINIUM Conductor with / without turn Buckle | set | 6 |  | 0
16.3 | 400 kV | Single Suspension | 400kV Single suspension insulator string comprising 1x25 discs with subconductor spacing 450mm suitable for QUAD ACSR BERSIMIS / MOOSE conductor with straight / drop clamp | set | 6 |  | 0
16.4 | 400 kV | Single Suspension | 400kV Single suspension insulator string comprising 1x25 discs with subconductor spacing 450mm suitable for TWIN HIGH AMPACITY ALUMINIUM Conductor with straight / drop clamp | set | 3 |  | 0
16.5 | - | 7/9 SWG Sield Wire | GI Stranded Shield wire including tension clamp, PG clamp and clamping on structure for down conductor, fixing/bolting with earth strip etc to complete. | M | 300 |  | 0
16.6 | - | HIGH AMPACITY ALUMINIUM | Conductor complete with Tee connectors for droppers to equipment connections, PG clamps for busbar jumpering, Twin bundle spacers etc to complete. | M | 450 |  | 0
16.7 | - | MOOSE ACSR | Conductor complete with Tee connectors for droppers to equipment connections, PG clamps for busbar jumpering, Quad bundle spacers etc to complete. | M | 2200 |  | 0
16.8 |  | 4.5" | Al Tube (ETC of Al.Tube includes Aluminium welding and bending to be included. Welding sleeve tube will be supplied by BHEL.) | kM | 0.45 |  | 0
| Cable Laying Work | [5 empty] | 0
|  |  | A. Cabling including laying, tagging , dressing, ferruling, lugging, ,soldering, tapping, jointing, crimping, termination, and drilling/ cutting holes in cable gland plates- laying can be either on trays, supports, underground, buried in ground or through GI/PVC pipe over/under ground, through wall etc. All erection materials viz. ferrules, copper lugs, cable ties / straps, Al. tags, markers, GI / PVC wall sleeves with rubber / nylon bushes and flexible steel conduits shall be supplied by bidder. Glands shall be quoted seprately. |  |  |  | 0
19 |  |  | Control cable |  |  |  | 0
19.1 |  | PVC | 2Cx2.5 sqmm Cu | Km | 2 |  | 0
19.2 |  | PVC | 4Cx2.5 or 5CX2.5 sqmm Cu | Km | 2 |  | 0
19.3 |  | PVC | 7Cx2.5 sqmm Cu | Km | 3 |  | 0
19.4 |  | PVC | 10Cx2.5 sqmm Cu | Km | 0.5 |  | 0
19.5 |  | PVC | 12Cx2.5 or 14CX2.5 sqmm Cu | Km | 1 |  | 0
19.6 |  | PVC | 19Cx2.5 sqmm Cu | Km | 3.5 |  | 0
19.7 |  | PVC | 27Cx2.5 sqmm Cu | Km | 0.5 |  | 0
19.8 |  | PVC | 4Cx4 sqmm Cu | Km | 1.2 |  | 0
|  | PVC | 12Cx4 sqmm Cu | Km | 2 |  | 0
20 | [6 empty] | 0
20.1 |  |  | Auxiliary and Power cable |  |  |  | 0
20.2 |  | PVC | 2Cx6 or 2CX4 sqmm Al/Cu | Km | 1 |  | 0
20.3 |  | PVC | 4Cx6 sqmm Al/Cu | Km | 0.5 |  | 0
20.4 |  | PVC | 4Cx16 sqmm Al/Cu | Km | 0.5 |  | 0
20.4 |  | PVC | 3.5Cx25 sqmm Al/Cu | Km | 0.2 |  | 0
20.5 |  | PVC | 3.5Cx50 sqmm Al/Cu | Km | 0.5 |  | 0
20.6 |  | PVC | 1Cx50 sqmm Al/Cu | Km | 2 |  | 0
0
0
| CABLE GLAND |  | CONTRACTOR'S SUPPLY |  |  |  | 0
21 |  |  | Supply & installation - Tin/ Nickel, Nichel/chromium - Plated (coating thickness not less than 10 microns) Powergrid approved / Sunil & Co. / Arup/ Comet / QPIE make brass cable glands, double compression heavy-duty type complete with necessary armour clamp & tapered washer etc for the following cables (Bidder's Scope is to supply and fixing) Qty may vary by ±50% |  |  |  | 0
19.1 |  | PVC | 2Cx2.5 sqmm Cu | No. | 50 |  | 0
19.2 |  | PVC | 4Cx2.5 or 5CX2.5 sqmm Cu | No. | 10 |  | 0
19.3 |  | PVC | 7Cx2.5 sqmm Cu | No. | 80 |  | 0
19.4 |  | PVC | 10Cx2.5 sqmm Cu | No. | 40 |  | 0
19.5 |  | PVC | 12Cx2.5 or 14CX2.5 sqmm Cu | No. | 60 |  | 0
19.6 |  | PVC | 19Cx2.5 sqmm Cu | No. | 150 |  | 0
19.7 |  | PVC | 27Cx2.5 sqmm Cu | No. | 10 |  | 0
19.8 |  | PVC | 4Cx4 sqmm Cu | No. | 50 |  | 0
|  | PVC | 12Cx4 sqmm Cu | No. | 30 |  | 0
20.2 |  | PVC | 2Cx6 or 2CX4 sqmm Al/Cu | No. | 40 |  | 0
20.3 |  | PVC | 4Cx6 sqmm Al/Cu | No. | 40 |  | 0
20.4 |  | PVC | 4Cx16 sqmm Al/Cu | No. | 20 |  | 0
20.4 |  | PVC | 3.5Cx25 sqmm Al/Cu | No. | 20 |  | 0
20.5 |  | PVC | 3.5Cx50 sqmm Al/Cu | No. | 10 |  | 0
20.6 |  | PVC | 1Cx50 sqmm Al/Cu | No. | 10 |  | 0
0
21 |  | SUPPLY INCLUDED | SUPPLY AND INSTALLATION OF ISMC 100, ISMC 50 for Panel Supports | MT | 1 |  | 0
|  |  | Total Amount (Rs.) |  |  |  | 0
Following also forms the scope of ETC work in addition to above, but not limited to this.
1 | Clamps and connectors shall be as per GETCO philosophy. e.g. Fire wedge type is to be used for Lines / Bus Dropper interconnection to bay equipment in place of bolted type clamps. Bidder to make all the arrangement for mounting of clamp and connectors except the gun/ firing procedure that will be dealt by connector supplier.
2 | FO cable shall be laid in HDPE duct, which shall be supported on side wall of cable trench
3 | GETCO standard ferruling methodology shall be adopted for wiring work. e.g. Wire No./ TB number/ destination wire no. with TB no. e.g. ( K3 / X01-05 / R1A X04-09).
5 | Installation, pre-commissioning test and commissioning tests (As per BHEL FQP) are included in the scope.
6 | Annexure- 2 (Switchyard Erection guidelines) shall be followed for ETC work.
7 | All the drawings and documents as per Annexure-1 shall be followed for ETC work.
8 | Minor Civil works such as modification of civil foundations, making holes in the trenches/ control room building, grouting, fixing of trench material will be in the scope of ETC contractor.
9 | Removal of gravel, if gravelling is done, for connection of Equipment earthing strip to the existing mat (wherever earthing mat is already laid), and after completion of earthing , contractor should place the gravel to bring it in original shape.
10 | The quantities given in items mentioned above may undergo a change to any extent.
11 | Quoted rates are deemed to be inclusive of miscellaneous works viz erection of clamps and connectors.
12 | All paint , welding electrodes & other consumable by contract supplies shall be part of ETC works. Paint /welding electrode make etc. is subject to BHEL/CUSTOMER site incharge approval.
13 | Equipment erection (say Isolator ) means complete erection, metallics, post insulator, connectors (expansion/rigid tubular for Al.Tube / single/double/quadraple conductor), connection to the next in line (if connected to overhead busbar or droppers) including PG clamps/Tee connectors etc. This will be clear from the enclosed electrical layout drawings.
14 | Equipment and tower erection would include supply and erection of miscellanneous items , viz Phase colour discs , labels painting of equipments , phase colour painting , phase marking , bay identification board , danger plates , rubber mats , device number marking on the equipment, keyboard etc as per site requirements. Supply & Mounting of phase color discs & Danger plates shall be as per IS-2551; 1982 & IS 5; 1978.
15 | Welding of Aluminium tubes ( supply of welding sleeve excluded) as per Annexure-3 is in ETC contractor's scope and joints shall be tested by radiography. Welding and Bending machines and any other equipment will be in ETC Contractor scope.
16 | Completete ETC package is under the scope of bidder. All TNP including oil filterating machine, cranes etc. required to complete the job shall be provided by bidder only.
17 | Testing istruments (dully calibrated) have to be arranged by ETC Contractor at it's own cost ( List is only provided for information , if any other instrument not mentioned below but required for sucessful completion of ETC work shall be in ETC contractor's scope) , (However OMICRON or equivalent kit for Numerical relay testing shall be arranged by BHEL.)
17.01 | DCRM (OPERATIONAL ANALYZER )
17.02 | Contact Resistance Measurement kit (CRM)
17.03 | Capacitance and Tan delta measurement Kit
17.04 | Dew Point Measurement kit
17.05 | 5kV/1kV Megger
17.06 | Primary current Injection Kit
17.07 | Secondary current/Voltgae Injection kit
17.08 | 1Ph Variac
17.09 | Multimeters
17.1 | Clamp on meter
17.11 | Relay test kit