## Enquiry
BHARAT HEAVY ELECTRICALS LIMITED |  |  |  | * This is only a request for quotation and not an order * The Enquiry No., Date and Due Date shall be super-scribed on the cover containing your offer * We work on Sundays and our weekly-off falls on Thursday until further notice. |  |  |  | ENQUIRY
R35 - 415D | (A Govt. of India Undertaking) Boiler Auxiliaries Plant, Ranipet - 632 406, Tamilnadu, INDIA. | [6 empty] | Enquiry No. and Date |  | Due Date (DD.MM.YYYY)
Fax : +91 - 4172 - 241107 & 241103 Phone: +91 - 4172 - 254343 & 254594 e-mail: mkmoorthy@bhelrpt.co.in (AND) mgs@bhelrpt.co.in | [7 empty] | BAP/OT-22/A16 & 06.04.2008 |  | 16.06.2008
Test Certificate |  | Guarantee Certificate |  | Sample | Rev. No. & Date |  | No. of Items | Destination |  | Sheet No.
Required |  | Required |  | Not Required | 0 |  | 1 | BHEL Stores, Ranipet |  | 1
Sl. No. | Material Code, Description & Specification |  |  |  |  | Unit | Quantity | Delivery Schedule
[8 empty] | Lot No. | Delivery Qty. | Dely. Reqd. by
1 | IM8295500100 Air Compressor - 1460 CFM as per the worksheet 'Tech_Spec'. |  |  |  |  | No. | 1 | 1 | 1 | Supplier to specify
Note:
1. This is a Notice Inviting Tender.
2. Sealed tenders (under two-bid, three-cover system) are to be submitted against this Enquiry.
3. Tender Documents - Technical Specification, Commercial Terms & Conditions etc. are to be downloaded from our web site www.bhel.com
4. Any Change/s and / or Corrigenda to the Tender Enquiry including change of tender opening date, if any, would be hosted on the web only. No separate publication in the newspapers or notice through other media would be given to the intending bidders by BHEL.
5. Tender fee for this tender is INR 5000/- (Indian Rupees Five Thousands only) for domestic suppliers and US $ 250/- (US $ Two hundred and fifty only) for foreign suppliers. Tender fee includes all taxes and duties, as applicable.
Supplier's Name and Address |  |  | Dear Sir, | [5 empty] | Please quote Enquiry No., Date, Due Date and Material Code in all your correspondences.
Please submit your lowest quotation on FIRM PRICE, in duplicate subject to our terms & conditions for the above materials so as to reach us on or before the due date by 1000 hrs.
|  |  | 1. Quotations will be opened at 1030 Hrs. on the due date in the presence of the tenderers who may like to be present. | [5 empty] | For and on behalf of Bharat Heavy Electriclas Limited, Ranipet
2. No revision of prices will be entertained after tenders are opened.
3. Late tenders are liable to be rejected.
4. The purchaser shall be under no obligation to accept the lowest or any other tender and shall be entitled to accept or reject any tender in part or full without assigning any reason whatsoever.
|  |  | 5. Manufacture's Name, Trade Mark or patent No., if any should be specified, illustrative leaflets giving particulars are required along with quotation wherever necessary. | [5 empty] | Dy. Manager - Capital Purchase

## Tech_Spec
Boiler Auxiliaries Plant, Bharat Heavy Electricals Limited, Ranipet - 632406, Tamilnadu, INDIA. |  |  | Enquiry No. & Dt.: | BAP/OT-22/A16 & 06.04.2008
|  |  | Due Date : | 16.06.2008
Supplier's Ref.:
Date :
Specification cum Compliance Certificate for Air Compressor - 1460 CFM
Note:-
1. The 'Offered' Column and where applicable, the 'Deviations' & 'Remarks' Column of this format shall be filled in by the Vendor and submitted along with the offer. Inadequate / incomplete, ambiguous or unsustainable information against any of the clauses of the specifications / requirements shall be treated as non-compliance.
2. The offer and all documents enclosed with offer should be in English language only.
Name & Address of the supplier: |  | Name & Address of the Indian Agent:
Telephone No. |  | Telephone No.
Fax No. |  | Fax No.
e-mail : |  | e-mail :
Scope: Supply, Erection & Commissioning of Air Compressor - 1460 CFM complying with the following specification
S No. | Description - BHEL's Requirement | Specified | Offered | Deviations | Remarks
1.0 | SCOPE OF SUPPLY :
1.1 | Design, Manufacture, Supply, Erection and Commissioning of 1460 CFM @ 7.5 bar.g. Air cooled, Two Stage, Stacked rotor, Screw Air Compressor along with complete accessories including 5 m3 Vertical Air Receiver with accessories at Specified Location in Bharat Heavy Electricals Limited, Ranipet, Tamil Nadu. | Vendor to confirm
1.2 | The Compressor with inbuilt inter-coolers and after-coolers, lube system, Control panel, Moisture Separator etc. shall be a complete packaged machine consistent with good accessibility for maintenance. | Vendor to confirm
1.3 | All equipment furnished is to be heavy-duty, continuous, designed for 46 Deg. C ambient temperature | Vendor to confirm
2.0 | TECHNICAL SPECIFICATION :
2.1 | Type: Air cooled, Stacked rotor, Screw Air Compressor | Vendor to confirm
2.2 | Rating | Continuous
2.3 | Delivered flow (Min) | 1460 CFM
2.4 | Rated Pressure (Min) | 7.5 BAR.G
2.5 | Pressure Setting Range | 5.0 to 8.2 BAR.G
2.6 | Compressor Shaft Power (KW) | Vendor to specify
2.7 | Specific Power consumption (Kw/100 CFM) | Vendor to specify
2.8 | Control type : Load/Unload & Modulation | Vendor to specify
2.9 | Lead / Lag facility to sequence multiple compressors | Vendor to specify
2.10 | No. of Stages of the Compressor | Two
3.0 | AIREND CONSTRUCTION :
3.1 | The airend should be of stacked rotors type, with an inlet for first stage only. | Vendor to confirm
3.2 | Intercooler to be housed within the air ends only and shall be designed to achieve peak efficiency across the entire range of flow and pressure. No external piping arrangement is acceptable between the stages | Vendor to confirm
3.3 | To avoid dry start of bearings initially, design should have a buffer coolant arrangement within the screw element. | Vendor to confirm
3.4 | Rotors should be of forged steel and of asymmetrical profile. Rotor shafts shall be precision ground for better efficiency and reliability. | Vendor to confirm
3.5 | Cylindrical roller bearings shall be provided to support the rotors at the inlet of the airend to absorb the radial load. | Vendor to confirm
3.6 | A pair of offset, tapered roller bearings shall be mounted on the discharge end of the male and female rotors, for better distribution of axial load & radial load. | Vendor to confirm
3.7 | Provision for start-up lubrication in airend to be provided to avoid dry start of bearing and consequently enhance life of bearings. | Vendor to confirm
4.0 | DRIVE ASSEMBLY
4.1 | The motor and compressor airend are to be joined by an integral gear drive system. Precision dowels are to be used to insure permanent motor / airend alignment. | Vendor to confirm
4.2 | The gear casing shall be totally enclosed and have a positive pressure coolant feed to the gear mesh for optimum lubrication. The speed optimising gears are to be of AGMA quality. | Vendor to confirm
5.0 | DRIVE MOTOR :
5.1 | The motor is to be specifically designed for the torque, speed and horsepower characteristics of the compressor. | Vendor to note
5.2 | The motor is to be operated by a 415V / 3-Phase / 50 Hz - power source. | Vendor to confirm
5.3 | The motor speed should not exceed 1500 rpm. The motor shall be selected such that full load brake horsepower requirements will permit operations in the motor's peak efficiency range. | Vendor to confirm
5.4 | Insulation for the motor shall be Class F. Class B is not acceptable. The motor shall be supplied such that the motor windings only experience a temperature rise of 95 deg C, above ambient at full load BHP. | Vendor to confirm
5.5 | Motor feet are to be cast as an integral part of the frame. The material shall provide for maximum strength and rigidity for bearing support. | Vendor to confirm
5.6 | Motor leads are to be protected by high temperature glass braided insulation, and are to be extended out of the motor to the starter connection terminals, without the use of an intermediate terminal box. | Vendor to confirm
5.7 | Motors are to be flange faced to accommodate permanent alignment with an integral drive system. The motor shall not require the use of a flexible coupling. | Vendor to confirm
6.0 | STARTER :
6.1 | The compressor package shall include a soft starter (Electronically controlled starter) mounted on its own enclosure. | Vendor to confirm
6.2 | The starter shall be mounted, wired and tested as part of the complete compressor package prior to shipment. | Vendor to confirm
6.3 | Main starter shall include fan motor starter electrically interlocked and wired for proper sequencing. | Vendor to confirm
7.0 | SITE CONDITIONS :
7.1 | Design Inlet conditions | Vendor to note
a. Ambient Temp 45 oC
b. Relative Humidity 70% (Non-condensing)
c. Altitude: 200 Mtr. Above MSL
7.2 | 415V, 3 Phase, 50 Hz 3 wire supply will be provided with an isolator near to the compressor usage point. Control voltage requirements shall be derived by the supplier by providing suitable transformers in the starter / control panels (the power supply may fluctuate + or – 10% from specified voltage and + or – 3% from specified frequency | Vendor to confirm
7.3 | Building size required (L X B X H) | Vendor to specify
8.0 | LUBE OIL SYSTEM:
8.1 | Total lube oil system to be mounted on the base frame of the compressor package | Vendor to confirm
8.2 | Lubrication throughout the compressor shall be maintained by differential pressure. | Vendor to confirm
8.3 | Initial fill of biodegradable oil should be supplied along with the compressor. | Vendor to confirm
8.4 | Coolant change period to be at least 8000 hrs, so as to reduce downtime for maintenance of the compressor. | Vendor to confirm
8.5 | The lubrication system that shall include check valves, relief valves, and other safety components as necessary to ensure cooling system shall be filtered by a 4-micron full flow coolant filter. | Vendor to confirm
8.6 | The coolant filter shall be complete with a pressure relief bypass. | Vendor to confirm
8.7 | A thermal control valve is required to maintain the proper operating temperature of the compressor. | Vendor to provide
9.0 | OPERATION & CONTROL:
9.1 | Compressor to incorporate power and cost saving mechanism for capacity controls: | Vendor to confirm
a. Load / Unload
b. Modulation valve – Electrically operated for precise control (Pneumatically operated actuators are not acceptable)
c. Auto Select mode also should be provided
9.2 | Microprocessor based Control panel with alphanumeric display. | Vendor to confirm
Lead / Lag facility shall be provided to facilitate operating multiple compressors in future.
Data displayed should be on real time reading recorded basis and not on timer based for accurate assessment of performance.
9.3 | Controls for | Vendor to offer
1. Blow down solenoid valve
2. High Airend discharge temp. trip
3. Motor over load trip
4. Air/discharge/sump pressure sensor
5. Solenoid operated oil stop check valve
9.3 | 6. Air discharge temperature sensor | Vendor to offer
7. Power on indication
8. Sensor calibration
9. Modulation controls with automatic control selector
10. Finger touch membrane type start /stop, load/unload, display selector buttons
9.4 | Display for | Vendor to offer
1. Package discharge pressure
2. Package discharge temperature
3. Total Hours / loaded hours
4. Airend discharge temperature
5. Injection Coolant temperature
6. Sump pressure
7. Inlet filter condition
8. Inlet vacuum
9. Coolant filter condition
10. Separator element pressure drop
11. Modulation % load
12. Motor current & voltage
13. Air flow meter
9.5 | Adjustable Operating Parameters for | Vendor to offer
1. Off-line pressure
2. On-line pressure
3. Star delta transition time
4. Stop delay time
5. Auto start & stop shutdown time
6. Auto start and stop on/off
7. Sequencer control on/off
8. Remote start and stop on/off
9.6 | Fault warnings for | Vendor to offer
1. Change inlet filter
2. Change Coolant filter
3. Change separator element
9.6 | 4. High Airend discharge temperature | Vendor to offer
5. High Airend discharge pressure
6. Sensor failure
9.7 | Fault Shutdowns | Vendor to provide
1. High airend discharge temperature
2. Low unloaded sump pressure
3. Low loaded sump, pressure
4. Starter failure
5. Main motor over load
6. Fan motor over load
7. Control Power loss
8. Reverse rotation
9. Inlet control
10. Sensor failure
11. Microprocessor failure memory fault
12. Remote start /stop failure
9.8 | The compressor package should have noise level less than 85 dB (A) at 1M distances | Vendor to confirm
10.0 | AIR RECEIVER :
10.1 | Vertical air receiver capacity (Min.) | 5 M3 (5000 Litres)
10.2 | Size of the vessel ( Diameter x length) | Vendor to specify
10.3 | Maximum working pressure | 12.5 Kg/Cm2.(g)
10.4 | Test pressure of the receiver (Specify the standard & pressure) | Vendor to specify
10.5 | Material of Construction – Shell & Dish end as per IS 2062 Gr. B | Vendor to confirm
10.6 | Code of Construction shall be as per BS 5169: 1992 | Vendor to confirm
10.7 | Corrosion Allowance | 1.5 mm
10.8 | Accessories like Pressure gauge with 4” dial, Spring loaded safety valve & drain valve shall be provided.. | Vendor to confirm
11.0 | GENERAL POINTS :
11.1 | The offer shall include the catalog for offered equipment and a complete technical description of all parts of the compressor as also the materials of construction of the major parts. Full description of compressor protection features should be included. | Vendor to confirm
11.2 | GA Drawing, Schematic & Foundation Diagram Showing the Layout and Interconnections shall be submitted along with the offer. | Vendor to submit
11.3 | Supply of all foundation materials like bolts & nuts, washers, leveling plates etc. required for total installation are vendor's scope. Only Civil works are BHEL scope. | Vendor to confirm
11.4 | Motor shall be any of the following makes: M/s BHEL, ABB, Siemens or any other reputed IMPORTED / LOCAL make. | Vendor to confirm
11.5 | All Electrical devices, Contactors, Relays, Limit, Switches, Push buttons, etc. shall be from Siemens / L&T / Alstom / Cuttler Hammer / Telemecanique or any other reputed. | Vendor to confirm
12.0 | SPARES :
12.1 | Itemized breakup of mechanical, electrical and electronic spares used in the machine in sufficient quantity as per recommendation of Vendor for 2 years of trouble free operation on three shifts continuous running basis shall be offered by vendor. (Unit Price for each item of spare shall be offered in the price bid) | Vendor to offer
12.2 | All types of spares for total machine and accessories shall be available for at least ten years after supply of the machine. If machine is likely to become obsolete in this period, the vendor should inform BHEL sufficiently in advance and provide drawings of parts / details of spares & suppliers to enable BHEL to procure these in advance, if required. | Vendor to offer
12.3 | Vendor to confirm that complete list of spares for machine and accessories, along with item part no / specification / type / model, and name & address of the spare supplier shall be furnished along with documentation to be supplied with the machine. | Vendor to offer
13.0 | DOCUMENTATION :
13.1 | Five sets of following documents (5 Hard copies) in English language should be supplied along with the Compressor
13.2 | Operation & Maintenance Instructions | Vendor to confirm
13.3 | Spare Parts Manual | Vendor to confirm
13.4 | GA Drawing | Vendor to confirm
13.5 | Electrical Wiring Drawings Power & Control circuits | Vendor to confirm
13.6 | Pressure Test certificate for Air receiver and also for inter & after coolers. | Vendor to confirm
13.7 | One additional set of all the above documentation shall be given in the form of CD. | Vendor to confirm
14.0 | TRAINING :
14.1 | The Vendor shall impart one week training to BHEL's Machine Operators and Maintenance crew in Operation and Maintenance after the commissioning of the Machine at BHEL works. | Vendor to confirm
15.0 | ERECTION & COMMISSIONING :
15.1 | Vendor to take full responsibility for erection, start up, test the compressor, it’s control & all types of other supplied equipments. Service requirement like power, interconnecting piping, civil works shall be provided by BHEL at only one point to be indicated by Vendor in their foundation/layout drawings. | Details of these requirements should be informed by Vendor in advance
15.2 | Tools, Tackles, instruments and other necessary equipment required to carry out all above activities should be brought by the Vendor. | Vendor to confirm
15.3 | Commissioning spares, required for commissioning of the machine within stipulated time, shall be brought by the Vendor if required on returnable basis. | Vendor to note
15.4 | Schedule of Erection and Commissioning shall be submitted with the offer. | Vendor to submit
15.5 | Charges, duration, terms & conditions for E&C should be furnished in detail separately by Vendor along with offer. | Vendor to furnish
16.0 | TESTING & ACCEPTANCE :
16.1 | The equipments shall be offered for inspection by BHEL Engineers at suppliers works prior to dispatch. | Vendor to confirm
16.2 | Testing: - Compressor shall be fully tested at the supplier’s works to determine its mechanical and electrical characteristics. Compressor air capacity, pressures and temperatures shall be measured and recorded. | Vendor to confirm
17.0 | GUARANTEE :
17.1 | The equipment and accessories shall be guaranteed for proper operation and shall have guarantee for all parts for a period of 24 months from the date of commissioning. | Vendor to confirm