## Sheet1
Sl. No. | Description for BHEL Requirement | SPECIFIED / TO BE CONFIRMED BY | Offered | Deviations | Remarks
1 | PURPOSE : The Diesel Generator set is intended to be used as a standby emergency power source for catering to emergency loads in case of Mains Power failure during high speed balancing of rotors of turbines, Generators, Compressors, etc.,
1.1 | 400 KW / 500 KVA DIESEL GENERATOR SET in APPCB approved Acoustic Enclosure with in built AVM (Anti Vibration Mounting) pads.
1.2 | Type of Installation : Outdoor
QUANTITY : 1 SET
2 | SCOPE:
This specification is intended to cover the design, manufacture, assembly, testing at manufacturer's works in presence of our representative, delivery to site and erection & commissioning of 400 KW / 500 KVA DIESEL GENERATOR SET, complete with all accessories fitted and features mentioned below:
2.1 | DIESEL ENGINE:
2.1.1 | Type : 4 Strokes
2.1.2 | No: of Cylinders : 6 Cylinders
2.1.3 | Cooling : water cooled and turbo charged, Diesel Engine
2.1.4 | Capacity : Minimum 600 BHP @ 1500 RPM under NTP conditions
2.1.5 | Engine designed to run continuously, confirming to BS: 5514/ DIN-6271/IS 10002/ ISO – 3046 with an overload capacity of 10% for one hour in any 12 hours continuous operation
2.1.6 | The engine shall be complete with the following accessories:
A | Radiator
B | Corrosion inhibitor coolant, Engine Lubrication system.
C | Paper element filters for fuel, lube oil and by-pass
D | Flywheel to single bearing alternator with housing
E | Dry type air cleaners and vacuum indicators
F | PT Self Adjusting direct fuel injection system
G | Silencer
H | Stainless steel exhaust flexible bellows
I | Electronic Control panel with digital governor suitable for synchronization
J | Electric Starter, Starter Motor & Batteries
K | Battery charging alternator
L | Electronic Instrument panel displaying the following:
i: Battery Voltage
ii: Coolant Water Temperature
iii: Lubricating Oil Pressure
iv: Engine Speed
v: Engine Hours
M | Safety Control (Trip & Indication for):
i: High water temperature(HWT)
ii: Low lube oil pressure (LLOP)
iii: Over speed stop
N | Air inlet system, Charging system, Control system, Exhaust system
2.2 | FUEL CONSUMPTION:
2.2.1 | At 75% of rated load the Bench Mark - Fuel Consumption is 78.0 litres /hr. The fuel consumption indicated by the supplier shall be guaranteed for first 600 hours of operation / first one year whichever is earlier
2.3 | EFFICIENCY:
2.3.1 | 90% or higher. Performance Guarantee Certificate (Specifically indicated from Authorized agency for Certification) to be provided by the supplier for Type approval and conformity of production testing of DG set.
2.4 | ALTERNATOR :
2.4.1 | Alternator confirming to BS:5000/ IS:4722 with standard design with IP 23 Protection, suitably rated at 400 KW / 500 KVA at 0.8pf, 415 Volts, 3 phase, 4 Wires, 50 Hz., 1500 RPM, self excited (brushless excitation)and self regulated, Band of Voltage Regulation +/-1.5% of rated voltage (from no load to full load) and Class “H” Insulation. Wave form distortion at no-load: < 1.8%. Alternator should be mounted on a common single base frame and coupled directly to the engine.
2.5 | BASE FRAME:
2.5.1 | Sturdy, fabricated / welded construction, made out of high quality Steel section suitable for mounting the engine and alternator. The base frame shall be suitably designed to simplify transportation, handling, slinging, E&C. Shall have provision for levelling adjustments, as required during installation.
2.6 | CONTROL PANEL:
2.6.1 | Vermin proof Cubicle type, floor mounting Control Panel, having facility to operate DG set incorporating the following:
i: Suitable Moulded Case Circuit Breaker, Ammeter with Selector switch
ii: Voltmeter with Selector Switch, 500 Volts
iii: Frequency Meter
iv: KWH Meter
v: KW/PF Meter
vi: Current Transformers
vii: Indicating Lamps for Supply “ON” & Load “ON”
viii: Instrument fuses duly wired & ferruled.
2.6.2 | Power connection from DG set to Control Panel.(Cable shall be included in the scope)
2.6.3 | The DG set will be run continuosly on no-load during balancing of rotors. Provision shall be made for continous operation of the DG set by incorporating bypass arrangement for Mains & DG set supply.
2.7 | FUEL TANK:
2.7.1 | Fuel Tank should be base mounted only and not as a separate day tank.
2.7.2 | Built in fuel pump (min. 0.5HP) for topping up of Diesel day tank.
2.8 | BATTERY:
2.8.1 | Suitable Dry type Batteries of Standard Make with leads and Terminals shall be part of the equipment. The pack shall be suitably positioned and modular withdraw able to ease of servicing. The Battery pack shall be minimum 180 AH, Lower capacity battery pack will be loaded to equipment cost. Battery charging shall be thru' built in charging alternator in the DG set.
2.9 | NOISE LEVEL outside the enclosure:
2.9.1 | 75 dbA at a distance of 1metre under free field condition and adhere to the guide lines of MOEF (Ministry of Environment and Forest) and APPCB (Andhra Pradesh Pollution Control Board) norms.
2.1 | ACOUSTIC ENCLOSURE :
2.10.1 | Acoustic enclosure should be integrated ready to use type and should not be drop down or canopy type
2.10.2 | Acoustic enclosure base frame should have provision for lifting the enclosure with DG set inside
2.11 | CHIMNEY :
2.11.1 | Exhaust from the DG set shall be provided along with the DG set as per the guide lines of APPCB (Andhra Pradesh Pollution Control Board) norms.
2.12 | Lube oil System: Complete with cooling system, oil temperature monitor, filtration system up to 20 microns, level indicator and fume disposal system to be provided. Fuel system with primary and secondary fuel filter, fuel pump to be provided.
3 | SPARES & MAINTENANCE:
3.1 | Free Maintenance of DG set with Spares for the guarantee period as per BHEL Terms & Conditions.
3.2 | The Supplier should attend to the Breakdowns within 24 hours of reporting the fault and put the DG set back in Operation.
4 | TRAINING :
4.1 | Training to the Staff of BHEL involved in Operation & Maintenance of DG set to be imparted at site. Vendor to specify duration.
5 | QUALIFICATION CRITERIA :
5.1 | Only those vendors (OEMs or their authorised agents for this tender), who have supplied and commissioned at least THREE such sets (400KW/500KVA or higher rating) and such sets are presently working satisfactorily for more than one year after commissioning (On the Date of Opening of tender), should quote. Vendor shall furnish details of such customers (as per clause 5.4 to 5.6) and also order copies. This is required from all the Vendors for qualification of their offer.
5.2 | Proof of service centre in twin cities to be provided.
5.3 | The engine/generator set distributor shall have factory trained service representatives in Hyderabad.
5.4 | 1. Name of the customer- I / company- I where referred DG set is installed.
2. Complete postal address of the customer- I
3. Month and year of commissioning
4. Parameters of DG set supplied
5. Name and designation of the contact person of the customer
6. Phone, FAX no. and email address of the contact person of the customer.
5.5 | 1. Name of the customer- II / company- II where referred DG set is installed.
2. Complete postal address of the customer- II
3. Month and year of commissioning
4. Parameters of DG set supplied
5. Name and designation of the contact person of the customer
6. Phone, FAX no. and email address of the contact person of the customer.
5.6 | 1. Name of the customer- III / company- III where referred DG set is installed.
2. Complete postal address of the customer- III
3. Month and year of commissioning
4. Parameters of DG set supplied
5. Name and designation of the contact person of the customer
6. Phone, FAX no. and email address of the contact person of the customer.
5.7 | Performance certificate from any one the above customers regarding satisfactory performance of DG set supplied to them (Original certificate or Through E-mail directly from the customer).The Original performance certificate may be returned after verification by BHEL, if required.
5.8 | BHEL reserves the right to verify the information provided by vendor. In case the information provided by vendor is found to be false/incorrect, the offer shall be rejected
6 | DOCUMENTATION:
6.1 | The following documents in two sets shall be furnished along with the offer:
A | GA drawings
B | Foundation details
C | Filled in data sheets
6.2 | The following documents shall be furnished in 4 sets within 2 weeks after LOI for our approval.
A | Final GA drawings
B | Final foundation details
C | Control schematics
D | Bill of materails
6.3 | The following documents shall be furnished in duplicate along with the equipment.
A | O&M Manual containing list of Components with Specification, Schematic diagram, circuit diagram, troubling shooting, instruction for O&M etc.
B | Type test certificates conducted on similar switchgear panel.
C | Current rating Vs Ambient temp.curves for the breaker, with breaker located inside the cubicle for ambient temperature ranging from 15 Deg.C to 50 Deg.C.
D | Typical foundation arrangement.
7 | GUARANTEE:
7.1 | Guarntee period shall be as per BHEL Terms and conditions.
8 | TESTING/INSPECTION:
8.1 | Inspection at supplier’s works before despatch is required for Performance evaluation at full load & 75% load. Complete DG set shall be tested along with acoustic enclosure.
8.2 | The equipment shall be despatched only after testing/inspection at supplier's works and on written clearance from BHEL