## Mode-1
Price Bid for Fabrication and Supply of Factory Fabricated Structures of Power house, CCR and Mill Bunker Structures at 2X800 MW Singrauli TPS
Total Price towards Execution of works of Package-A in Mode-1
| Description | UOM | Qty | Average Rates | Amount | Weightage
2300 | STRUCTURAL WORKS: Structural steel works including all labour, material (unless otherwise specified in BOQ/contract specification), equipments unless otherwise specified, transportation, handling etc. at all level as per specification, drawings and as directed by engineer - in - charge.
A2301 | Fabrication (shop fabricated in customer approved shop as per specification including painting as per applicable corrosivity class mentioned in specification), of Medium and High Tensile structural steel (Grade designation E350/E250 or higher unless stated otherwise) Quality B0 (Fully killed), conforming to IS 2062. Plates beyond 12mm thickness and up to 40mm thickness shall be normalized rolled. Plates beyond 40mm thickness shall be vacuum degassed & furnace normalised and shall also be 100% ultrasonically tested as per ASTM –A578 level BS2. The fabrication can be with rolled section / built up section / combination of both conforming to IS:2062, pipes conforming to IS:1161/ IS:1239, chequered plate conforming to IS: 3052, mild steel rounds, monorails, stays, safety chains, ladders, MS grating etc. in columns, beams, gantry girders, roof trusses, portals, laced purlins, space frames, hangers, struts, monorails, galleries, stiffeners, wall beams, sheeting runners, brackets, stub columns, bracings, cleats, trestles, base plates, splice plates, chequered plate flooring, decking and seal plates, steel frame grid over false ceiling, walkway platforms, ladders, stairs, stringers, treads, landings, fabrication, straightening, cutting, bending, rolling, grinding, machining, drilling, welding, electrodes and other consumables, alignment, assembly, edge preparation, preheating (min preheat and interpass temperature of 20o C for welding over 20 mm and upto 40 mm & 66o C for welding over 40 mm and upto 63 mm & 110o C for thickness over 63 mm & use of low hydrogen/ radiogenic electrodes), post heating, testing of welders, inspection of welds, visual inspection, non-destructive and special testing which shall cover the conductance of Radiography Testing, Ultra sonic Testing of welds, RT, UT, DPT and MPT of Plates as per ASTM A435, and/or on welds wherever specified including equipments, measuring devices, gauges, test report etc. all complete, rectification and correction of defective welding works, production test plate, inspection and testing, protection against damage in transit, stability of structures, installation of temporary structures, setting column bases, rectification, dismantling and removal of all temporary structures, assembly of the structures at factory for testing etc. of Unit#2.
A2301 a | Grade of Steel: E250 Sections (Material shall be in BHEL scope) | MT | 8913 | 0 | 0 | 0.34158
A2301 b | Grade of Steel: E350 Sections (Material shall be in BHEL scope) | MT | 5948 | 0 | 0 | 0.22795
A2301 c | Grade of Steel: E250 Sections (Material shall be in Vendor scope) | MT | 1000 | 0 | 0 | 0.14617
A2301 d | Grade of Steel: E350 Sections (Material shall be in Vendor scope) | MT | 660 | 0 | 0 | 0.098665
A2302 | Extra over ST NO. A2301 for blast cleaning of steel structures to near white metal surface(Sa 2 1/2 ) and applying coat of two component moisture curing zinc (ethyl) Silicate primer (solid by volume Minimum 60+/-2% & zinc dust % on dry film minimum 80 %). Zinc dust composition and properties shall be Type-II as per ASTM D520-00. Primer of minimum 70 micron DFT shall be applied over shot blast cleaned surface including touch-up painting etc all complete. Primer coat shall be applied in Shop immediately after blast cleaning by airless spray technique. | MT | 16521 | 0 | 0 | 0.082598
A2305 | Providing and applying (with airless spray technique) intermediate coat of two component polyamide cured epoxy with MIO Content (containing lamellar MIO minimum 30% on pigment, solid by volume minimum 80% ±2%) of minimum 100 micron DFT to be applied after an interval of minimum 24 hours (from the application of primer coat by airless spray technique.) and of approved make including protection and cleaning, scaffolding etc. all complete as per specification for all structures . | MT | 16521 | 0 | 0 | 0.051315
B2305 | Providing and applying Finish coat of two-pack aliphatic Isocyanate cured acrylic finish paint (solid by volume minimum 55% ±2%) with Gloss retention (SSPC Paint Spec No 36, ASTM D 4587, D 2244, D 523) of Level 2 (after minimum 1000 hours exposure, Gloss loss less than 30 and colour change less than 2.0 ΔE) and minimum 70 micron DFT shall be applied after an interval of minimum 10 hours (from the application of sealer coat), Colour and shade of the coat shall be as approved by the Employer) over steel sections already having intermediate coats including protection and cleaning, scaffolding etc. all complete as per specification for all structures . | MT | 16521 | 0 | 0 | 0.051727
[5 empty] | 0 | 1

## Mode-1A
2X800 MW Singrauli TPS
Summary (Un-Priced Rate Schedule)-Mode-1
Sl No | Description | Total Amount | Weightage
1 | Fabrication and Supply of Factory Finished Fabricated Structure of Power House, Common Control Room, Mill Bunker Structure (Columns, Bracings, Wall beams, Floor Beams, Trusses etc.) up-to Project Site, based on input design & detailed drawing provided by BHEL and where most of the raw material supply is in BHEL scope, and as specified in scope / BOQ of Unit#1 and Unit#2. for 2x800 MW NTPC Singrauli (Stage-III), Shakti Nagar, Uttar Pradesh State India. |  | 100%

## Mode-2
Price Bid for Fabrication and Supply of Factory Fabricated Structures of Power house, CCR and Mill Bunker Structures at 2X800 MW Singrauli TPS
Total Price towards Execution of works of Package-A in Mode-2
| Description | UOM | Qty | Average Rates | Amount | Weightage
2300 | STRUCTURAL WORKS: Structural steel works including all labour, material (unless otherwise specified in BOQ/contract specification), equipments unless otherwise specified, transportation, handling etc. at all level as per specification, drawings and as directed by engineer - in - charge.
A2301 | Fabrication (shop fabricated in customer approved shop as per specification including painting as per applicable corrosivity class mentioned in specification), of Medium and High Tensile structural steel (Grade designation E350/E250 or higher unless stated otherwise) Quality B0 (Fully killed), conforming to IS 2062. Plates beyond 12mm thickness and up to 40mm thickness shall be normalized rolled. Plates beyond 40mm thickness shall be vacuum degassed & furnace normalised and shall also be 100% ultrasonically tested as per ASTM –A578 level BS2. The fabrication can be with rolled section / built up section / combination of both conforming to IS:2062, pipes conforming to IS:1161/ IS:1239, chequered plate conforming to IS: 3052, mild steel rounds, monorails, stays, safety chains, ladders, MS grating etc. in columns, beams, gantry girders, roof trusses, portals, laced purlins, space frames, hangers, struts, monorails, galleries, stiffeners, wall beams, sheeting runners, brackets, stub columns, bracings, cleats, trestles, base plates, splice plates, chequered plate flooring, decking and seal plates, steel frame grid over false ceiling, walkway platforms, ladders, stairs, stringers, treads, landings, fabrication, straightening, cutting, bending, rolling, grinding, machining, drilling, welding, electrodes and other consumables, alignment, assembly, edge preparation, preheating (min preheat and interpass temperature of 20o C for welding over 20 mm and upto 40 mm & 66o C for welding over 40 mm and upto 63 mm & 110o C for thickness over 63 mm & use of low hydrogen/ radiogenic electrodes), post heating, testing of welders, inspection of welds, visual inspection, non-destructive and special testing which shall cover the conductance of Radiography Testing, Ultra sonic Testing of welds, RT, UT, DPT and MPT of Plates as per ASTM A435, and/or on welds wherever specified including equipments, measuring devices, gauges, test report etc. all complete, rectification and correction of defective welding works, production test plate, inspection and testing, protection against damage in transit, stability of structures, installation of temporary structures, setting column bases, rectification, dismantling and removal of all temporary structures, assembly of the structures at factory for testing etc. of Unit#2.
A2301 a | Grade of Steel: E250 Sections (Material shall be in Vendor scope) | MT | 9912.6 | 0 | 0 | 0.5525
A2301 b | Grade of Steel: E350 Sections (Material shall be in Vendor scope) | MT | 6608.4 | 0 | 0 | 0.37671
A2302 | Extra over ST NO. A2301 for blast cleaning of steel structures to near white metal surface(Sa 2 1/2 ) and applying coat of two component moisture curing zinc (ethyl) Silicate primer (solid by volume Minimum 60+/-2% & zinc dust % on dry film minimum 80 %). Zinc dust composition and properties shall be Type-II as per ASTM D520-00. Primer of minimum 70 micron DFT shall be applied over shot blast cleaned surface including touch-up painting etc all complete. Primer coat shall be applied in Shop immediately after blast cleaning by airless spray technique. | MT | 16521 | 0 | 0 | 0.031496
A2305 | Providing and applying (with airless spray technique) intermediate coat of two component polyamide cured epoxy with MIO Content (containing lamellar MIO minimum 30% on pigment, solid by volume minimum 80% ±2%) of minimum 100 micron DFT to be applied after an interval of minimum 24 hours (from the application of primer coat by airless spray technique.) and of approved make including protection and cleaning, scaffolding etc. all complete as per specification for all structures . | MT | 16521 | 0 | 0 | 0.019567
B2305 | Providing and applying Finish coat of two-pack aliphatic Isocyanate cured acrylic finish paint (solid by volume minimum 55% ±2%) with Gloss retention (SSPC Paint Spec No 36, ASTM D 4587, D 2244, D 523) of Level 2 (after minimum 1000 hours exposure, Gloss loss less than 30 and colour change less than 2.0 ΔE) and minimum 70 micron DFT shall be applied after an interval of minimum 10 hours (from the application of sealer coat), Colour and shade of the coat shall be as approved by the Employer) over steel sections already having intermediate coats including protection and cleaning, scaffolding etc. all complete as per specification for all structures . | MT | 16521 | 0 | 0 | 0.019724
[5 empty] | 0 | 1

## Mode-2A
2X800 MW Singrauli TPS
Summay (Un-Priced Rate Schedule)- Mode-2
Sl No | Description | Total Amount | Weightage
1 | Fabrication and Supply of Factory Finished Fabricated Structure of Power House, Common Control Room, Mill Bunker Structure (Columns, Bracings, Wall beams, Floor Beams, Trusses etc.) up-to Project Site, based on input design & detailed drawing provided by BHEL and where most of the raw material supply is in BHEL scope, and as specified in scope / BOQ of Unit#1 and Unit#2. for 2x800 MW NTPC Singrauli (Stage-III), Shakti Nagar, Uttar Pradesh State India. |  | 100%