## Sheet1
DATE : 26-05-2015 | PRE TREATMENT PLANT - 1 x 800 MW TSGENCO KOTHAGUDEM TPS, STAGE - VII, PALONCHA
SCHEDULE OF PRE-BID CLARIFICATION
All clarification from the Technical Specification shall be filled in by the BIDDER clause by clause in this format only.
VOLUME | SECTION | CLAUSE NO. | PAGE NO. | SPECIFICATION REQUIREMENT | CLARIFICATION | REASONS FOR CLARIFICATION | BHEL REPLY
COMMERCIAL QUERIES:
General | - | - | - | - | Kindly confirm whether separate orders are issued for supply & service part. | For bidder's confirmation | REPLIES HAVE ALREADY BEEN FURNISHED
General | - | - | - | - | Kindly clarify if road permits & way bills for materials purchased outside Telangana shall be provided by BHEL. | For bidder's confirmation
General | - | - | - | - | Kindly clarify whether service tax applicable on services part would be paid extra. | For bidder's confirmation
General | - | - | - | - | Kindly clarify if Form C shall be issued by BHEL on Quarterly basis before the end of subsequent quarter. | For bidder's confirmation
General | - | - | - | - | Kindly provide us BHEL VAT registration number for Telangana. | For bidder's confirmation
General | - | - | - | - | Kindly clarify if BHEL would sign High Sea Sales agreement for import purchases and whether applicable certificates and import & export registration codes for the same would be provided. | For bidder's confirmation
General | - | - | - | - | Kindly clarify if insurance coverage during transit, storage, erection & commissioning is under the scope of BHEL. If so, insurance premium costs would not be in the scope of the contractor. | For bidder's confirmation
General | - | - | - | - | Kindly confirm if any concessions/benefits/exemptions on taxes & duties would be available for this job. If so, whether certificates for the same would be provided. | For bidder's confirmation
General | - | - | - | - | Kindly confirm if civil works is envisaged in the scope. | For bidder's confirmation
General | - | - | - | - | Kindly clarify whether service tax (reverse charge) applicable on freight would be reimbursed or it should be loaded in the price bid. | For bidder's confirmation
General | - | - | - | - | Kindly clarify if two separate orders are issued for supply & services whether TDS under Telangana VAT would not be applicable. For supply part tax invoice would be submitted and for service part, service tax invoice would be submitted. | For bidder's confirmation
General | - | - | - | - | Kindly clarify if VAT registration under Telangana would not be required for the contractor since Supply invoice would be submitted using Tamil Nadu VAT/CST registration since all the materials would be purchased outside the state of Telangana. | For bidder's confirmation
General | - | - | - | - | Kindly clarify whether billing schedule of the order would be jointly signed by purchaser and contractor for the contract price. | For bidder's confirmation
General | - | - | - | - | Kindly indicate us whether Octroi and Entry tax are applicable in the state of Telanagana. If applicable whether same would be reimbursed by BHEL. | For bidder's confirmation
PROCESS QUERIES:
(Indian Bidder) PT Plant Price Schedule (As per sheet titled PRICE SCH - MAIN) | SUGGESTIVE PRICE SCHEDULE | 4 | (Indian Bidder) PT Plant Price Schedule (As per sheet titled PRICE SCH - MAIN) | Break-up (%) of prices given at Sl No-2.01 above (To be used during contract execution for payment). | Please confirm whether we can give the percentage breakup according to our estimated cost. Since most of the percentage are not matching to our estimation. | For bidder's confirmation | Please follow technical specification.
Volume II-B | Section C1 | 8.6 | Page 19 of 869 | Chemical House | Kindly clarify if the chlorination system is under BHEL scope. If so, kindly provide the terminal points for the chlorine dosing system. | For Bidder's confirmation/clarification | Chlorination system is excluded from Bidder's scope. For terminal points pls refer ammendmet # 2.
Volume II-B | Section C1 | 9.2 | Page 22 of 869 | "All the civil work of complete Pre-treatment plant……and protection of all the buried pipe shall be as per IS 10221" | Kindly clarify if the supporting structures for equipments housed in the chemical house and centrifuge building will be under BHEL's scope? | For Bidder's confirmation/clarification | Please follow technical specification.
Volume II-B | Section C1 | 10 | Page 23 of 869 | Terminal Points | Kindly clarify the terminal points of the piping for the centrifuge building. | For Bidder's confirmation/clarification | Please follow technical specification.
Volume II-B | Section C1 | 21.00.00 | Page 97 of 869 | F) i)"Coupling with coupling guard, base……operation platforms" | Kindly clarify if the coupling guard, base plate, foundation bolts etc. for the centrifuge will be provided by BHEL? | For Bidder's confirmation/clarification | Please follow technical specification.
Volume II-B | Section C1 | 21.00.00 | Page 97 of 869 | F) ii) "Flushing connections for centrifuge and interconnecting piping, dosing lines" | Kindly clarify if the flushing connections and the interconnecting pipings and dosing lines for centrifuge will be provided BHEL in the centrifuge building? | For Bidder's confirmation/clarification | Please follow technical specification.
Volume II-B | Section D1 | 2.01.09 | Page 126 of 869 | "Three (3) numbers DMF Feed Pumps, each complete with drive moter and all other accessories" | Kindly clarify if the provision of the three DMF feed pumps is under BHEL scope? The same has not been indicated in the technical specification & datasheets. | For Bidder's confirmation/clarification | DMF feed pumps are excluded from Bidder's scope.
Volume II-B | Section D1 | 2) | Page 152 of 869 | v) "In order to increase the efficiency of solid/liquid……supernatant centrate shall be sent to the Thickener by gravity." | Kindly clarify if the provision of the platform for the centrifuge is under BHEL scope? | For Bidder's confirmation/clarification | Please follow technical specification.
Volume VII-A | - | ANNEXURE -1 GROUND CONTOUR PLAN | Page 752 of 869 | Annexure -1 Ground Contour Plan | The ground contour plan is missing from the Technical Specification. Kindly provide us with the same to enable us to work on the civil design. | For Bidder's confirmation/clarification | Ground profile can be seen by bidder by visiting site.
General | - | - | - | - | Please clarify whether buried pipes are required. If so, kindly clarify the area of the piping to be buried along with the corresponding pipe lengths. | For bidder's confirmation | Please follow technical specification.
CIVIL QUERIES:
Volume III-E | Section-IV | 6.03.05 | Page 191 of 869 | Backfilling maybe obtained from b.) some borrow pits as specified by the engineer | provide us the distance of borrow area for backfilling of soils for the PTP plant. | Cost implication. | Please follow technical specification.
Volume II-A | Section-IV | 5.05.00 | Page 394 of 869 | Suitable fencing shall be provided to enclose all openings | In the Key plan DWG PE-DG-410-158-A002 Rev 0, Fencing was not shown. Please confirm whether fencing is required for the proposed PTP plant. | Cost implication. | Please follow technical specification.
Volume VII-A | Section-D4 | 2.00.00-A | Page 616 of 869 | In, general, demolition of existing quarters, levelling & grading of the site will be taken up by TSGENCO. Any additional site preparatory work will be in bidders scope. | Kindly let us know, what extent of area will be cleared & provided for the PTP. | Clarity on scope & land utilisation | Site shall be fully leveled and graded as per plot plan. Only micro grading shall be in bidder scope.
Volume VII-A | Section-D4 | 2.00.00 | Page 616 of 869 | Disposal of surplus soil outside of plant boundary. | provide us the distance of disposal point for surplus earth from the PTP plant. | Cost implication. | Please follow technical specification.
Volume VII-A | Section-D4 | 7.01.00 | Page 650 of 869 | The preliminary soil report is available with the owner and will be furnished for reference on request. | Kindly provide the soil report for bidding reference. | To get the idea on the type of soils and suitable type of foundations required at site. | Bidder to refer ammendment # 2.
Volume VII-A | Section-D4 | 8.02.00 | Page 664 of 869 | Factor of safety against uplift due to hydrostatic forces shall be 1.25 and due to any other loads shall be 1.5 | As per IS 3370 part-1-2009 clause 7.2 b factor of safety against floatation & check against uplift should be 1.20. kindly confirm. | Cost implication. | Please follow technical specification.
Volume VII-A | Section-D4 | 12.02.02 | Page 695 of 869 | Minimum grade of concrete for water retaining structures - M25 | As per Table-1 of IS 3370 part-1 2009, minimum grade of concrete for water retaining structures shall be M30. please confirm. | Codal Provisions. | Water retaining strucutres shall be with Concrete grade M30
Volume VII-A |  | Annexure- I | Page 752 of 869 | Ground Contour Plan | Please provide the contour map. | Clarity on ground profile. | Ground profile can be seen by bidder by visiting site.
General | - | - | - | FGL, EGL, HFL etc.., | Please provide the FGL, FFL, EGL, HFL etc.., | To prepare the HFD. | Refer soil report and plot plan.
ELECTRICAL QUERIES:
Volume II-B | Section C3 | 7 | Page 118 of 869 | PLC shall be connected to DCS through serial link with OPC compliant for monitoring/control. For detailed please refer PLC Architecture | As per the PLC Architecture, the Bidder has assumed that the Fibre Optic cables from PLC to DCS is under BHEL's scope. | For Bidder's confirmation | Confirmed
Volume II-B | Section D | 6.01.00 | Page 133 of 869 | PLC shall be connected to the common BOP network for remote operation / monitoring from CCR. BOP network shall be interfaced with DDCMIS through soft links. | Kindly confirm that the connection to BOP network is in BHEL's scope. | For Bidder's confirmation | BOP network connection with PLC is not rquired. Kindly ignore.
Volume II-B | Section D3 | 1.01.0 | Page 498 of 869 | Each of the relevant BOP areas and different auxiliary systems shall be provided with dedicated PLC or proprietary control system for overall operation and control. | The Bidder has understood that entire DM Plant can be controlled from a single PLC. Please confirm | For Bidder's confirmation | Please follow technical specification.
Volume II-B | Section D3 | 1.01.01 | Page 498 of 869 | There shall be redundant bidirectional OPC link between DDCMIS network and each package PLC including PADO for monitoring/ performance activities. | The bidder has understood that the scope of instrumentation cables is only upto JB. JB to PLC, PLC to DDCMIS is under BHEL's scope. Please confirm. | For Bidder's confirmation | Confirmed
Volume II-B | Section D3 | PLC Data Sheet | Page 504 of 869 | RIO Panel | The Bidder has understood that there is no requirement of an RIO Panel. Hence only the main PLC panel will be provided. Please confirm. | For Bidder's confirmation | Remote I/O panels are required.
Volume II-B | Section D3 | PLC Data Sheet & PLC configuration-PES 145-36A | Page 506 of 869 | Back Up Panel | In the Data sheet, it is marked as not required , whereas in the configuration a back up panel is shown. Should the Bidder provide a back up panel or not? | For Bidder's confirmation | Bidder to provide Back up panel
Volume II-B | Section D3 | PLC configuration-PES 145-36A | Page 506 of 869 | OWS in CCR | Kindly mention the distance between the DM Control Room and CCR, so that the Bidder can consider the required FO Cable | Length of FO Cable to be considered is not known. | Distance between the DM Control Room and CCR is 450 meters.