ATTACHMENT -1-SCHEDULE OF PREBID CLARIFICATION

| SL NO. | VOLUME/SECTION | CLAUSE NO. | PAGE NO. | SPECIFICATION REQUIREMENT | CLARIFICATIONS | REASON FOR CLARIFICATIONS | BHEL REPLIES |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B SECTION –C1 | 6.0 | Page 15 of 869 | SCOPE OF SUPPLY (CIVIL) All civil design and construction works except Chemical House and centrifuge building are in bidder’s scope | We understand that all civil works for RCC tanks & sumps, foundation of pumps, tanks & equipments along with lining of tanks inside chemical house & centrifuge building will be in the scope of the client. Please clarify. | Since construction of chemical house & centrifuge building is not in the scope of the bidder. Hence we understand that all civil works for RCC tanks & sumps, foundation of pumps, tanks & lining & equipments inside chemical house & centrifuge building will be in the scope of the client. Please clarify. | Please follow technical specification. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B SECTION –C1 | 7.0 | Page 16 of 869 | DESIGN CRITERIA AND TECHNICAL DETAILS A minimum free board of 300 mm shall be provided in all the water retaining structures of PT Plant (such as Aerator, Stilling chamber, all the channels, Clarifiers, Clarified water tank, Overhead filtered water tank, Sludge sump, Backwash water collection sump, Chemical tanks etc.) above the maximum water level/ overflow level as the case may be excluding the thickness of the slab / beam thickness if any. | We understand that civil works for overhead filtered water tank & backwash water collection sump is excluded from bidder’s scope. Please clarify. | Please note that as per datasheet & P&ID overhead filtered water tank & backwash water collection sump is not in our scope of supply. Hence we understand that the same is excluded from our scope. Please clarify. | Bidder to note that Clarified water tank, overhead filtered water tank & backwash water collection sump are excluded from Bidder’s scope. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B SECTION –C1 OR SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B SECTION –C1/DATASHEET –A FOR PRE TREATMENT PLANT | 8.1 OR 1.00.00 | Page 17 of 869 OR Page 83 of 869 | OTHER DESIGN AND CONSTRUCTION FEATURES Plan area shall not be less than 0.03 m^2 per m^3/hr OR CASCADE AERATOR Design minimum surface flow rate for Aerator m2/m3/hr:0.04 | We understand that the bidder needs to consider the design min. surface flow rate as 0.03 m^2 per m^3/hr. Please clarify. | As there is contradiction in the tender documents for min. surface flow rate of cascade aerator in datasheet & other design & construction features. | Bidder to note that the Design minimum surface flow rate for Aerator shall be 0.04 m2/m3/hr. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B SECTION –C1 | 8.1 , 8.6 | Page 18, 23 of 869 | Chemical house All chemicals required for the entire System of Pre-treatment plant & Effluent treatment plant will be stored in the ground floor of a two-storied Chemical House | We understand that as the chemical requirement of effluent treatment plant is not known to us, we need to consider the chemical house as per the tender layout which is adequate to store pre-treatment plant chemicals. Please confirm. | As we effluent treatment plant is not in our scope of supply. And capacity and details of the same is unknown. | The same shall be provided during detailed engineering stage. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B SECTION –C1 | 8.1 , 8.6 | Page 23 of 869 | Termination points | We understand that as effluent treatment plant is not in our scope of supply, so the service water piping, Instrument air piping, and service air piping in the effluent treatment plant area is not in the scope of PT plant bidder. Please clarify. | As effluent treatment plant is not in the scope of PT plant bidder & the location and area of the same is not known. Please clarify. | Noted. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B SECTION –C1/ DATASHEET –A FOR PRE TREATMENT PLANT | 17.00.0 0 | Page 94 of 869 | THICKENER Guaranteed TSS in treated effluent (supernatant): < 100 mg/l OR Water overflow rate (max): Suitable to provide efficient settlement and removal of solids to maintain Suspended Solids concentration 50 ppm maximum in treated effluent | We understand that the same will be 100 ppm in treated effluent. Please clarify. | As there is contradiction in the tender documents for TSS in treated effluent from thickener as 100 ppm & 50 ppm. Hence we understand that the same will be 100 ppm. Please clarify. | Please follow technical specification. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B SECTION –C1/ DATASHEET –A FOR PRE TREATMENT PLANT OR SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME III-C SECTION –VIII | 2.0. OR 4.14.2 | Page 99 of 869 OR Page 220 of 869 | DATASHEET OF PIPING,ISOLATION GATES & VALVES FOR PRE TREATMENT PLANT CAST IRON BODY BUTTERFLY VALVES Basic Design Code: All the Butterfly valves shall be of double flanged type of low leakage rate confirming to AWWA-C-504 class 150 (min.). OR TECHNICAL SPECIFICATION FOR PIPING, FITTINGS & VALVES Butterfly Valves (for river water / clarified water / filtered water / similar application) Butterfly valves shall be of double flanged or lugged wafer type of low leakage rate conforming to AWWA-C 504 class 150 (min.) or BS-5155 PN 10 / class 150 (minimum) | We understand that the butterfly valves will be as lugged wafer type, BS-5155 PN 10. Please clarify. | Please note that there is contradiction in the tender documents for type of butterfly valves as double flanged or lugged. Hence we understand that the same is lugged type as mentioned in Technical Specifications for piping, fittings & valves of VOLUME III-C SECTION –VIII. Please clarify. | All the Butterfly valves shall be of double flanged type of low leakage rate confirming to AWWA-C-504 class 150 (min.). |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B SECTION –C1/ DATASHEET –A FOR PRE TREATMENT PLANT OR SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME III-C SECTION –VIII | 2.0.00 OR 4.14.2 | Page 99 of 869 OR Page 220 of 869 | DATASHEET OF PIPING, ISOLATION GATES & VALVES FOR PRE TREATMENT PLANT OR TECHNICAL SPECIFICATION FOR PIPING, FITTINGS & VALVES For location and type of Valves / Isolation Gates, Bidder need to refer to the P&I drawings enclosed with this specification. | We understand that bidder has to consider the type of valves for various services as per P&ID & MOC as per the Technical Specifications for Piping, Fittings & valves. Please clarify. | As there is contradiction in the type of valves for various services & MOC of the valves in datasheet & Technical Specifications. Hence we understand that have the bidder has to consider the same as mentioned in Technical Specifications for piping, fittings & valves of VOLUME III-C SECTION –VIII. Please clarify. | Please follow technical specification. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B GENERAL TECHNICAL REQUIREMENT FOR FOR PRE TREATMENT PLANT SECTION-D1 | 2.0.00 | Page 126 of 869 | SCOPE OF SUPPLY AND SERVICES Three (3) numbers DMF Feed Pumps, each complete with drive motor and all other accessories. | We understand that DMF feed pumps are not in the scope of PT plant bidder. Please clarify. | As there is contradiction in the datasheet, P&ID & Scope of supply & service for DMF feed Pumps. Hence we understand that the same is excluded from Pre treatment Package. The same has to be considered in DM package. Please clarify. | DMF feed pumps are excluded from Bidder's scope. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B GENERAL TECHNICAL REQUIREMENT FOR FOR PRE TREATMENT PLANT SECTION-D1 | 2.01.19 | Page 126 of 869 | SCOPE OF SUPPLY AND SERVICES One (1) number Electrically Operated Monorail Hoist of 1.0 Ton safe working capacity and complete with all accessories for handling of Backwash Water Disposal Pumps within Backwash Waste Sump cum Pump House. | We understand that the same is not in our scope of supply. Please clarify. | As Filters along with backwash disposal pumps & sump is not in Pre-treatment Plant bidder. Hence we understand that the Electrically operated monorail hoists for backwash waste sump cum pump house is excluded from our scope of supply. Please clarify. | Noted. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME III-C GENERAL TECHNICAL REQUIREMENT FOR FOR PRE TREATMENT PLANT SECTION-C | 9.0.00 | Page 142 of 869 | BID EVALUATION CRITERIA With reference to Bid Evaluation Criteria, Bidder may please refer to Lead Specification - Volume I-Part-B of this Bid Document | We have not received the documents. Please provide the same or send the website link to download the document | Please note that we could not locate the same in the tender documents. | The same shall be as per the documents available at BHEL site. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME III-C/SECTION-C OR SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B/SECTION C1 | 13.15.00 OR 11.00.00 | Page 143 of 869 OR Page 23 of 869 | GENERAL TECHNICAL REQUIREMENT FOR FOR PRE TREATMENT PLANT All Documents/Drawings/Information as addressed in Specifications for Ventilation and Air Conditioning System - Volume III-D of this Bid Document. OR EXCLUSIONS Air conditioning, ventilation & fire fighting facilities. | We understand that Ventilation & Air conditioning system is not in our scope of supply. Please clarify. | Please note that there is contradiction in the tender documents for the scope of air conditioning & ventilation system. Hence we understand that the same is not in our scope of supply as per Exclusions as mentioned in SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B/SECTION C1. Please clarify. | Air conditioning, ventilation & fire fighting facilities are excluded from Bidder’s scope. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME : IIIE SECTION-IV | 1.00.00 | Page 176 of 869 | GENERAL TECHNICAL REQUIREMENT FOR LARGE DIAMETER LOW PRESSURE PIPING, VALVES AND MISC. TANKS The Large Diameter Piping to be fabricated and installed shall include the following pipe lines having sizes 450 mm NB and above: a) Circulating Water Piping b) Auxiliary Cooling Water Piping c) Raw Water Piping d) DM Closed Cooling Water Piping e) Cooling Tower Make-up Water Piping 1.02.00 The different steel storage tanks are: a) Demineralised Water make up tank. b) Potable Water Storage Tank. c) Service Water RCC Tank. d) Demineralised Water storage tanks e) Condensate Storage Tank f) Fire Water Storage Tanks | We understand that the following large diameter low pressure piping, valves & miscellaneous tanks are excluded from our scope of supply. Please clarify. | As per P&ID & datasheet the same is not in our scope of supply. Hence we understand that the same is excluded from our scope of supply. Please clarify. | Bidder to note that for these items scope shall be in line with section C of the technical specification. |
|  | VOLUME : IIIF SECTION-I SUMP PUMPS, DRIVES AND ACCESSORIES SPECIFICATION NO.-PE-TS-410-158-A001 Page 254 of 869 | 1.00.00 | Pg 257 of 869 | GENERAL TECHNICAL REQUIREMENT FOR SUMP PUMPS, DRIVES AND ACCESSORIES SUMP PUMPS, DRIVES AND ACCESSORIES Group-A Group-B Group-C Group-D | We understand that the following sump pumps are not in the scope of PT plant bidder. Please clarify. | As per datasheet of PT plant the following group pumps are not mentioned. Hence we understand that the following sump pumps are not in the scope of PT plant bidder. Please clarify. | Bidder to note that for these items scope shall be in line with section C of the technical specification. |
|  | VOLUME : IIIF SECTION-III | 1.00.00 | Pg 291 of 869 | MISCELLANEOUS HOISTS ANNEXURE-I LIST OF LOCATION FOR MONORAIL HOIST | We understand that the miscellaneous hoists as per Annexure-I are excluded from PT Plant bidder’s scope of supply. Please clarify. | Please note that as per datasheet of PT plant the same is not mentioned. Hence we understand that the same is not in our scope of supply. We understand that hoists which are mentioned in the datasheet is in the scope of PT plant bidder. Please clarify. | Bidder to note that for these items scope shall be in line with section C of the technical specification. |
|  | VOLUME : IIIB | 1.00.00 | Pg 321 of 869 | SPECIFICATIONS FOR PLANT WATER SYSTEM GENERAL TECHNICAL REQUIREMENT PLANT WATER SYSTEM & POTABLE WATER PUMPS . | We understand that the following is excluded the same from the scope of supply of PT plant bidder. Please clarify. | As per datasheet & P&ID of PT plant the plant water system and potable water pumps are not mentioned. Hence we understand that the following is excluded from the scope of supply of PT plant bidder. Please clarify. | Bidder to note that for these items scope shall be in line with section C of the technical specification. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B SECTION C3 | 12 | 119 OF 869 | Supplied System Shall Provide Group Alarm to be Hard wired to plant DCS | We understand that any Hard wired Cable, Cable Trays, Supports, installation etc between field Instruments /PLC to DCS Shall be in BHEL/Owners Scope. Please clarify. | As per PLC System Configuration diagram, our scope ends at Ethernet port of PLC located in PLC room. | Confirmed that any cable b/w PLC/ Instrument to DCS is in BHEL scope. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B SECTION D1 | 6.01.00 | Pg. 133 of 869 | The operation of River Water Pre-Treatment System (RWPS) control shall be semi-automatic through a PLC based control system with PC based workstations located in RWPS Chemical House Control Room. The PLC shall be connected to the common BOP network for remote operation / monitoring from CCR. BOP network shall be interfaced with DDCMIS through soft links. | As per our understanding the CCR will be located in the BOP network location. As the location of the same is not known, we exclude the OWS in CCR area of BOP network and communication between PLC to OWS in CCR. Our within the raw water pre-treatment plant battery limit | The location of the CCR and OWS in BOP network is not known. | Bidder to consider one number OWS in CCR room and the FO cable b/w OWS and PLC network shall be in bidder scope of supply. |
|  | Vol-11B/Section D1 | 6.05.00 | 136 of 869 | The operation of the Chlorination System for River Water Pre-Treatment shall be semi-automatic and envisaged through the RWPT PLC. | Please provide the IOs to consider in our PLC for raw water pre-treatment chlorination system. | Please note that the details of the chlorination plant are not provided. | Bidder to refer Amendment # 2. |
|  | Vol-11B/Section D2 | 1.01.01 | Pg 498 of 869 | STANDARD TECHNICAL SPECIFICATION FOR CONTROL AND INSTRUMENTATION There shall be redundant bidirectional OPC Link Between DDCMIS and each Package PLC including PADO for Monitoring /Performance Activities. | As Per PLC Architecture Diagram drawing No: ( PES-145-36A)OFC Cable Between PLC to DCS Shall be in BHEL Scope, We have not considered this cable in bidder Scope. | As there is contradiction in standard technical specification in control and instrumentation and PLC Architecture Diagram drawing No. And also note that we do not know the location of the DDCMS/ DCS | FO Cable b/w PLC and DDCMIS is in BHEL Scope of supply. |
|  | Vol-11B /Section D2 | 1.06.01 | Pg 498 of 869 | STANDARD TECHNICAL SPECIFICATION FOR CONTROL AND INSTRUMENTATION The redundant Upper Level Network of each Package PLC System will be connected to redundant server to be located in Plant engineers room .Suitable Fiber Optical cable shall be used for redundant interconnection. | As per PLC configuration PT drawing, drwing No: PES-145-36A) ,scope for OFC Cable for Plant engineers room is not shown/Mentioned with PT System, hence we have excluded any hard wired Cable /OFC, Cable Trays, Supports, installation etc between PLC/Instruments to Plant engineers room . Please confirm | As there is contradiction in standard technical specification in control and instrumentation and PLC Architecture Diagram drawing No. And also note that we do not know the location of the plant engineers room. | Please follow PLC configuration diagram. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 Vol-11B/Section C3 | 7.00.00 | Pg. 118 of 869 | As per the TECHNICAL SPECIFICATION FOR CONTROL AND INSTRUMENTATION it is stated that, PLC Shall be Connected to DCS Through Serial Link with OPC Compliant For monitoring /Control. For Detailed ,Please Refer PLC Architecture Diagram | As Per PLC Architecture Diagram drawing No: ( PES-145-36A)OFC Cable Between PLC to DCS Shall be in BHEL Scope, We have not considered this cable in bidder Scope the same cable will be in owner scope. | Contradiction in scope at different place in tender. | FO Cable b/w PLC and DDCMIS is in BHEL Scope of supply. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B SECTION D3 |  | Pg 506 of 869 | PLC System Configuration | We understand that bidders scope ends at Ethernet port of DM PLC. The Cable, Cable trays, supports, installation, termination Shall be in BHEL Scope. | There are contradiction in various clauses of the tender specifications and the PLC configuration diagram. We have followed the PLC configuration diagram for scope clarity. | Please follow technical specification. |
|  | PE-TS-410-158-A001 |  | Pg 605 of 869 | CABLE BOQ | We understand that in BOQ for cable provided in the referred specification is indicative for cable format and this not the actual requirement. We have considered C&I cable requirement as per scope of supply in tender i.e., from Inst to JBs. | The Bidder’s scope of cabling is only from instruments to JB and JB to PLC. The cables shall be 1P x 0.5 Sqmm. All other cables are excluded from our scope. | Please follow technical specification. |
|  | PE-TS-410-158-A001 |  | -- | Scope of civil work | We understand that the following is excluded : 1) Sand filling under footing of foundations 2) storm water drainage 3) Internal plant roads 4) Overall plant paving 5) Pile foundations are not envisaged Kindly clarify. | As the tender is not clear about the requirement of the following. We have excluded the same. 1) Sand filling under footing of foundations 2) storm water drainage 3) Internal plant roads 4) Overall plant paving 5) Pile foundations are not envisaged | Please follow technical specification. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B SECTION C1 |  |  | P&ID FOR PRE TREATMENT PLANT Clarified Water storage Tank | We understand that civil works for clarified water storage tank is in the scope of the client. | Since the same has been shown as dotted in P&ID and the clarified water storage tank details are not provided in the Data sheets, we understand that the complete works associated with clarified water tank shall be in the scope of the client. | Please follow technical specification. |
|  | SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME II-B SECTION C1 |  |  | P&ID FOR PRE TREATMENT PLANT Motorised plug valves for Lime Dosing System Motorised diaphragm valves for alum & poly Dosing System | Please note that the line size of the chemical dosing line is small and availability of motorised plug and diaphragm valves are less. Hence we presume the same as manual valves | Availability of motorised plug valves & diaphragm valves are less in the market. And the dosing pumps can be controlled by PLC hence we do not envisage any requirement of auto valves in chemical dosing line. | Please follow technical specification. |
|  | VOLUME – II B & III, Technical Specification NO.: PE-TS-410-158-A001 | 7.00.00 7.01.00 | Page 650 of 869 | The preliminary geotechnical investigation report is available with the owner and will be furnished for reference on request. | We requested BHEL to provide the geotechnical investigation report vide email dated 22.06.2015, but the same is not yet received by us | Requesting BHEL to provide the geotechnical investigation report as soon as possible | Bidder to refer Amendment # 2.. |
|  | VOLUME – II B & III, Technical Specification NO.: PE-TS-410-158-A001 | 12.02.02 | Page 695 of 869 | For Reinforced concrete for water retaining structure - the grade of concrete is mentioned as “M-25” | As per IS – 3370 “the minimum grade of concrete for water retaining structure is M-30” | Please confirm the correct grade of concrete for water retaining structure to be followed for bid preparation | Grade of Concrete for Water retailing structures shall be M30 |