## Kothagudam
1x800 MW TSGENCO KOTHAGUDAM TPS STAGE - VII, PALONCHA
PRE-TREATMENT PLANT
PRE-BID QUERIES
Sl.No | Volume | Section | Clause No | Page No | Specification Requirement | Clarification | Reasons for Clarification | BHEL REPLY
1 | NIT |  | 12 - Delivery Schedule |  | Supply: Within 10 months from the date of LOI; E &C: within 6 months from the date of site front availability | Please confirm if site clearance to start the civil works will be given immediately upon issue of LOI and please confirm the duration for completion of civil works. | E&C time given as 6 months is very less if civil works also has to be completed within this time frame from the date of site front availability | Please follow technical specification/ NIT.
2 | VII A | General specification and design criteria for civil and structural works | 10.01.00 - a | 668 of 869 | All major foundation shall rest on pile or on virgin soil. Preliminary Geo-Technical investigation for the proposed site has been carried out by the owner and the report is available with the owner. The same will be furnished to bidder on request and for reference only | There is no soil report attached with the tender documents. We request you to provide us the available Soil report to assess the soil profile at site |  | Please refer ammendment # 2.
3 | II B | SECTION C1 SPECIFIC TECHNICAL REQUIREMENT MECHANICAL | 3.0 SCOPE OF SUPPLY (MECHANICAL & CIVIL) | 11 OF 869 | 3.10 Two (2) numbers distribution chamber as per P & ID enclosed for pre-treatment plant. | Kindly confirmthe requirement of distribution chamber as the HRSCC for each stream working independantly. | There is no requirement of distribution chamber | Please follow technical specification.
4 | II B | SECTION C1 ANNEXURE – III FUNCTIONAL GUARANTEES AND LIQUIDATED DAMAGES | 4.00.01 PRE TREATMENT PLANTPerformance Guarantee Parameters for River Water Pre-treatment System | 60 OF 869 | Sludge Thickener - Suspended Solids in treated water not to exceed 100 ppm. | As the sludge thcikener supernatant will be blended with the raw water, thickener supernatant water can be up to 250 ppm. Request you to review this guarantee requirements. |  | Please follow technical specification.
5 | II B | SECTION C1 DATASHEET –A FOR PRE TREATMENT PLANT | 20.00.00 CENTRIFUGE FEED PUMP | 96 OF 869 | Pumping temperature - 100 C (min), 600 C (max) | Kindly confirm the pumping temperature. |  | The pumping temperature shall be 10 Degree Celsius (minimum) to 60 Degree Celsius (maximum).
6 | II B | SECTION C1 DATASHEET –A FOR PRE TREATMENT PLANT | 21.00.00 CENTRIFUGE | 97 OF 869 | Outlet solid concentration - 25 %(min) | Polymer required to achive 25%(min) outlet solid concentration is high. Kindly confirm the requirement. |  | Please follow technical specification.
7 | II B | SECTION C1 DATASHEET –A FOR PRE TREATMENT PLANT | 21.00.00 CENTRIFUGE | 97 OF 869 | Solid recovery (Guaranteed) - 98 % (min) | Polymer required to achive 98%(min) solid recovery (Guaranteed) is high. Kindly confirm |  | Please follow technical specification.
8 | II B | SECTION C1 SPECIFIC TECHNICAL REQUIREMENT MECHANICAL | 3.0 SCOPE OF SUPPLY (MECHANICAL & CIVIL) | 26 OF 869 | Wherever pipes are running on pipe rack ,Bidder will consider 15 m static head + 10% margin ,in addition to the losses in straight length and bend in pipes and valves etc. while selection of pump head during detailed engineering. | We are designing the pumps with calculated head + 10% margin on the frictional losses. Please confirm. |  | Please follow technical specification.
9 | II B | SECTION-C1 SPECIFIC TECHNICAL REQUIREMENT MECHANICAL | 3.0 SCOPE OF SUPPLY (MECHANICAL & CIVIL) | 11 of 869 | For all pumps, while calculating the pump head, 10% margin shall be considered on frictional losses.
10 | II B | SECTION-C1 SPECIFIC TECHNICAL REQUIREMENT MECHANICAL | 1.0 DESIGN CRITERIA AND TECHNICAL DETAILS | 17 of 869 | Walkway Shall be provided with hand railings around launder periphery of width 1200 mm. Wherease the II B, Clause "1.0 DESIGN CRITERIA AND TECHNICAL DETAILS" (Clause 1.3 Sl.no.VIII) specifies that -The clarifier periphery (all around) shall have sufficient width (minimum 850 mm) to have an easy walkway for general inspection. | Please confirm the width of the walkway. |  | Width of the walkway for each clarifier shall not be less than 1200 mm.
11 | II B | SECTION – D1 GENERAL TECHNICAL REQUIREMENTS FOR PRE TREATMENT PLANT | 8.04.00 Performance Guarantee Parameters for River Water Pre-treatment System : | 141 of 869 | Each pump shall be guaranteed for capacity, total dynamic head and power consumption. | Please furnish us with the format for submission of power consumption. |  | Please follow technical specification.