CLIENT	 :  BHARAT HEAVY ELECTRICAL LIMITED, POWER SECTOR

PROJECT: 1 X 800 MW TSGENCO KOTHAGUDEM TPS STAGE – VII, PALONCHA

SPECIFICATION NO. : PE-TS-410-163-A001

TECHNICAL SPECIFICATION FOR DM PLANT (VOL IIB & III)

PRE-BID QUERIES FOR DM PLANT

Pre-bid queries date: 25.05.2015

ANNEXURE I – LIST OF QUERIES

| Sr No | CLAUSE | DESCRIPTION | QUERIES | BHEL’s REPLY |
| --- | --- | --- | --- | --- |
|  | QUERIES |  |  |  |
|  | Tender doc: PE-TS-410-163-A001, Vol: IIB, Section C1. | Exclusion : Point no. 1 - Sheet 15 of 630, Civil works | We request you to remove all the civil and civil related work from WTP vendor scope. | Please follow technical specification. |
|  | Tender doc: PE-TS-410-163-A001, Vol: IIB, Section C1. | 3.PIPING : Point no. 3 - Page no. 14 of 630, (DM plant feed piping) | Please clarify piping laying is above-ground or underground. If laying of piping is above ground than please confirm the scope of supports, If laying of piping is on ground than please confirm the scope of pedestal. If it is underground please confirm the scope of excavation, back filling and bedding etc. | Bidder to consider entire piping as underground piping. Bidder to please follow technical specification. |
|  | Tender doc: PE-TS-410-163-A001, Vol: IIB, Section C1. | 3.PIPING : Point no. 4 - Page no. 14 of 630, (DM water piping) | Please clarify piping laying is above-ground or underground. If laying of piping is above ground than please confirm the scope of supports, If laying of piping is on ground than please confirm the scope of pedestal. If it is underground please confirm the scope of excavation, back filling and bedding etc. | Bidder to consider entire piping as underground piping. Bidder to please follow technical specification. |
|  | Tender doc: PE-TS-410-163-A001, Vol: IIB, Section C1. | 3.PIPING : Point no. 5 - Page no. 14 of 630, (DM water piping) | Please clarify piping laying is above-ground or underground. If laying of piping is above ground than please confirm the scope of supports, If laying of piping is on ground than please confirm the scope of pedestal. If it is underground please confirm the scope of excavation, back filling and bedding etc.) | Bidder to consider entire piping as underground piping. Bidder to please follow technical specification. |
|  | Tender doc: PE-TS-410-163-A001, Vol: IIB, Section C1. | 3.PIPING : Point no. 6 - Page no. 14 of 630, (DM water piping from common suction header) | Please clarify piping laying is above-ground or underground. If laying of piping is above ground than please confirm the scope of supports, If laying of piping is on ground than please confirm the scope of pedestal. If it is underground please confirm the scope of excavation, back filling and bedding etc. | Bidder to consider entire piping as underground piping. Bidder to please follow technical specification. |
|  | Tender doc: PE-TS-410-163-A001, Vol: IIB, Section C1. | 3.PIPING : Point no. 7 - Page no. 14 of 630, (Filter backwash water piping) | Please clarify piping laying is above-ground or underground. If laying of piping is above ground than please confirm the scope of supports, If laying of piping is on ground than please confirm the scope of pedestal. If it is underground please confirm the scope of excavation, back filling and bedding etc. | Bidder to consider entire piping as underground piping. Bidder to please follow technical specification. |
|  | Tender doc: PE-TS-410-163-A001, Vol: IIB, Section C1. | 3.PIPING : Point no. 8 - Page no. 14 of 630, (Neutralized effluent disposal piping) | Please clarify piping laying is above-ground or underground. If laying of piping is above ground than please confirm the scope of supports, If laying of piping is on ground than please confirm the scope of pedestal. If it is underground please confirm the scope of excavation, back filling and bedding etc. | Bidder to consider entire piping as underground piping. Bidder to please follow technical specification. |
|  | Tender doc: PE-TS-410-163-A001, Vol: IIB, Section C1. | 3.PIPING : Point no. 9 - Page no. 14 of 630, (Potable water piping) | Please clarify piping laying is above-ground or underground. If laying of piping is above ground than please confirm the scope of supports, If laying of piping is on ground than please confirm the scope of pedestal, If it is underground please confirm the scope of excavation, back filling and bedding etc. | Bidder to consider entire piping as underground piping. Bidder to please follow technical specification. |

ANNEXURE II – LIST OF QUERIES – E&I

| Sr No | CLAUSE | DESCRIPTION | CLARIFICATION | BHEL’s REPLY |
| --- | --- | --- | --- | --- |
|  | CLARIFICATION |  |  |  |
|  | Spec No – PE – TS – 410 – 145 – I Page No 511 of 633 | PLC Configuration - In Local Control Room (LCR) 1 no 24” CRT OWS and 1 no 24” CRT OWS+EWS required. In DATA Sheet 1no Laptop is required for PLC Programming. | Shall we considered the below mentioned Items: 1 no 24” CRT OWS, 1 no 24” CRT OWS+EWS and 1 no 15” Laptop Please confirm our understanding. | Bidder to please follow technical specification. |
|  | Spec No – PE – TS – 410 – 145 – I Page No 511 of 633 | PLC Configuration - In Common Control Room (CCR) 1 no 24” CRT OWS | Shall we considered the 1 no 24” CRT OWS for CCR location. Also Please confirm the distance between LCR and CCR. | Bidder to please follow technical specification. |
|  | Spec No – PE – TS – 410 – 145 – I Page No 511 of 633 | PLC Configuration – backup Control Desk | We are not clear the actual requirements by BHEL, Requesting you elaborate the technical requirements and which process application is it required. | Back up Panel shall comprise a window annunciator, MIMIC and Start /Stop push buttons/Indication for the drives for which local operation is required (Quantity shall be finalized during detailed engineering stage). Above requirement shall be considered in addition to the technical specification as given in Pg. 582 of 630, Pt.2.03.00, “Backup Panel” in C&I Spec. Bidder to please follow technical specification. |
|  | Spec No – PE – TS – 410 – 145 – I Page No 511 of 633 | PLC Configuration – LVS 67” | Shall we consider 2 nos 67” LVS for proposed jobs. Please confirm our understanding. | Bidder to please follow technical specification. |