SCHEDULE OF PREBID CLARIFICATION

D.M. PLANT as per Technical Specification No. PE-TS-410-163-A001 for 1X800 MW KOTHAGUDEM TPS

| SL NO. | VOLUME/SECTION | CLAUSE NO. | PAGE NO. | SPECIFICATION REQUIREMENT | CLARIFICATIONS | REASON FOR CLARIFICATIONS | BHEL REPLIES |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SPECIFICATION NO: PE-TS-410-163-A001-VOLUME: II-B /SECTION_C1_ _ SPECIFIC_TECHNICAL_ REQUIREMENT_ | 3.0 | Page 14 of 630 | PIPING All piping within the DM Plant and potable water treatment plant | Please note that since the potable water treatment plant is not in our scope, so we understand that Potable water treatment Plant piping is excluded from the bidder’s scope except Potable water piping upto Potable water storage tank and the piping shall be routed through structural supports. Please clarify. | Please note that Potable water treatment Plant is not in our scope of supply. Hence we understand that all piping is excluded from bidder’s scope except potable water from DM plant to Potable water storage tank in TG building. Please clarify. | Please follow technical specification. |
|  | SPECIFICATION NO: PE-TS-410-163-A001-VOLUME: II-B /SECTION_C1 | 3.0 | Page 14 of 630 | PIPING 200 meter DM water piping from DM plant to DM Water storage tanks 200 meter DM water recirculation piping from DM water regeneration pumps to each DM Water storage tanks. 80 meter DM water piping from common suction header of DM Water storage tanks to DM water regeneration pumps. For details pls refer P&ID for Condensate transfer system (PE-DG-410-100-N109 REV 01) attached elsewhere in the specification. OR Key Plot Plan Of DM Plant | We understand that bidder has to consider DM water piping of 20 meters from MB to DM water storage tank instead of 200 meters & 80 meters suction piping. Please clarify. | As per key plan of DM Plant the distance of MB from DM water storage tank is only 20 m. Hence we understand that bidder has to consider only 20 m piping from MB to DM water storage tank including recirculation & regeneration piping. Please clarify. | Please follow technical specification. |
|  | SPECIFICATION NO: PE-TS-410-163-A001-VOLUME: II-B /SECTION_C1_ _ SPECIFIC_TECHNICAL_ REQUIREMENT_ OR VOLUME : III-C SECTION-II | 9.0 OR 2.33.00 | Page 16 of 630 OR Page 140 of 630 | EXCLUSIONS All chemicals. OR All consumables, bulk chemicals like hydrochloric acid etc., required for pre-commissioning, PG test till taking over along with topping up required for 3 months of operation shall be in the scope of the Bidder. | We understand that all chemicals required for pre commissioning, PG test till taking over along with topping including initial fill is excluded from bidder’s scope of supply. Please clarify. | Please note that there is contradiction in the tender documents for the scope of chemicals. Hence we understand that the same is excluded as per Exclusions mentioned in Section-C1 of Volume-II. Please clarify. | All consumables, bulk chemicals like hydrochloric acid, sodium hydroxide etc., required for pre-commissioning, trial run, PG test till plant hand over shall be in the scope of the Bidder. |
|  | SPECIFICATION NO.: PE-TS-410-163-A001 VOLUME II-B SECTION –C1 | 4.00.00 | Pg 50 of 630 | DM PLANT Performance Guarantee parameters for Demineralization System Activated Carbon Filter Free chlorine content of treated water shall be nil | Please note that the free chlorine will be BDL after ACF. Please confirm. | Please note that Nil guarantee t the outlet of the ACF is not possible. | Please follow technical specification. |
|  | SPECIFICATION NO.: PE-TS-410-163-A001 VOLUME II-B SECTION –C1 |  | Pg 50 of 630 | Water Quality at the outlet of MB Exchanger Total Silica as SiO2:0.01 ppm as SiO2 | Please note that reactive silica will be 0.01 ppm as SiO2 after MB. | Please note that DM plant removes only reactive silica. The guarantee of total silica after MB is not possible. Please confirm. | Please follow technical specification. |
|  | SPECIFICATION NO: PE-TS-410-163-A001 VOLUME: II-B SECTION: C1 | Pg 72 of 630 | 1.00.00 | DM FEED PUMPS Start and stop facility provided both at local and remote Shall be provided by the Bidder in conjunction with Auto Start Facility. | Please note that instrumentation cabling scope is only up to JB. Hence We have provided JB near to DMF Feed pumps. Please note that we have not considered cabling of 800 meters. Please confirm. | Please note that as per tender specifications bidder has to consider cables only upto Junction box. | Please follow technical specification. |
|  | SPECIFICATION NO: PE-TS-410-163-A001 VOLUME: II-B SECTION: C1 | 5.00.00 | Pg 75 of 630 | FILTER BACKWASH SUMP Material of Construction RCC. Type of Protection a) Internal Epoxy painted as per relevant sub section | We understand that all lining & painting for civil structures are excluded from bidder’s scope of supply. Please clarify. | Since RCC is in the scope of BHEL. Hence we understand that all lining/ coating/ tiling/ painting for civil structures & tanks are excluded from bidder’s scope of supply. Please clarify. | Please follow technical specification. |
|  | SPECIFICATION NO: PE-TS-410-163-A001 VOLUME: II-B SECTION: C1 | 5.00.00 | Pg 75 of 630 | Sludge Flushing Arrangement Required through high pressure water and nozzles to ensure no deposition / settling of sludge as per the Bid P&ID Water shall be taken from service water pump discharge header. Booster Pump if required, for producing high pressure water, shall be in Bidder’s scope | Please note that We donot envisage the requirement of any booster pumps/ high pressure jet arrangement. Please clarify. | The backwash waste will carry the waste from only the filter backwash and not any sludge. Hence we do not envisage any high pressure jet arrangement. | Please follow technical specification. |
|  | SPECIFICATION NO: PE-TS-410-163-A001 VOLUME: II-B SECTION: C1 | 33.00.00 | Pg 105 of 630 | NEUTRALIZATION PIT Protection a) Internal: Acid and Alkali Proof Tiles / Lining | We understand that all lining & painting for civil structures are excluded from bidder’s scope of supply. Please clarify. | Since RCC is in the scope of BHEL. Hence we understand that all lining/ coating/ tiling/ painting for civil structures & tanks are excluded from bidder’s scope of supply. Please clarify. | Please follow technical specification. |
|  | SPECIFICATION NO: PE-TS-410-163-A001 VOLUME: II-B SECTION: C1 OR Vol III-C/SEC-VIII | 1.0 OR 4.03.00 | Pg 108 of 630 OR Pg 230 of 630 | DATASHEET OF PIPING & VALVES FOR DM PLANT Demineralised water, Service and Instrument Air Piping less than and equal to 50 mm NB. Stainless Steel as per ASTM A- 312 Gr. 304. Size- as per schedule 40 ANSI B36.10 Demineralised water, Service and Instrument air piping for sizes equal to greater than 65 mm NB: Stainless steel as per ASTM A-312 Gr. 304. Size-upto 150 mm NB as per schedule 10S, ANSI B-36.10 OR Demineralised Water: Carbon Steel (inside rubber lined) | We understand that DM water piping is CS Rubber lined as per datasheet of piping & valves for DM plant. | As there is contradiction in the datasheet & specification for the MOC of DM water piping. Hence we understand that the same as CSRL piping as per the specifications. | Bidder to consider the material of the DM water piping as indicated at “DATASHEET OF PIPING & VALVES DM PLANT” Section C1, SL. NO. 1.3 & 1.4 at page number 108 to 109 of 630 in technical specification. |
|  | SPECIFICATION NO: PE-TS-410-163-A001 VOLUME: II-B SECTION: C1 OR SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME III SECTION -VIII | 1.0 OR 4.14.02 | Pg 108 of 630 OR Pg 227 of 630 | DATASHEET OF PIPING & VALVES FOR DM PLANT CAST IRON BODY BUTTERFLY VALVES ST IRON BODY BUTTERFLY VALVES : i. Basic Design Code: All the Butterfly valves shall be of double flanged type of low leakage rate confirming to AWWA-C-504 class 150 (min.). OR TECHNICAL SPECIFICATION FOR PIPING, FITTINGS & VALVES Butterfly Valves (for river water / clarified water / filtered water / similar application) Butterfly valves shall be of double flanged or lugged wafer type of low leakage rate conforming to AWWA-C 504 class 150 (min.) or BS-5155 PN 10 / class 150 (minimum) | We understand that the butterfly valves will be as lugged wafer type, BS-5155 PN 10 (min.). Please clarify. | Please note that there is contradiction in the tender documents for type of butterfly valves as double flanged or lugged. Hence we understand that the same is lugged type as mentioned in Technical Specifications for piping, fittings & valves of VOLUME III-C SECTION –VIII. Please clarify.. | Bidder to note that the basic design code of all the butterfly valves shall be as indicated at “DATASHEET OF PIPING & VALVES DM PLANT” Section C1, SL. NO. 2.1 at page number 109 of 630 in technical specification. |
|  | SPECIFICATION NO: PE-TS-410-163-A001 VOLUME: II-B SECTION: C1 OR SPECIFICATION NO.: PE-TS-410-158-A001 VOLUME III SECTION -VIII | 1.0 OR 4.14.02 | Pg 108 of 630 OR Pg 227 of 630 | DATASHEET OF PIPING & VALVES FOR DM PLANT OR TECHNICAL SPECIFICATION FOR PIPING, FITTINGS & VALVES | We understand that bidder has to consider the type of valves for various services as per P&ID & MOC as per the Technical Specifications for Piping, Fittings & valves. Please clarify. | As there is contradiction in the type of valves for various services & MOC of the valves in datasheet & Technical Specifications. Hence we understand that have the bidder has to consider the same as mentioned in Technical Specifications for piping, fittings & valves of VOLUME III SECTION –VIII. Please clarify. | The type of valves shall be as indicated in the P&ID for DM plant. Bidder to please follow technical specification. |
|  | VOLUME : III-C SECTION-II OR SPECIFICATION NO.: PE-TS-410-163-A001 VOLUME: II-B SECTION: C1 | 2.38.00 & 2.39.00 OR 9.00.00 | Pg 141 of 630 OR Pg 141 of 630 | (PART-A): DEMINERALISATION SYSTEM SCOPE OF SUPPLY AND SERVICES All civil as well as structural design, construction and architectural works as addressed in General Specification and Design Criteria for Civil and Structural Work - Volume –VII / A, General Specification and Design Criteria for Architectural Work - Volume - VII / B & Technical Specification for Civil, Structural and Architectural Work – Volume- VII / C of this Bid Document. All equipment and accessories as addressed in Specifications for Ventilation and Air Conditioning System - Volume III-D of this Bid Document. OR EXCLUSIONS Air conditioning, ventilation &fire fighting facilities All civil works including foundation of equipment. However complete grouting for equipment, fixing and any concreting inside vessels and lining shall be in the scope of the bidder. Also civil works including operating / maintenance platforms and interconnection platforms (if any) with ladders / stairs & handrails, structural supports and hangers for pipes / cables / ducts, crane rails, all embedment’s and inserts with lugs including anchor fasteners, bolts etc., dressing of foundations, grouting of pockets and underpinning of base plates for equipment / structures and fixing supports, filling and finishing of openings in walls, floors, cladding, roof and trenches shall be in bidder’s scope | We understand that entire civil works & ventilation & air conditioning system & ventilation is excluded from bidder’s scope of supply. Please clarify. | As there is contradiction in the tender documents for the scope of civil & ventilation & air conditioning system. Hence we understand that the same is excluded from our scope as per Exclusions mentioned in SPECIFICATION NO.: PE-TS-410-163-A001 VOLUME: II-B SECTION: C1. The scope of Civil works will be as per Exclusions mentioned in SPECIFICATION NO.: PE-TS-410-163-A001 VOLUME: II-B SECTION: C1. Please confirm. | Bidder to note that the scope of these items shall be as indicated in Section C1 of technical specification. |
|  | VOLUME : III-E SECTION-IV | 1.00.00 | Pg 180 of 630 | LARGE DIAMETER LOW PRESSURE PIPING, VALVES AND FABRICATED TANKS The Large Diameter Piping to be fabricated and installed shall include the following pipe lines having sizes 450 mm NB and above: a) Circulating Water Piping b) Auxiliary Cooling Water Piping c) Raw Water Piping d) DM Closed Cooling Water Piping e) Cooling Tower Make-up Water Piping 1.02.00 The different steel storage tanks are : a) Demineralised Water make up tank. b) Potable Water Storage Tank. c) Service Water RCC Tank. d) Demineralised Water storage tanks e) Condensate Storage Tank f) Fire Water Storage Tanks | We understand that the following large diameter low pressure piping, valves & fabricated tanks are excluded from our scope of supply. Please clarify. | As per P&ID & datasheet the same is not in our scope of supply. Hence we understand that the same is excluded from our scope of supply. Please clarify. | Bidder to note that the scope of these items shall be as indicated in Section C1 of technical specification. |
|  | VOLUME : IIIF SECTION-I | 1.00.00 | Pg 260 of 630 | SUMP PUMPS, DRIVES AND ACCESSORIES Group-A Group-B Group-C Group-D | We understand that the following sump pumps are not in the scope of DM plant bidder. Please clarify. | As per datasheet of DM plant the following group pumps are not mentioned. Hence we understand that the following sump pumps are not in the scope of DM plant bidder. Please clarify. | Bidder to note that the scope of these items shall be as indicated in Section C1 of technical specification. |
|  | VOLUME : IIIB | 1.00.00 | Pg 323 of 630 | TECHNICAL SPECIFICATIONS FOR PLANT WATER SYSTEM GENERAL TECHNICAL REQUIREMENT PLANT WATER SYSTEM & POTABLE WATER PUMPS | We understand that the following is excluded the same from the scope of supply of DM plant bidder. Please clarify. | As per datasheet & P&ID of DM plant the same is not mentioned. Hence we understand that the following is excluded the same from the scope of supply of DM plant bidder. Please clarify. | Bidder to note that the scope of these items shall be as indicated in Section C1 of technical specification. |
|  | SECTION C3 | 7 | 127/630 | PLC Shall be Connected to DCS Through Serial Link with OPC Compliant For monitoring /Control. For Detailed ,Please Refer PLC Architecture Diagram | We understand that as Per PLC Architecture Diagram OFC Cable Between PLC to DCS Shall be in BHEL Scope. Please clarify. | As per PLC System Configuration diagram, our scope ends at Ethernet port of PLC located in PLC room. | Noted. |
|  | SECTION C3 | 12 | 127/630 | Supplied System Shall Provide Group Alarm to be Hard wired to plant DCS | We understand that any Hard wired Cable, Cable Trays, Supports, installation etc, between PLC/Instruments to DCS Shall be in BHEL/Owners Scope. Please clarify. | As per PLC System Configuration diagram, our scope ends at Ethernet port of PLC located in PLC room. | Group Alarm to be Hard wired from PLC to plant DCS shall be in BHEL scope. Bidder to please follow technical specification. |
|  | SECTION D1 | 6.02.00 | 145/630 | DM PLC shall be connected to the common BOP network for remote operation / monitoring from CCR. BOP network shall be interfaced with DDCMIS through soft links. | We understand that bidder will Supply only PLC, Any Cable, Trays, Supports, Installation Between PLC to DCS/DDCMIS /Master Clock/BOP Package shall be in BHEL/Owner Scope. If required Please Mention Distance to be considered. | As per PLC System Configuration diagram, our scope ends at Ethernet port of PLC located in PLC room. | Cabling between PLC & DCS shall be in BHEL scope. However, provision for Master clock signals/OFC in PLC shall be as per specification. |
|  | SECTION D1 | 4.02.00 | Pg 262 of 630 | 3 nos Capacitance Level Switches per sump & Local Control Panel for Sump Pump and also ON/OFF indication for sump pump shall be monitored at DCS | We understand that any Cable, Trays, Supports, Installation Between LCP to DCS Shall be in BHEL/Owners Scope. Please clarify. | As per PLC System Configuration diagram, our scope ends at Ethernet port of PLC located in PLC room. | Please follow technical specification. |
|  | SECTION D3 -1.00.0 General | 1.01.01 | 501/630 | There Shall be Redundant Bidirectional OPC Link between DDCMIS Network & Each Package PLC including PADO for Monitoring/Performance Activities | Please note that as per PLC Architecture Diagram OFC Cable Between PLC to DCS/DDCMIS Shall be in BHEL Scope, Kindly Confirm the Same. If required, please mention the distance to be considered. | As per PLC System Configuration diagram, our scope ends at Ethernet port of PLC located in PLC room. | Noted. |
|  | SECTION D3 |  | Pg 506 of 869 | PLC System Configuration | We understand that BHEL Scope Starts from Ethernet port of DM PLC How Ever Along With Cable, Cable trays, supports, installation, termination Shall Also be in BHEL Scope. This is For Better Scope Clarity. | We understand that BHEL Scope Starts from Ethernet port of DM PLC How Ever Along With Cable, Cable trays, supports, installation, termination Shall Also be in BHEL Scope. This is For Better Scope Clarity. | Noted. Bidder shall follow the specification. |
|  | SECTION D3 | 2.03.03 | 582/630 | DDCMIS Back-up Panel (referred as Unit Control Panel-UCP) shall also mount annunciation fascia (minimum 500 nos.) and the flame Monitoring cameras along with Other hardwired devices as decided during detail Engineering stage by Owner. Color coding shall also subject to Owner’s approval. | We understand that bidder shall supply only Backup Panel for DM PLC, Back-up Panel for DDCMIS Shall be in BHEL Scope. Kindly Confirm the same. | As the scope is only up to PLC the Back-up Panel for DDCMIS is not in our scope of supply. Please confirm. | Noted. Bidder shall supply only Backup Panel for DM PLC. |
|  | PE-TS-410-163-A001 |  | Pg 609 of 630 | CABLE BOQ | We understand that cable Supplied Shall be up to JB from Instruments/ Pneumatic Valves/MOV and as per bidders cable length not as per tender BOQ , But as per Specification Provided by BHEL/Owner Kindly Confirm | This is for better clarity | Cables of Bidder’s scope (as per electrical scope sheet) shall be in line with the specification as provided under “Cable BOQ”. However, quantity of cables shall be decided by bidder. |