Pre Bid Clarification Dated 22nd july 2015

for

1x 8000 MW tsgenco kothagudem TPS, stage –vii, paloncha, Specification No. PE-TS-410-163-A001

| Sr. No. | Volume | Section | Clause No. | Page No. | Specification Requirement | Clarification / Query | Reason for clarification / Query | BHEL Reply |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Volume - IIB | Section C1 | Datasheet A for DM plant | Page no. 87 and 143 of 630 | Resin type for SBA | It is written in Tender on Page 85 of 630 that “Type-I and have macro-porous styrene-divinyl benzene matrix with quaternary ammonium (minimum 95%) type functional group. (gel type with particle size 0.5 to 0.65 mm)” However on Pg 143, it is clearly mentioned to consider macro porous type resin. Kindly clarify as both statements is contradicting each other.(DCPL specification) Also as per corrigendum 03, your reply against this point (Sr. No. 8) is “The same shall be decided during detail engineering.” | This will have impact on the sizing of DM plant vessel, Height, Resin Volume, DG water storage tanks, Measuring tanks, Bulk Storage tanks, Shed height etc. So, please clarify whether we have to consider Gel type resin or Macro-porous resin for SBA Vessel. | Type of anion resin for Strongly Basic Anion Exchangers shall be Type-I and have macro-porous styrene-divinyl benezene matrix with quaternary ammonium (minimum 95%) type functional group. The same shall be suitable for counter current regeneration. |