## ANNEXURE -A
ANNEXURE-A
UNPRICED SCHEDULE
PROJECT: R & M of ESP Stage-II Package, Ramagundam STPS (3X500 MW)
Sl. No. | MATERIAL CODE | Boards | Rating | UNIT | Qty | Unit Ex-Works Price including P&F Charges | Total Ex-Works Price including P&F Charges | Freight % (in terms of Total Ex-Works Price including P&F Charges) | Freight Amount | Total Ex-Works Price including P&F Charges + Freight Amount | GST % | GST Amount | FOR Destination
1 | ELRAMACPJ11901 | 415V AHP NEW COMPRESSOR HOUSE PMCC | 1600A | EA | 1
2 | ELRAMACPJ119002 | 415V AHP NEW SILO MCC | 400A | EA | 1
3 | ELRAMACPJ11903 | MANDATORY SPARES -ANNEXURE-D |  | LOT | 1
4 | ELRAMACPJ11904 | COMMISSIONING SPARES-ANNEXURE-E |  | LOT | 1
5 | ELRAMACPJ11905 | TOOLS & TACKLES -ANNEXURE-F |  | LOT | 1
6 | ELRAMACPJ11906 | TRAINING CHARGES FOR TRAINING WORKSHOP AT SITE FOR SWITCHGEAR & NUMERICAL RELAY-ANNEXURE-G |  | LOT | 1
7 | ELRAMACPJ11907 | COMMISSIONING CHARGE FOR NUMERICAL RELAY-ANNEXURE-H |  | LOT | 1
8 | ELRAMACPJ11908 | CHARGES FOR SUPERVISION OF COMMISSIONING FOR LT SWITCHGEAR-ANNEXURE-I |  | LOT | 1
9 | ELRAMACPJ11909 | SITE MODIFICATION CHARGES- ANNEXURE-J |  | LOT | 1
10 | ELRAMACPJ11910 | SITE MODIFICATION MATERIAL @1 % OF TOTAL EXWORKS FOR SL NO 1 TO 2 |  | LOT | 1
TOTAL (1 to 10), IN FIGURES
TOTAL (1 to 10), IN WORDS
NOTES:
1. SUMMATION OF ALL UNIT RATES OF MODULES SHALL BE EQUIVALENT TO TOTAL BOARD COST QUOTED, VARIANCE OF +/- 5% IS ACCEPTABLE. BEYOND 5% OFFER WILL NOT BE CONSIDER AS VALID OFFER. IN UNIT ADDITION-DELETION PRICES, PRICES QUOTED FOR COMPONENTS SHALL BE AS PER LIST PRICE OF CONCERNED MANUFACTURES. IF ANY ABNORMAL PRICES ON HIGHER SIDE OBSERVED OFFER MAY BE REJECTED.
2. ALL LT PCC/ MCC/ DBs SHALL BE SUPPLIED ALONGWITH THE INTEGRAL BASE FRAMES, FOUNDATION BOLTS, CABLE GLANDS & LUGS AND TOOLS & TACKLES AS MENTIONED IN DIFFERENT SECTIONS. ALL FIXING NUTS & BOLTS TOGETHER WITH FOUNDATION BOLTS SHALL ALSO BE SUPPLIED.
3. ITEM WISE PRICES WITH DESCRIPTION AND RATING OF EACH ITEM COMPLYING TO LIST FURNISHED IN THE SCHEDULE OF UNIT PRICES SHALL BE FURNISHED IN SCHEDULE OF UNIT PRICE.
4. FOR DETAILED BOARD WISE BOM, REFER ANNEXURE-B1-B2.
5. FOR DETAILED MODULE WISE BOM, REFER ANNEXURE-C.
6.ADDITION/DELETION OF QUANTITIES SHALL BE APPLICABLE AT THE QUOTED PRICE.THE UNIT RATE OF SUPPLY OF ALL EQUIPMENTS & SERVICES QUOTED BY THE BIDDER SHALL BE FIRM FOR A VARIATION OF QUANTITIES , WHICH MAY BE TO THE EXTENT OF ±30% OF THE TOTAL CONTRACT VALUE DERIVED ON THE BASIS OF ORDERED QUANTITY. SUM OF INDIVIDUAL MODULE SHALL EQUAL TO BOARD PRICE.
a. COMPLETE DIMENSIONS OF ALL THE BOARDS INCLUDING NO OF ACB, MCC. GA DRAWING SHALL BE DULY SUBMITTED FOR ALL BOARDS.
b. DIMENSIONS OF EACH TYPE OF PANEL.
c. MODULE SIZE OF EACH TYPE OF FEEDER.
d. MINIMUM CLEARANCES REQUIRED ON ALL SIDES FOR EACH TYPE OF PANEL.
e. NO. of VERTICAL (including PCC, MCC etc.) of EACH PANLES TO BE GIVEN, ELSE YOUR OFFER WILL BE REJECTED..
7. DOUBLE COMPRESSION, NICKLE PLATED BRASS CABLE GLANDS & HEAVY DUTY LUGS OF NTPC APPROVED MAKE FOR EXTERNAL POWER, CONTROL & EARTHING CONNECTIONS AT SUPPLIED EQUIPMENT END AND FOUNDATION BOLT ARE IN THE SCOPE OF BIDDER. BIDDER TO QUOTE ALL EQUIPMENT WITH CABLE GLANDS, LUGS AND FOUNDATION BOLTS.
8. EACH CABLE ALLEY SHALL BE PROVIDED WITH SPACE HEATER & ILLUMINATION CIRCUIT ALONG WITH PLUG,SOCKET & DOOR SWITCH.

## ANNEXURE-B1
ANNEXURE-B1
Name of the Board: 415V AHP COMPRESSOR HOUSE PMCC
TYPE OF CONNECTION: TOP/SIDE BUSDUCT ENTRY
DOUBLE FRONT D/O TYPE
FEEDER TYPE | RATING | TOTAL FEEDER | Unit Ex-Works Price including P&F Charges | Total Ex-Works Price including P&F Charges | Freight % (in terms of Total Ex-Works Price including P&F Charges) | Freight Amount | Total Ex-Works Price including P&F Charges + Freight Amount | GST % | GST Amount | FOR Destination
E3 | 16A | 14
E3 | 32A | 10
E3 | 63A | 6
E3 | 250A | 2
E3 | 400A | 3
EA3 | 7.5KW | 9
DK2 | 15KW | 8
DK21 | 45KW | 4
DK21 | 55KW | 3
BUS PT - G1 | 50VA | 2
CS | 2KVA | 2
DAET IC | 1600A | 2
DAET BC | 1600A | 1
ACB I/C PANELS | 1600A | 2
ACB B/C PANEL | 1600A | 1
MCC (DFDO) | 1600A | As req.
DUMMY PANEL | 1600A | 1
ETHERNET SWITCH |  | 1
TOTAL

## ANNEXURE-B2
ANNEXURE-B2
Name of the Board: 415V AHP SILO
TYPE OF CONNECTION: CABLE ENTRY BOTTOM
DOUBLE FRONT D/O TYPE
FEEDER TYPE | RATING | TOTAL FEEDER | Unit Ex-Works Price including P&F Charges | Total Ex-Works Price including P&F Charges | Freight % (in terms of Total Ex-Works Price including P&F Charges) | Freight Amount | Total Ex-Works Price including P&F Charges + Freight Amount | GST % | GST Amount | FOR Destination
E3 | 16A | 9
E3 | 32A | 8
E3 | 63A | 1
E3 | 250A | 2
DN1 | 0.37KW | 3
EA3 | 10.5KW | 4
DK2 | 1.5KW | 2
DK2 | 18.5KW | 3
DK2 | 22KW | 2
DK2 | 3.7KW | 3
BUS PT - G1 | 50VA | 2
CS | 2KVA | 2
EM3 IC | 400A | 2
EM3 BC | 400A | 1
MCC (DFDO) | 400A | As req.
TOTAL

## ANNEXURE-C
ANNEXURE-C
MODULE WISE BOM
SL NO | MODULE TYPE | ITEM DESCRIPTION | QTY. | Unit Ex-Works Price including P&F Charges | Total Ex-Works Price including P&F Charges | Freight % (in terms of Total Ex-Works Price including P&F Charges) | Freight Amount | Total Ex-Works Price including P&F Charges + Freight Amount | GST % | GST Amount | FOR Destination
1 | DAET (I/C) | PMCC INCOMER OF 1600A, 2500A, 3000A, 3200A, 4000A SHALL COMPRISE OF:
|  | ACB TP, ELECTRICALLY OPERATED D/O TYPE, WITHOUT RELEASES, CONTROL SUPPLY VOLTAGE 220V DC,4NO + 4NC CONTACTS OF POSITION/ CELL SWITCH. SPRING CHARGE LIMIT SWITCH WITH minimum 2NO + 2NC contacts. | 1
|  | CONTROL FUSE 6A | 15
|  | CONTROL FUSE 16A | 4
|  | FUSE BASE 32A | 19
|  | Indicating Lamp | 5
|  | CURRENT TRANSFORMER (PROTECTION) 10VA,CL-5P20 | 3
|  | CURRENT TRANSFORMER (PROTECTION) with VDR 10VA,CL-PS | 3
|  | POTENTIAL TRANSFORMER -CAST RESIN, OVER VOLTAGE FACTOR 1.2 CONT./1.5 FOR 30 SEC . 415/110,50 VA CL-0.5 INSL CL-E | 1
|  | NEUTRAL LINK 32A | 1
|  | CONTROL TERMINALS(FIXED) | As required
|  | CT SHORTING TERMINAL-STUD TYPE | As required
|  | POWER TERMINAL | As required
|  | DOUBLE POLE ON/OFF SWITCH-16 A,220 V DC | 2
|  | 2POLE 2POSI SELECTOR SWITCH KEY LOCKABLE-10A, 220VDC | 1
|  | NUMERICAL RELAY WITH COMMUNICATION FACILITY AS PER IEC-61850 FOR FOLLOWING FUNCTIONS: • SHORT CIRCUIT PROTECTION (51) • EARTH FAULT PROTECTION (51N) • OVER LOAD PROTERCTION • RESTRICTED EARTRH FAULT PROTECTION • RESIDUAL EARTH FAULT PROTECTION • TRIP CIRCUIT SUPERVISION (95) • CIRCUIT BREAKER MONITORING • PT FUSE FAILURE • ENERGY METERING • CURRENT, VOLTAGE & FREQUENCY MEASURENMENT • SYNCHRONIZING FEATURE • No of DI/DO SHALL BE AS PER SCHEME REQUIREMNET • ALL THE BINARY INPUTS SHALL BE CAPABLE OF TAKING THE 220V DC ,HOWEVER THE THERSHOLD VALUE FOR BINARY INPUT SHALL BE 18V DC (+/- 5%) | 1
|  | INTERPOSING RELAY REM302/EQVT. WITH BUILT IN LED, TEST KNOB & FREEWHEELING DIODE | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
2 | DAE (I/C) | MCC INCOMER OF 400A, 630A, 800A, 1000A, 1250A, 1600A SHALL COMPRISE OF:
|  | ACB TP, ELECTRICALLY OPERATED D/O TYPE, WITHOUT RELEASES, CONTROL SUPPLY VOLTAGE 220V DC,4NO + 4NC CONTACTS OF POSITION/ CELL SWITCH. SPRING CHARGE LIMIT SWITCH WITH minimum 2NO + 2NC contacts. | 1
|  | CONTROL FUSE 6A | 15
|  | CONTROL FUSE 16A | 4
|  | FUSE BASE 32A | 19
|  | Indicating Lamp | 5
|  | CURRENT TRANSFORMER (PROTECTION) 10VA,CL-5P20 | 3
|  | POTENTIAL TRANSFORMER -CAST RESIN, OVER VOLTAGE FACTOR 1.2 CONT./1.5 FOR 30 SEC . 415/110,50 VA CL-0.5 INSL CL-E | 1
|  | NEUTRAL LINK 32A | 1
|  | CONTROL TERMINALS(FIXED) | As required
|  | CT SHORTING TERMINAL-STUD TYPE | As required
|  | POWER TERMINAL | As required
|  | DOUBLE POLE ON/OFF SWITCH-16 A,220 V DC | 2
|  | 2POLE 2POSI SELECTOR SWITCH KEY LOCKABLE-10A, 220VDC | 1
|  | NUMERICAL RELAY WITH COMMUNICATION FACILITY AS PER IEC-61850 FOR FOLLOWING FUNCTIONS: • SHORT CIRCUIT PROTECTION (51) • EARTH FAULT PROTECTION (51N) • OVER LOAD PROTERCTION • RESIDUAL EARTH FAULT PROTECTION • TRIP CIRCUIT SUPERVISION (95) • CIRCUIT BREAKER MONITORING • PT FUSE FAILURE • ENERGY METERING • CURRENT, VOLTAGE & FREQUENCY MEASURENMENT • SYNCHRONIZING FEATURE • No of DI/DO SHALL BE AS PER SCHEME REQUIREMNET • ALL THE BINARY INPUTS SHALL BE CAPABLE OF TAKING THE 220V DC ,HOWEVER THE THERSHOLD VALUE FOR BINARY INPUT SHALL BE 18V DC (+/- 5%) | 1
|  | INTERPOSING RELAY REM302/EQVT. WITH BUILT IN LED, TEST KNOB & FREEWHEELING DIODE | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
3 | DAET/DAE (B/C) | PMCC/MCC BUSCOUPLER OF 400A, 630A, 800A, 1000A, 1250A, 1600A, 2500A, 3000A, 3200A,4000A SHALL COMPRISE OF:
|  | ACB TP, ELECTRICALLY OPERATED D/O TYPE, WITHOUT RELEASES, CONTROL SUPPLY VOLTAGE 220V DC | 1
|  | CONTROL FUSE 6A | 9
|  | CONTROL FUSE 16A | 6
|  | FUSE BASE 32A | 15
|  | AUXILIARY CONTACTOR 2NO+2NC 220VDC | 1
|  | BREAKER CONTACT MULTIPLICATION RELAY TYPE VAJC 11 OR EQVT | 1
|  | Indicating Lamp | 2
|  | CURRENT TRANSFORMER (PROTECTION) 10VA,CL-5P20 | 3
|  | NEUTRAL LINK 32A | 1
|  | CONTROL TERMINALS(FIXED) | As required
|  | CT SHORTING TERMINAL-STUD TYPE | As required
|  | POWER TERMINAL | As required
|  | DOUBLE POLE ON/OFF SWITCH-16 A,220 V DC | 5
|  | 2POLE 2POSI SELECTOR SWITCH KEY LOCKABLE-10A, 220VDC | 1
|  | NUMERICAL RELAY WITH COMMUNICATION FACILITY AS PER IEC-61850 FOR FOLLOWING FUNCTIONS: • SHORT CIRCUIT PROTECTION (51) • EARTH FAULT PROTECTION (51N) • OVER LOAD PROTERCTION • RESTRICTED EARTRH FAULT PROTECTION • RESIDUAL EARTH FAULT PROTECTION • TRIP CIRCUIT SUPERVISION (95) • CIRCUIT BREAKER MONITORING • PT FUSE FAILURE • ENERGY METERING • CURRENT, VOLTAGE & FREQUENCY MEASURENMENT • SYNCHRONIZING FEATURE • No of DI/DO SHALL BE AS PER SCHEME REQUIREMNET • ALL THE BINARY INPUTS SHALL BE CAPABLE OF TAKING THE 220V DC ,HOWEVER THE THERSHOLD VALUE FOR BINARY INPUT SHALL BE 18V DC (+/- 5%) | 1
|  | INTERPOSING RELAY REM302/EQVT. WITH BUILT IN LED, TEST KNOB & FREEWHEELING DIODE | 2
|  | DC SOURCE SLECTION SWITCH | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
4 | DAEG(-I/C) | EMERGENCY MCC INCOMER OF 800A, 1000A, 1250A, 1600A, 2000A, 2500A SHALL COMPRISE OF:
|  | ACB TP, ELECTRICALLY OPERATED D/O TYPE, WITHOUT RELEASES, CONTROL SUPPLY VOLTAGE 220V DC,4NO + 4NC CONTACTS OF POSITION/ CELL SWITCH. SPRING CHARGE LIMIT SWITCH WITH minimum 2NO + 2NC contacts. | 1
|  | CONTROL FUSE 6A | 15
|  | CONTROL FUSE 16A | 4
|  | FUSE BASE 32A | 19
|  | Indicating Lamp | 5
|  | CURRENT TRANSFORMER (PROTECTION) 10VA,CL-5P20 | 3
|  | CURRENT TRANSFORMER (PROTECTION) with VDR 10VA,CL-PS | 3
|  | POTENTIAL TRANSFORMER -CAST RESIN, OVER VOLTAGE FACTOR 1.2 CONT./1.5 FOR 30 SEC . 415/110,50 VA CL-0.5 INSL CL-E | 1
|  | NEUTRAL LINK 32A | 1
|  | CONTROL TERMINALS(FIXED) | As required
|  | CT SHORTING TERMINAL-STUD TYPE | As required
|  | POWER TERMINAL | As required
|  | DOUBLE POLE ON/OFF SWITCH-16 A,220 V DC | 2
|  | 2POLE 2POSI SELECTOR SWITCH KEY LOCKABLE-10A, 220VDC | 1
|  | NUMERICAL RELAY WITH COMMUNICATION FACILITY AS PER IEC-61850 FOR FOLLOWING FUNCTIONS: • SHORT CIRCUIT PROTECTION (51) • EARTH FAULT PROTECTION (51N) • OVER LOAD PROTERCTION • RESTRICTED EARTRH FAULT PROTECTION • RESIDUAL EARTH FAULT PROTECTION • TRIP CIRCUIT SUPERVISION (95) • CIRCUIT BREAKER MONITORING • PT FUSE FAILURE • ENERGY METERING • CURRENT, VOLTAGE & FREQUENCY MEASURENMENT • SYNCHRONIZING FEATURE • No of DI/DO SHALL BE AS PER SCHEME REQUIREMNET • ALL THE BINARY INPUTS SHALL BE CAPABLE OF TAKING THE 220V DC ,HOWEVER THE THERSHOLD VALUE FOR BINARY INPUT SHALL BE 18V DC (+/- 5%) • DIFFERENTIAL PROTECTION (HIGH IMPEDANCE) • REVERSE POWER PROTECTION • DG NEUTRAL DISPLACEMENT • DG MONITORING | 1
|  | INTERPOSING RELAY REM302/EQVT. WITH BUILT IN LED, TEST KNOB & FREEWHEELING DIODE | 2
Materials Cost
Integration Cost
Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. )
TOTAL
5 | DAE/DAE-TIE (O/G) | OUTGOING BREAKER FEEDER OF 630A, 800A, 1000A, 1250A, 1600A, 2500A SHALL COMPRISE OF:
|  | ACB TP, ELECTRICALLY OPERATED D/O TYPE, WITHOUT RELEASES, CONTROL SUPPLY VOLTAGE 220V DC,4NO + 4NC CONTACTS OF POSITION/ CELL SWITCH. SPRING CHARGE LIMIT SWITCH WITH minimum 2NO + 2NC contacts. | 1
|  | CONTROL FUSE 6A | 8
|  | CONTROL FUSE 16A | 2
|  | FUSE BASE 32A | 10
|  | Indicating Lamp | 2
|  | CURRENT TRANSFORMER (PROTECTION) 10VA,CL-5P20 | 3
|  | NEUTRAL LINK 32A | 1
|  | CONTROL TERMINALS(FIXED) | As required
|  | CT SHORTING TERMINAL-STUD TYPE | As required
|  | POWER TERMINAL | As required
|  | DOUBLE POLE ON/OFF SWITCH-16 A,220 V DC | 1
|  | 2POLE 2POSI SELECTOR SWITCH KEY LOCKABLE-10A, 220VDC | 1
|  | NUMERICAL RELAY WITH COMMUNICATION FACILITY AS PER IEC-61850 FOR FOLLOWING FUNCTIONS: • SHORT CIRCUIT PROTECTION (51) • EARTH FAULT PROTECTION (51N) • OVER LOAD PROTERCTION • RESIDUAL EARTH FAULT PROTECTION • TRIP CIRCUIT SUPERVISION (95) • CIRCUIT BREAKER MONITORING • PT FUSE FAILURE • ENERGY METERING • CURRENT, VOLTAGE & FREQUENCY MEASURENMENT • SYNCHRONIZING FEATURE • No of DI/DO SHALL BE AS PER SCHEME REQUIREMNET • ALL THE BINARY INPUTS SHALL BE CAPABLE OF TAKING THE 220V DC ,HOWEVER THE THERSHOLD VALUE FOR BINARY INPUT SHALL BE 18V DC (+/- 5%) | 1
|  | INTERPOSING RELAY REM302/EQVT. WITH BUILT IN LED, TEST KNOB & FREEWHEELING DIODE | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
6 | DM /PM | BREAKER CONTROLLED MOTOR ABOVE 110KW & & ABOVE SHALL COMPRISE OF:
|  | ACB TP, ELECTRICALLY OPERATED D/O TYPE, WITHOUT RELEASES, CONTROL SUPPLY VOLTAGE 220V DC,4NO + 4NC CONTACTS OF POSITION/ CELL SWITCH. SPRING CHARGE LIMIT SWITCH WITH minimum 2NO + 2NC contacts. | 1
|  | CONTROL FUSE 6A | 9
|  | CONTROL FUSE 16A | 2
|  | FUSE BASE 32A | 11
|  | Indicating Lamp | 2
|  | CURRENT TRANSFORMER (METERING) 10VA, CL-1 | 1
|  | CURRENT TRANSFORMER (PROTECTION) 10VA,CL-5P20 | 3
|  | CURRENT TRANSDUCER (DC),4-20mA, DUAL O/P,AUX.-220V DC | 1
|  | NEUTRAL LINK 32A | 1
|  | CONTROL TERMINALS(FIXED) | As required
|  | CT SHORTING TERMINAL-STUD TYPE | As required
|  | POWER TERMINAL | As required
|  | SP ON/OFF SWITCH FOR MOTOR SPACE HTR. OF BREAKER MOTOR FDR-12A, 240VAC | 1
|  | DOUBLE POLE ON/OFF SWITCH-16 A,220 V DC | 1
|  | 2POLE 2POSI SELECTOR SWITCH KEY LOCKABLE-10A, 220VDC | 1
|  | NUMERICAL RELAY WITH COMMUNICATION FACILITY AS PER IEC-61850 FOR FOLLOWING FUNCTIONS: • SHORT CIRCUIT PROTECTION (51) • EARTH FAULT PROTECTION (51N) • OVER LOAD PROTERCTION UNDER VOLTAGE • EARTH FAULT PROTECTION • TRIP CIRCUIT SUPERVISION (95) • CIRCUIT BREAKER MONITORING • PT FUSE FAILURE • ENERGY METERING • CURRENT, VOLTAGE & FREQUENCY MEASURENMENT • LOCKED ROTOR PROTECTION CURRENT UNBALANCE PROTECTION • No of DI/DO SHALL BE AS PER SCHEME REQUIREMNET • ALL THE BINARY INPUTS SHALL BE CAPABLE OF TAKING THE 220V DC ,HOWEVER THE THERSHOLD VALUE FOR BINARY INPUT SHALL BE 18V DC (+/- 5%) •NEGATIVE SEQUENCE PROTECTION •RESTART INHIBIT PROTECTION | 1
|  | INTERPOSING RELAY REM302/EQVT. WITH BUILT IN LED, TEST KNOB & FREEWHEELING DIODE | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
7 | G1 | BUS PT MODULE FOR PCC / PMCC SHALL COMPRISE OF:
|  | CONTROL FUSE-6A | 7
|  | FUSE BASE-32A | 7
|  | POTENTIAL TRANSFORMER -415/ROOT3 /110/ROOT3, 50 VA CL-0.5 INSL CL-E | 3
|  | NEUTRAL LINK-32A | 1
|  | CONTROL TERMINALS(FIXED) | As required
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
8 | G2 | BUS PT MODULE FOR DG PCC SHALL COMPRISE OF:
|  | CONTROL FUSE-6A | 7
|  | FUSE BASE-32A | 7
|  | POTENTIAL TRANSFORMER -415/ROOT3 /110/ROOT3, 50 VA CL-0.5 INSL CL-E | 3
|  | NEUTRAL LINK-32A | 1
|  | CONTROL TERMINALS(FIXED) | As required
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
9 | VM | BUS PT MODULE FOR MCC/ACDB SHALL COMPRISE OF:
|  | CONTROL FUSE-6A | 3
|  | FUSE BASE-32A | 3
|  | AUX. CONTACTOR 2NO+2NC CV. 415 V AC | 1
|  | VOLTMETER (AC),96 X 96 mm2, SCALE-90, CL-1.5,0-500V DIRECT | 1
|  | VOLTAGE TRANSDUCER (AC),4-20 m A DUAL O/P AUX. 220 V DC,0-500/4-20mA, 415V DIRECT | 1
|  | VOLTMETER SELECTOR SWITCH-12 A,415 V AC | 1
|  | RECTIFIER (AC TO DC),I/P-240V AC, O/P-220VDC | 1
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
10 | CS | EACH CONTROL SUPPLY OUTGOING SHALL COMPRISE OF:
|  | CONTROL FUSE-6A | 4
|  | CONTROL FUSE-25A | 4
|  | FUSE BASE-32A | 8
|  | AUX. CONTACTOR , 2NO+2NC,CV. 110 V AC | 4
|  | NEUTRAL LINK-32A | 6
|  | CONTROL TERMINALS(FIXED) | As required
|  | POWER TERMINALS | As required
|  | CONTROL TRANSFORMER,DRY TYPE, CAST RESIN,415/110 V, 2KVA | 2
|  | 4POLE,2POSI, SELECTOR SWITCH FOR CONTROL TRF.-25A, 110V AC | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
11 | DB | 220V DC INCOMER FROM BATTERY SHALL COMPRISE OF:
|  | DC AMMETER WITH SHUNT AND CENTER ZERO | 1
12 | DC | 220V DC BUS COUPLER SHALL COMPRISE OF:
|  | DOUBLE POLE 250V DC SWITCH/CIRCUIT BREAKER WITH 2NO+2NC AUXILIARY CONTACTS | 1
13 | CH | 220V DC INCOMER OF DCDB FROM CHARGER SHALL COMPRISE OF:
|  | Double pole, 250 V DC fuse -switch unit | 1
|  | INDICATING LAMP | 2
|  | VOLTMETER | 1
|  | DC AMMETER WITH SHUNT | 1
|  | CURRENT TRANSDUCER | 1
14 | HD | 220V DC ISOLATING SWITCH/CIRCUIT BREAK MODULE SHALL COMPRISE OF:
|  | DOUBLE POLE 250V DC SWITCH ISOLATOR/CIRCUIT BREAKER WITH REQUIRED AUXILIARY CONTACTS | 1
15 | S | 220V DCDB BUS MODULE FOR METERING & PROTECTION SHALL COMPRISE OF:
|  | UNDERVOLTAGE (INSTANNANEOUS WITH SETTING OF 95% OF 240VDC. THE RESETTING OF RELAY SHOULD NOT BE MORE THAN 1.05) | 1
|  | OVERVOLTAGE(INSTANEOUS WHICH SHALL OPERATE AT 110% OF 240V DC. THE RESETTINGRATION SHOULD NOT BE LESS THAN .95) | 1
|  | EARTHFAULT (CAEM21 OR EQV.) | 1
|  | INDICATING LAMP | 2
|  | CONTROL FUSE-6A | 3
|  | FUSE BASE-32A | 3
|  | NEUTRAL LINK | 1
|  | DC VOLTAGE METER (0-300V) | 1
|  | VOLTMETER SELECTOR SWITCH | 1
|  | AUXILIARY CONTACTOR,2NO+2NC,CV 220AC | 1
|  | PUSH BUTTON- SPRING RETURN WITH 1NO+1NC AUX, CONTACT | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
16 | X | 220V DC OUTGOING FEEDER SHALL COMPRISE OF:
|  | DOUBLE POLE 250V DC FUSE SWITCH UNIT | 1
|  | HRC FUSES | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
17 | CC | ISOLATOR INCOMER WITH CONTACTOR UPTO 630A SHALL COMPRISE OF
|  | TRI POLE LOAD BREAK ISOLATING SWITCH | 2
|  | Power Fuse | 3
|  | Auxiliary Switch | 1
|  | INDICATING LAMP | 2
|  | CONTROL FUSE-6A | 5
|  | FUSE BASE-32A | 5
|  | SERVICE POSITION LIMIT SWITCH | 2
|  | TRIPLE POLE POWER CONTACTOR WITH COIL SUITABLE FOR 415V AC WITH 2NO+2NC AUX | 2
|  | AUXILIARY CONTACTOR 2NO+2NC ,CV 415V AC | 2
|  | TERMINAL BLOCKS | 30
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
18(a) | EM3 (I/C) | INCOMER MCCB FOR MCC / ACDB FOR RATING from 100A UPTO 630A
|  | CONTROL FUSE-6A | 1
|  | FUSE BASE-32A | 1
|  | MCCB TP MICROPROCESSOR BASED ADJ. O/L,S/C & E/F RELEASE | 1
|  | AUX. SWITCH FOR MCCB-2C/O | 2
|  | ALARM SWITCH FOR MCCB-1C/O | 1
|  | SHUNT TRIP COIL 220VAC | 1
|  | EXTENDED ROTORY HANDLE | 1
|  | INDICATION LAMP | 3
|  | NEUTRAL LINK 32A | 1
|  | NEUTRAL LINK AS PER MCCB RATING | 1
|  | CONTROL TERMINALS (DRAWOUT) | AS REQUIRED
|  | CT SHORTING TERMINAL-STUD TYPE | AS REQUIRED
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
18(b) | EM3 (I/C) | INCOMER SFU FOR MCC / ACDB FOR RATING below 100A
|  | CONTROL FUSE-6A | 1
|  | FUSE BASE-32A | 1
|  | SFU (3 POLE WITH AUX. CONTACT 1NO+1NC) | 1
|  | INDICATION LAMP | 3
|  | NEUTRAL LINK 32A | 1
|  | NEUTRAL LINK AS PER MCCB RATING | 1
|  | CONTROL TERMINALS (DRAWOUT) | AS REQUIRED
|  | CT SHORTING TERMINAL-STUD TYPE | AS REQUIRED
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
19(A) | EM3 (B/C) | BUSCOUPLER MCCB FOR MCC / ACDB FOR RATING UPTO 630A
|  | MCCB TP MICROPROCESSOR BASED ADJ. O/L,S/C & E/F RELEASE | 1
|  | EXTENDED ROTORY HANDLE | 1
|  | AUXILARY CONTACTOR | 2
|  | CONTROL FUSES-6A | 2
|  | FUSE BASE-32A | 2
|  | NEUTRAL LINK | 2
|  | INDICATING LAMP | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
19(B) | EM3 (B/C) | BUSCOUPLER SFU FOR MCC / ACDB FOR RATING below 100A
|  | SFU (3 POLE WITH AUX. CONTACT 1NO+1NC) | 1
|  | AUXILARY CONTACTOR | 2
|  | CONTROL FUSES-6A | 2
|  | FUSE BASE-32A | 2
|  | NEUTRAL LINK | 2
|  | INDICATING LAMP | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
20(A) | E/E3 | TPN AC OUTGOING MCCB OPERATED FEEDER FOR RATING 100A AND ABOVE
|  | MCCB TP MICROPROCESSOR BASED ADJ. O/L,S/C & E/F RELEASE | 1
|  | EXTENDED ROTORY HANDLE | 1
|  | NETURAL LINK EQUIVALENT TO POWER FUSE RATING | 1
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
20(B) | E/E3 | TPN AC OUTGOING SFU OPERATED FEEDER FOR RATING below 100A
|  | 3 POLES SFU | 1
|  | POWER FUSE | 3
|  | NETURAL LINK EQUIVALENT TO POWER FUSE RATING | 1
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
21(A) | E2 | DP AC OUTGOING MCCB OPERATED FEEDER FOR RATING 100A AND ABOVE
|  | MCCB TP MICROPROCESSOR BASED ADJ. O/L,S/C | 1
|  | EXTENDED ROTORY HANDLE | 1
|  | NETURAL LINK EQUIVALENT TO POWER FUSE RATING | 1
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
21(B) | E2 | DP AC OUTGOING SFU OPERATED FEEDER FOR RATING below 100A
|  | (DP)SWITCH FUSE UNIT | 1
|  | HRC FUSE (POWER) | 2
|  | NETURAL LINK EQUIVALENT TO POWER FUSE RATING | 1
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
22(A) | E1 | SP AC OUTGOING MCCB OPERATED FEEDER FOR RATING 100A AND ABOVE
|  | MCCB TP MICROPROCESSOR BASED ADJ. O/L,S/C | 1
|  | EXTENDED ROTORY HANDLE | 1
|  | NETURAL LINK EQUIVALENT TO POWER FUSE RATING | 1
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
22(B) | E1 | SP AC OUTGOING SFU OPERATED FEEDER FOR RATING below 100A
|  | (TP)SWITCH FUSE UNIT | 1
|  | HRC FUSE (POWER) | 1
|  | NETURAL LINK EQUIVALENT TO POWER FUSE RATING | 1
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
23 | DK2/PK2/ AK2 | UNIDIRECTIONAL MOTOR FEEDER BELOW 30KW (AU/BU/CU CONTROLLED FROM ATRS/DDCMIS/PLC SHALL COMPRISE OF:
|  | (TP)SWITCH FUSE UNIT | 1
|  | AUX. CONTACT FOR SFU (1NO+1NC) | 1
|  | HRC FUSE (POWER) | 3
|  | CONTROL FUSE-6A | 1
|  | FUSE BASE-32A | 1
|  | POWER CONTACTOR(AC) WITH 1NO AUX CONTACT COIL VOLTAGE 110V AC | 1
|  | AUX. CONTACTOR,2N0+2NC, CV. 110 V AC | 2
|  | ADD ON AUX. CONTACTOR BLOCK 2NO+2NC | 1
|  | OVERLOAD RELAY,BUILT IN SPPR FEATURE 1NO+1NC AUX. & INDEPENDENT MOUNTING TYPE | 1
|  | MOUNTING KIT FOR O/L RELAY | 1
|  | RESET CORD ACTUATOR | 1
|  | Indication lamp | 3
|  | NEUTRAL LINK-32A | 1
|  | CONTROL TERMINALS (DRAWOUT) | 30
|  | COUPLING RELAY WITH BUILT IN DIODE | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
24 | EA1 | 1-PHASE SFU CONTACTOR CONTROLLED FEEDER SHALL COMPRISE OF:
|  | (TP)SWITCH FUSE UNIT | 1
|  | AUX. CONTACT FOR SFU (1NO+1NC) | 1
|  | HRC FUSE (POWER) | 2
|  | CONTROL FUSE-6A | 1
|  | FUSE BASE-32A | 1
|  | 2P POWER CONTACTOR(AC) WITH 1NO AUX CONTACT COIL VOLTAGE 110V AC | 1
|  | AUX. CONTACTOR,2N0+2NC, CV. 110 V AC | 2
|  | ADD ON AUX. CONTACTOR BLOCK 2NO+2NC | 1
|  | Indication lamp | 3
|  | NEUTRAL LINK-32A | 1
|  | CONTROL TERMINALS (DRAWOUT) | 30
|  | COUPLING RELAY WITH BUILT IN DIODE | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
25 | EA3 | 3-PHASE SFU CONTACTOR CONTROLLED FEEDER SHALL COMPRISE OF:
|  | (TP)SWITCH FUSE UNIT | 1
|  | AUX. CONTACT FOR SFU (1NO+1NC) | 1
|  | HRC FUSE (POWER) | 3
|  | CONTROL FUSE-6A | 1
|  | FUSE BASE-32A | 1
|  | 3P POWER CONTACTOR(AC) WITH 1NO AUX CONTACT COIL VOLTAGE 110V AC | 1
|  | AUX. CONTACTOR,2N0+2NC, CV. 110 V AC | 2
|  | ADD ON AUX. CONTACTOR BLOCK 2NO+2NC | 1
|  | Indication lamp | 3
|  | NEUTRAL LINK-32A | 1
|  | CONTROL TERMINALS (DRAWOUT) | As required
|  | COUPLING RELAY WITH BUILT IN DIODE | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
26 | DK21/PK21/ AK21 | UNIDIRECTIONAL MOTOR FEEDER 30KW & ABOVE UPTO 110KW CONTROLLED FROM DDCMIS/PLC/ATRS SHALL COMPRISE OF:
|  | (TP)SWITCH FUSE UNIT | 1
|  | AUX. CONTACT FOR SFU (1NO+1NC) | 1
|  | HRC FUSE (POWER) | 3
|  | CONTROL FUSE-6A | 2
|  | FUSE BASE-32A | 2
|  | POWER CONTACTOR(AC) WITH 1NO AUX CONTACT COIL VOLTAGE 110V AC | 1
|  | AUX. CONTACTOR,2NO+2NC CV. 110 V AC | 2
|  | ADD ON AUX. CONTACTOR BLOCK 2NO+2NC | 1
|  | OVERLOAD RELAY,BUILT IN SPPR FEATURE 1NO+1NC AUX. & INDEPENDENT MOUNTING TYPE | 1
|  | RESET CORD ACTUATOR | 1
|  | Indication lamp | 3
|  | CURRENT TRANSFORMER (METERING) 10VA, CL-1 | 1
|  | AMMETER CTSEC 1A (AC),96 X 96 mm2, SCALE-90, CL-1.5 | 1
|  | CURRENT TRANSDUCER (AC),4-20mA, DUAL O/P,AUX.-11OV AC | 1
|  | NEUTRAL LINK | 1
|  | CONTROL TERMINALS (DRAWOUT) | 50
|  | CT SHORTING TERMINAL-STUD TYPE | 18
|  | SP ON/OFF SWITCH FOR MOTOR SPACE HTR. OF MOTOR FDR.,10A, 240VAC | 1
|  | COUPLING RELAY WITH BUILT IN DIODE,24V DC 2C/O | 2
|  | One (1) Digital Energy Meter with Analog output of Current (4-20 mA) | 1
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
27 | DKE2** | UNIDIRECTIONAL MOTOR FEEDER (ESSENTIAL) BELOW 30KW CONTROLLED FROM DDCMIS/PLC/ ATRS SHALL COMPRISE OF:
|  | TRIPLE POLE SWITCH FUSE UNIT | 1
|  | AUX. CONTACT FOR SFU (1NO+1NC) | 1
|  | HRC FUSE (POWER) | 3
|  | TRIPLE POLE POWER CONTACTOR | 1
|  | THERMAL O/L RELAY OF SUITABLE RANGE | 1
|  | Mounting Kit | 1
|  | THERMAL O/L RELAY RESET PUSH BUTTON | 1
|  | INDICATING LAMP | 3
|  | CONTROL FUSE | 4
|  | Contorl Fuse base | 4
|  | NEUTRAL LINK | 2
|  | AUXILIARY CONTACTOR | 2
|  | CT FOR METERING | 1
|  | AMMETER | 1
|  | CURRENT TRANSDUCER (DUAL OUTPUT) | 1
|  | INTERPOSING RELAY RE302 OR EQVT | 2
|  | TIMER | 1
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
28 | DKE21** | UNIDIRECTIONAL MOTOR FEEDER (ESSENTIAL) 30KW & ABOVE UPTO 110KW CONTROLLED FROM ATRS/DDCMIS/PLC SHALL COMPRISE OF:
|  | 3P SFU | 1
|  | AUX. CONTACT FOR SFU (1NO+1NC) | 1
|  | HRC FUSE (POWER) | 3
|  | TRIPLE POLE POWER CONTACTOR | 1
|  | THERMAL O/L RELAY OF SUITABLE RANGE | 1
|  | THERMAL O/L RELAY RESET PUSH BUTTON | 1
|  | INDICATING LAMP | 3
|  | CONTROL FUSE | 8
|  | Contorl Fuse base | 8
|  | NEUTRAL LINK | 2
|  | AUXILIARY CONTACTOR | 2
|  | CT FOR METERING | 1
|  | AMMETER SELECTOR SWITCH | 1
|  | AMMETER | 1
|  | CURRENT TRANSDUCER (DUAL OUTPUT) | 1
|  | INTERPOSING RELAY RE302 OR EQVT | 2
|  | TIMER | 1
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
29 | K3 | UNIDIRECTIONAL MOTOR FEEDER BELOW 30KW CONTROLLED FROM LPBS SHALL COMPRISE OF:
|  | 3P SFU | 1
|  | AUX. CONTACT FOR SFU (1NO+1NC) | 1
|  | HRC FUSE (POWER) | 3
|  | TRIPLE POLE POWER CONTACTOR | 1
|  | THERMAL O/L RELAY OF SUITABLE RANGE | 1
|  | Mounting Kit | 1
|  | THERMAL O/L RELAY RESET PUSH BUTTON | 1
|  | INDICATING LAMP | 3
|  | AUXILIARY CONTACTOR | 1
|  | INTERPOSING RELAY RE302 OR EQVT | 2
|  | CONTROL FUSE | 1
|  | Control fuse base | 1
|  | NEUTRAL LINK | 1
|  | NO. OF TERMINALS | 25
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
30 | K31 | UNIDIRECTIONAL MOTOR FEEDER 30KW & ABOVE UPTO 110KW CONTROLLED FROM LPBS SHALL COMPRISE OF:
|  | 3P SFU | 1
|  | AUX. CONTACT FOR SFU (1NO+1NC) | 1
|  | HRC FUSE (POWER) | 3
|  | TRIPLE POLE POWER CONTACTOR | 1
|  | THERMAL O/L RELAY OF SUITABLE RANGE | 1
|  | THERMAL O/L RELAY RESET PUSH BUTTON | 1
|  | INDICATING LAMP | 3
|  | AUXILIARY CONTACTOR | 1
|  | AMMETER | 1
|  | INTERPOSING RELAY RE302 OR EQVT | 2
|  | CT FOR METERING | 1
|  | CONTROL FUSE | 1
|  | Control Fuse base | 1
|  | NEUTRAL LINK | 1
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
31 | DK2** | HEATER FEEDER BELOW 30KW (AU/BU/CU CONTROLLED FROM ATRS/DDCMIS/PLC SHALL COMPRISE OF:
|  | (TP)SWITCH FUSE UNIT | 1
|  | AUX. CONTACT FOR SFU (1NO+1NC) | 1
|  | HRC FUSE (POWER) | 3
|  | CONTROL FUSE-6A | 1
|  | FUSE BASE-32A | 1
|  | POWER CONTACTOR(AC) WITH 1NO AUX CONTACT COIL VOLTAGE 110V AC | 1
|  | AUX. CONTACTOR,2N0+2NC, CV. 110 V AC | 2
|  | ADD ON AUX. CONTACTOR BLOCK 2NO+2NC | 1
|  | Indication lamp | 3
|  | NEUTRAL LINK-32A | 1
|  | CONTROL TERMINALS (DRAWOUT) | 30
|  | COUPLING RELAY WITH BUILT IN DIODE | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
32 | DK21** | HEATER FEEDER 30KW & ABOVE UPTO 110KW CONTROLLED FROM DDCMIS/PLC/ATRS SHALL COMPRISE OF:
|  | (TP)SWITCH FUSE UNIT | 1
|  | AUX. CONTACT FOR SFU (1NO+1NC) | 1
|  | HRC FUSE (POWER) | 3
|  | CONTROL FUSE-6A | 2
|  | FUSE BASE-32A | 2
|  | POWER CONTACTOR(AC) WITH 1NO AUX CONTACT COIL VOLTAGE 110V AC | 1
|  | AUX. CONTACTOR,2NO+2NC CV. 110 V AC | 2
|  | ADD ON AUX. CONTACTOR BLOCK 2NO+2NC | 1
|  | Indication lamp | 3
|  | CURRENT TRANSFORMER (METERING) 10VA, CL-1 | 1
|  | AMMETER CTSEC 1A (AC),96 X 96 mm2, SCALE-90, CL-1.5 | 1
|  | CURRENT TRANSDUCER (AC),4-20mA, DUAL O/P,AUX.-11OV AC | 1
|  | NEUTRAL LINK | 1
|  | CONTROL TERMINALS (DRAWOUT) | 60
|  | CT SHORTING TERMINAL-STUD TYPE | 60
|  | SP ON/OFF SWITCH FOR MOTOR SPACE HTR. OF MOTOR FDR.,10A, 240VAC | 1
|  | COUPLING RELAY WITH BUILT IN DIODE,24V DC 2C/O | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
33 | DW | 220V DC SOLENOID VALVE FEEDER SHALL COMPRISE OF:
|  | DOUBLE POLE 250V DC ISOLATING SWITCH FUSE UNIT | 1
|  | HRC FUSE | 2
|  | 220V DC POWER CONTACTOR | 1
|  | AUXILIARY CONTACTOR | 1
|  | NEUTRAL LINK | 1
|  | DIODE WITH PEAK INVERSE VOLTAGE OF 440V | 1
|  | COUPLING RELAY | 1
|  | Control fuse | 2
|  | Control fuse base | 2
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
34 | DN1 | BIDIRECTIONAL MOTOR FEEDER
|  | (TP)SWITCH FUSE UNIT | 1
|  | AUX. CONTACT FOR SFU (1NO+1NC) | 1
|  | HRC FUSE (POWER) | 3
|  | TRIPLE POLE POWER CONTACTOR | 2
|  | THERMAL O/L RELAY OF SUITABLE RANGE | 1
|  | MOUNTING Kit | 1
|  | THERMAL O/L RELAY RESET PUSH BUTTON | 1
|  | INDICATING LAMP | 3
|  | CONTROL FUSE | 4
|  | Control fuse base | 4
|  | NEUTRAL LINK | 1
|  | AUXILIARY CONTACTOR | 2
|  | NO. OF TERMINALS (240V AC/24V DC) | 60
|  | INTREPOSING RELAY | 3
|  | TEST PUSH BUTTON | 1
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
35 | K1 | UNIDIRECTIONAL MOTOR FEEDER BELOW 30KW CONTROLLED FROM MCC SHALL COMPRISE OF:
|  | (TP)SWITCH FUSE UNIT | 1
|  | AUX. CONTACT FOR SFU (1NO+1NC) | 1
|  | HRC FUSE (POWER) | 3
|  | TRIPLE POLE POWER CONTACTOR | 1
|  | THERMAL O/L RELAY OF SUITABLE RANGE | 1
MOUNTING Kit
|  | THERMAL O/L RELAY RESET PUSH BUTTON | 1
|  | INDICATING LAMP | 3
|  | CONTROL FUSE | 1
|  | CONTROL FUSE BASE | 1
|  | NEUTRAL LINK | 1
|  | NO. OF TERMINALS | 30
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL
36 | K11 | UNIDIRECTIONAL MOTOR FEEDER RATED FROM 30KW to 110KW CONTROLLED FROM MCC SHALL COMPRISE OF:
|  | (TP)SWITCH FUSE UNIT | 1
|  | AUX. CONTACT FOR SFU (1NO+1NC) | 1
|  | HRC FUSE (POWER) | 3
|  | TRIPLE POLE POWER CONTACTOR | 1
|  | THERMAL O/L RELAY OF SUITABLE RANGE | 1
|  | THERMAL O/L RELAY RESET PUSH BUTTON | 1
|  | INDICATING LAMP | 3
|  | CURRENT TRANSFORMER (METERING) 10VA, CL-1 | 1
|  | AMMETER | 1
CURRENT TRANSDUCER (AC),4-20mA, DUAL O/P,AUX.-11OV AC
|  | CONTROL FUSE | 1
CONTROL FUSE base
|  | NEUTRAL LINK | 1
|  | NO. OF TERMINALS | 50
|  | Single Phase switch for motor Space Heater | 1
Materials Cost
|  | Integration Cost | 1
|  | Breakar Module Cost (Beakar Plat, Support, Paint & Class-C items wire, lugs, Cable gland etc. ) | 1
TOTAL

## ANNEXURE-D
ANNEXURE-D
Mandatory Spares
Item | Description | UNIT | QTY. | Unit Ex-Works Price including P&F Charges | Total Ex-Works Price including P&F Charges | Freight % (in terms of Total Ex-Works Price including P&F Charges) | Freight Amount | Total Ex-Works Price including P&F Charges + Freight Amount | GST % | GST Amount | FOR Destination
A.1 | Complete breaker of each rating | Nos. | 1
A.2 | Ammeter of each type, size & range | Nos. | 2
A.3 | Voltmeter of each type, size & rating | Nos | 2
A.4 | Relays of each type | Nos | 2
A.5 | Busbar support insulators | Nos. | 10
B.1 | Spring charging motors of each type & rating | Nos. | 3
B.2 | Aux. Contact set of each type & rating | Set | 6
B.3 | Limit switches of each type & rating | Nos | 10
B.4 | Arc Chutes of each type and rating | % | 10%
B.5 | Fixed Contact Sets of each type and rating | Set | 3
B.6 | Moving contact Sets of each type and rating | Set | 3
B.7 | Arcing Contacts of each type | Set | 3
B.8 | Charging spring of each type & rating | Nos | 2
B.9 | Current transformer of each type & ratio | Nos. | 3
B.10 | Closing coil of each type & rating | Nos | 6
B.11 | Trip coil of each type & rating | Nos | 6
B.12 | CT for Bimetal O/L relays of each type & rating | Nos. | 3
B.13 | Voltage transformer of each type & ratio | Nos | 3
B.14 | Control supply transformer of each type & rating | Nos. | 3
B.15(a) | Power Contactor of each type & rating | Nos. | 2
B.16 (b) | Coils for the above | Nos. | 2
B.17 | Air break switches & MCCB's of each type & rating | Nos. | 3
B.18 | DP air break switches(DC) of each type & rating | Nos. | 3
B.19 | Control & selector switches of each type & rating | Nos | 3
B.20 (a) | Control fuses (equally divided for all ratings) | Nos. | 50
B.20 (b) | Neutral links (equally divided for all ratings) | Nos. | 10
B.21 | Indicating lamps (equally divided for all types & ratings) | Nos. | 30
B.22 | Vertical busbar dropper support insulators | Nos. | 25
B.23 | Bus Duct Flexible & Connectors (both transformer and switchgear end)of each type & size (1 set for three phases) | Set | 1
B.24.a | Primary disconnect in MCC - Busbar end (Male/female contact) (equally divided for all ratings) | Nos. | 15
B.25.b | Secondary disconnect in MCC - Cable end (equally divided for all ratings) | Nos. | 15
B.26 | Push buttons of each type | Nos. | 10
B.27 | Power Fuses (Total 20% proportionately divide for all ratings)(min 3 Nos) | Nos. | 3
B.28 | Thermal Bimetal relays( Total 5%.proportionately divide for all ratings )(min 1 No) | Nos. | 1
B.29 | Current transducers of each type & rating | Nos. | 2
B.30 | Voltage transducers of each type & rating | Nos. | 2
B.31 | Busbar aluminium flat pieces of each type & rating | Mtrs | 12
B.32.36 | Busbar angles / formed pieces for breaker of each type & rating | Nos | 2
B.33.37 | Terminal blocks of each type & rating | Nos. | 12
TOTAL

## ANNEXURE_E
ANNEXURE-E
COMISSIONING SPARE
SL NO | DESCRIPTION | UNIT | QUANTITY | Unit Ex-Works Price including P&F Charges | Total Ex-Works Price including P&F Charges | Freight % (in terms of Total Ex-Works Price including P&F Charges) | Freight Amount | Total Ex-Works Price including P&F Charges + Freight Amount | GST % | GST Amount | FOR Destination
1 | Factory built assemblies (PCC/MCC/DB)
1.1 | Busbar supports (Horizontal) | 1 set of 3 ph | 1
1.2 | Primary isolating contacts (Bus side) of each rating | 1 set of 3 ph | 1
1.3 | Primary isolating contacts (Load side) of each rating | 1 set of 3 ph | 1
1.4 | Secondary isolating contacts of each rating | 1 set of 3 ph | 1
1.5 | Gaskets (each size) | Meter | 10
1.6 | Fixed terminal (one way) | Nos | 20
1.7 | Shrouds (for outgoing modules)(of each type) | Nos | 1
1.8 | Wire (for secondary wiring)
| 2.5mm2 | Meter | 50
| 1.5mm2 | Meter | 50
1.9 | Lugs (for secondary wiring) | Nos | 50
2 | Air circuit breaker (for each rating)
2.1 | Shunt trip coil | Nos | 1
2.2 | Spring charging motor (1 no for each rating) | Nos | 1
2.3 | Closing coil | Nos | 1
2.4 | Auxiliary switch | Nos | 1
3 | Isolating switch
3.1 | Main contact kiot for each rating | 1 set of 3 poles | 1
4 | Power Contactors
4.1 | contactor coil of each rating | Nos | 1
4.2 | contactor kit (main) for each rating | 1 set of 3 poles | 1
5 | Auxiliary conatctors
5.1 | Complete unit with 2NO+2NC contacts (1 no of each rating/ type) | Nos | 1
5.2 | contactor coils
a. | AC for each rating | set | 1
b. | DC for each rating | set | 1
6 | HRC fuse
6.1 | Fuse base (each rating) | Nos | 1
6.2 | Fuse link
a. | Upto 40A (assorted ratings) | Nos | 10
b. | 63A to 200A (assorted ratings) | Nos | 10
c. | 250A to 400A (assorted ratings) | Nos | 5
7 | Push Buttons
7.1 | Actuator contacts | Nos | 5
7.2 | Element | Nos | 5
8 | Indicating Lamps
8.1 | Complete unit | Nos | 10
8.2 | Lens (assorted ) | Nos | 10
9 | Others
9.1 | Selector & control switch (each type) | Nos | 1
9.2 | AC Voltmeter (0-500V) | Nos | 1
9.3 | DC Voltmeter (0-300V) | Nos | 1
TOTAL

## ANNEXURE-F
ANNEXURE-F
LIST OF TOOLS & TACKLES
S.No. | ITEM / COMPONENT | UNIT | QUANTITY | Unit Ex-Works Price including P&F Charges | Total Ex-Works Price including P&F Charges | Freight % (in terms of Total Ex-Works Price including P&F Charges) | Freight Amount | Total Ex-Works Price including P&F Charges + Freight Amount | GST % | GST Amount | FOR Destination
1 | ACB RACKING HANDLE | Nos | 2
2 | MODULE RACKING HANDLE | Nos | 2
3 | FUSE PULLERS | Nos | 2
4 | TROLLEY FOR ACB HANDLING | Nos | 1
TOTAL

## ANNEXURE-G
ANNEXURE-G
TRAINING CHARGES FOR TRAINING WORKSHOP AT SITE FOR SWITCHGEAR & NEMERICAL REALY
SL.NO. | DETAILS | UNIT | QUANTITY | Unit Ex-Works Price including P&F Charges | Total Ex-Works Price including P&F Charges | Freight % (in terms of Total Ex-Works Price including P&F Charges) | Freight Amount | Total Ex-Works Price including P&F Charges + Freight Amount | GST % | GST Amount | FOR Destination
1 | LUMP SUM ALL INCLUSIVE CHARGES PER VISIT FOR TRAINING ENGINEER (EXCEPT DAILY CHARGES) | VISITS | 1
2 | LUMP SUM ALL INCLUSIVE DAILY CHARGES FOR TRAINING ENGINEER FOR ONE NUMBER OF LT SWITCHGEAR WORKSHOP AND TRAINING FOR A BATCH OF 20 ENGINEERS AT SITE | DAYS | 2
3 | LUMP SUM ALL INCLUSIVE DAILY CHARGES FOR TRAINING ENGINEER FOR ONE NUMBER OF LT SWITCHGEAR WORKSHOP AND TRAINING FOR A BATCH OF 20 SUPERVISORS / TECHNICIANS AT SITE | DAYS | 2
4 | LUMP SUM ALL INCLUSIVE DAILY CHARGES FOR TRAINING ENGINEER FOR ONE NUMBER OF NUMERICAL RELAY WORKSHOP AND TRAINING FOR A BATCH OF 20 ENGINEERS AT SITE | DAYS | 2
TOTAL
NOTES:
1) AMOUNT PAYABLE FOR TRAINING ENGINEER PER VISIT TO SITE = VISIT CHARGES AS PER SL. NO. 1 ABOVE + (DAILY CHARGES AS PER SL. NO. 2 ABOVE X NO. OF DAYS AT SITE) (TO BE CERTIFIED BY BHEL SITE)+(DAILY CHARGES AS PER SL. NO. 3 ABOVE X NO. OF DAYS AT SITE) (TO BE CERTIFIED BY BHEL SITE)+(DAILY CHARGES AS PER SL. NO. 4 ABOVE X NO. OF DAYS AT SITE) (TO BE CERTIFIED BY BHEL SITE)

## ANNEXURE-H
ANNEXURE-H
COMMISSIONING CHARGES FOR NUMERICAL RELAYS AT SITE
SL.NO. | DETAILS | UNIT | QUANTITY | Unit Ex-Works Price including P&F Charges | Total Ex-Works Price including P&F Charges | Freight % (in terms of Total Ex-Works Price including P&F Charges) | Freight Amount | Total Ex-Works Price including P&F Charges + Freight Amount | GST % | GST Amount | FOR Destination
1 | LUMP SUM ALL INCLUSIVE CHARGES PER VISIT FOR SERVICE ENGINEER (EXCEPT DAILY CHARGES) | VISITS | 1
2 | LUMP SUM ALL INCLUSIVE PER NUMERICAL RELAY COMMISSIONING CHARGES | NOS | 3
TOTAL
NOTES:
1) AMOUNT PAYABLE FOR SERVICE ENGINEER PER VISIT TO SITE = VISIT CHARGES AS PER SL. NO. 1 ABOVE + (PER NUMERICAL RELAY COMMISSIONING CHARGES AS PER SL. NO. 2 ABOVE X NO. OF RELAYS) (TO BE CERTIFIED BY BHEL SITE)

## ANNEXURE-I
ANNEXURE-I
CHARGES FOR SUPERVISION OF COMMISSIONING FOR LT SWITCHGEAR
SL.NO. | DETAILS | UNIT | QUANTITY | Unit Ex-Works Price including P&F Charges | Total Ex-Works Price including P&F Charges | Freight % (in terms of Total Ex-Works Price including P&F Charges) | Freight Amount | Total Ex-Works Price including P&F Charges + Freight Amount | GST % | GST Amount | FOR Destination
1 | LUMP SUM ALL INCLUSIVE CHARGES PER VISIT FOR SERVICE ENGINEER (EXCEPT DAILY CHARGES) | VISITS | 1
2 | LUMP SUM ALL INCLUSIVE DAILY CHARGES FOR SERVICE ENGINEER | DAYS | 4
TOTAL
NOTES:
1) AMOUNT PAYABLE FOR SERVICE ENGINEER PER VISIT TO SITE = VISIT CHARGES AS PER SL. NO. 1 ABOVE + (DAILY CHARGES AS PER SL. NO. 2 ABOVE X NO. OF DAYS AT SITE) (TO BE CERTIFIED BY BHEL SITE)

## ANNEXURE-J
ANNEXURE-J
SITE MODIFICATION CHARGES
SL.NO. | DETAILS | UNIT | QUANTITY | Unit Ex-Works Price including P&F Charges | Total Ex-Works Price including P&F Charges | Freight % (in terms of Total Ex-Works Price including P&F Charges) | Freight Amount | Total Ex-Works Price including P&F Charges + Freight Amount | GST % | GST Amount | FOR Destination
1 | LUMP SUM ALL INCLUSIVE CHARGES PER VISIT FOR SKILLED TECHNICIAN (EXCEPT DAILY CHARGES) | VISITS | 1
2 | LUMP SUM ALL INCLUSIVE DAILY CHARGES FOR SKILLED TECHNICIAN | DAYS | 4
3 | LUMP SUM ALL INCLUSIVE CHARGES PER VISIT FOR SERVICE ENGINEER (EXCEPT DAILY CHARGES) | VISITS | 1
4 | LUMP SUM ALL INCLUSIVE DAILY CHARGES FOR SERVICE ENGINEER | DAYS | 4
TOTAL
NOTES:
1) AMOUNT PAYABLE FOR SKILLED TECHNICIAN PER VISIT TO SITE = VISIT CHARGES AS PER SL. NO. 1 ABOVE + (DAILY CHARGES AS PER SL. NO. 2 ABOVE X NO. OF DAYS AT SITE) (TO BE CERTIFIED BY BHEL SITE)
2) AMOUNT PAYABLE FOR SERVICE ENGINEER PER VISIT TO SITE = VISIT CHARGES AS PER SL. NO. 3 ABOVE + (DAILY CHARGES AS PER SL. NO. 4 ABOVE X NO. OF DAYS AT SITE) (TO BE CERTIFIED BY BHEL SITE)

## ANNEXURE-K
SL.NO. | ITEM DESCRIPTION | MODEL NO./ ITEM DESCRIPTION | UNIT PRICE (Rs.)
1 | INCOMING FEEDER UNIT
a) | ACB Incomer to PCC/PMCC from Trafo. - Module Type DAET (I/C)
630A
1000A
1600A
2000A
2500A
3000A
3500A
4000A
b) | ACB Incomer to MCC - Module Type DAE/ DAEN/ AE (I/C)
630A
800A
1000A
1600A
2500A
3200A
c) | MCCB Incomer for MCC / ACDB – Module Type EM3 (I/C)
200A – Fixed Type
125A – Fixed Type
200A – Fixed Type
250A – Fixed Type
400A – Fixed Type
630A – Fixed Type
125A – Drawout Type
200A – Drawout Type
200A – Drawout Type
250A – Drawout Type
400A – Drawout Type
630A – Drawout Type
d) | SFU Incomer for MCC / ACDB – Module Type E3 (I/C)
Upto 63A – Fixed Type
Upto 63A – Drawout Type
e) | 220V DCDB Incomer from charger - Module type CH (I/C)
150A – CH Fixed Type
200A – CH Fixed Type
400A – CH Fixed Type
630A – CH Fixed Type
800A – CH Fixed Type
1250A – CH Fixed Type
150A – CH Drawout Type
200A – CH Drawout Type
400A – CH Drawout Type
630A – CH Drawout Type
800A – CH Drawout Type
1250A – CH Drawout Type
f) | 220V DCDB Incomer from battery - Module type DB (I/C)
150A – DB Fixed Type
200A – DB Fixed Type
400A – DB Fixed Type
630A – DB Fixed Type
800A – DB Fixed Type
1250A – DB Fixed Type
150A – DB Drawout Type
200A – DB Drawout Type
400A – DB Drawout Type
630A – DB Drawout Type
800A – DB Drawout Type
1250A – DB Drawout Type
g) | 220V DC Fuse DB Incomer from DCDB - Module type H2
32A
50A
63A
h) | AC MCCB DB Incomer– Module Type H3
32A
63A
125A
i) | ACB Incomer to Emergency Board - Module Type DAEG/ DAEGN (I/C)
1600A
2 | BUSCOUPLER UNIT
a) | ACB Buscoupler to PCC/PMCC/MCC from Trafo. - Module Type DAET/ DAE (B/C)
630A
800A
1000A
1600A
2000A
2500A
3000A
4000A
b) | MCCB Buscoupler for MCC / ACDB – Module Type EM3 (B/C)
Upto 63A – Fixed Type
125A – Fixed Type
200A – Fixed Type
200A – Fixed Type
250A – Fixed Type
400A – Fixed Type
630A – Fixed Type
Upto 63A – Drawout Type
125A – Drawout Type
200A – Drawout Type
200A – Drawout Type
250A – Drawout Type
400A – Drawout Type
630A – Drawout Type
c) | 220V DCDB buscoupler - Module Type - DC
150A – DC Fixed Type
200A – DC Fixed Type
400A – DC Fixed Type
630A – DC Fixed Type
800A – DC Fixed Type
1250A – DC Fixed Type
150A – DC Drawout Type
200A – DC Drawout Type
400A – DC Drawout Type
630A – DC Drawout Type
800A – DC Drawout Type
1250A – DC Drawout Type
d) | 220V DCDB TIE - Module Type - HD
150A – HD Fixed Type
200A – HD Fixed Type
400A – HD Fixed Type
630A – HD Fixed Type
800A – HD Fixed Type
1250A – HD Fixed Type
150A – HD Drawout Type
200A – HD Drawout Type
400A – HD Drawout Type
630A – HD Drawout Type
800A – HD Drawout Type
1250A – HD Drawout Type
e) | ACB BUSCOUPLER to Emergency Board - Module Type DAEG (B/C)
1600A
3 | Outgoing ACB supply feeder - Module Type DAE/DAE-TIE (O/G)
630A
800A
1000A
1600A
3000A
4 | Outgoing ACB motor feeder - Module Type DM/PM (controlled from DDCMIS/PLC)
90.1- 200KW
5.1 | DOL Motor Starter - Unidirectional Drive(SFU CONTROLLED) - Drawout Type
a) | Module Type K2 (Controlled from LPBS)
Upto 5.5KW
5.6 - 7.0KW
7.1 - 13KW
13.1 - 24KW
24.1 - 29.9KW
b) | Module Type K21 (Controlled from LPBS)
30.0 - 37.0KW
37.1 - 40KW
40.1 - 50.0KW
50.1 - 75KW
75.1 - 90KW
90.1 - 110KW
c) | Module Type K3 (Controlled from LCP)
Upto 5.5KW
5.6 - 7.0KW
7.1 - 13KW
13.1 - 24KW
24.1 - 29.9KW
d) | Module Type K31 (Controlled from LCP)
30.0 - 37.0KW
37.1 - 40KW
40.1 - 50.0KW
50.1 - 75KW
75.1 - 90KW
90.1 - 110KW
e) | Module Type DK2/PK2/AK2 (Controlled from DDCMIS/PLC/ATRS)
Upto 5.5KW
5.6 - 7.0KW
7.1 - 13KW
13.1 - 24KW
24.1 – 29.9KW
f) | Module Type DK21/PK21/AK21 (Controlled from DDCMIS/PLC/ATRS)
30.0 - 37.0KW
37.1 - 40KW
40.1 - 50.0KW
50.1 - 75KW
75.1 - 90KW
90.1 - 110KW
g) | Module Type DK2E/PK2E/AK2E (Controlled from DDCMIS/PLC/ATRS)
Upto 5.5KW
5.6 - 7.0KW
7.1 - 13KW
13.1 - 24KW
24.1 – 29.9KW
h) | Module Type DK21E/PK21E/AK21E (Controlled from DDCMIS/PLC/ATRS)
30.0 - 37.0KW
37.1 - 40KW
40.1 - 49.9KW
50 - 75KW
75.1 - 90KW
90.1 - 110KW
6.1 | RDOL Motor Starter – Bidirectional Drive(SFU CONTROLLED) Drawout Type
a) | Module Type DN1/ PN1/ AN1 (Controlled from DDCMIS/PLC/ATRS)
Upto 5.5KW
5.6 - 7.0KW
7.1 - 13KW
13.1 - 24KW
24.1 – 29.9KW
a) | Module Type DN21/ PN21/ AN21 (Controlled from DDCMIS/PLC/ATRS)
30.0 - 37.0KW
37.1 - 40KW
40.1 - 49.9KW
50 - 75KW
75.1 - 90KW
7 | Outgoing MCCB/ SFU controlled feeders
a) | Outgoing SFU controlled supply feeder - Module Type E3 (O/G)
upto 10A - Fixed type
16A - Fixed type
25A - Fixed type
32A - Fixed type
63A - Fixed type
125A - Fixed type
160A - Fixed type
200A - Fixed type
250A - Fixed type
400A - Fixed type
600A - Fixed type
upto 10A - Drawout type
16A - Drawout type
25A - Drawout type
32A - Drawout type
63A - Drawout type
125A - Drawout type
160A - Drawout type
200A - Drawout type
250A - Drawout type
400A - Drawout type
600A - Drawout type
b) | Outgoing MCCB controlled supply feeder - Module Type E3 (O/G)
16A - Fixed type
32A - Fixed type
63A - Fixed type
125A - Fixed type
160A - Fixed type
200A - Fixed type
250A - Fixed type
400A - Fixed type
600A - Fixed type
16A - Drawout type
32A - Drawout type
63A - Drawout type
125A - Drawout type
160A - Drawout type
200A - Drawout type
250A - Drawout type
400A - Drawout type
600A - Drawout type
c) | Double pole SFU controlled 1-ph feeder - E1 (O/G)
10A - Fixed type
16A - Fixed type
25A - Fixed type
32A - Fixed type
63A - Fixed type
10A - Drawout type
16A - Drawout type
25A - Drawout type
32A - Drawout type
63A - Drawout type
d) | Double pole MCCB controlled 1-ph feeder - E1 (O/G)
16A - Fixed type
32A - Fixed type
63A - Fixed type
125A - Fixed type
16A - Drawout type
32A - Drawout type
63A - Drawout type
125A - Drawout type
e) | 1-Ph SFU controlled outgoing contactor feeder (EA1)
10A - Fixed type
16A - Fixed type
25A - Fixed type
32A - Fixed type
63A - Fixed type
10A - Drawout type
16A - Drawout type
25A - Drawout type
32A - Drawout type
63A - Drawout type
f) | 1-Ph MCCB controlled outgoing contactor feeder (EA1)
16A - Fixed type
32A - Fixed type
63A - Fixed type
16A - Drawout type
32A - Drawout type
63A - Drawout type
g) | 3-Ph SFU controlled outgoing contactor feeder (EA3)
10A - Fixed type
16A - Fixed type
25A - Fixed type
32A - Fixed type
63A - Fixed type
125A - Fixed type
200A - Fixed type
250A - Fixed type
400A - Fixed type
600A - Fixed type
10A - Drawout type
16A - Drawout type
25A - Drawout type
32A - Drawout type
63A - Drawout type
125A - Drawout type
200A - Drawout type
250A - Drawout type
400A - Drawout type
600A - Drawout type
h) | 3-Ph MCCB controlled outgoing contactor feeder (EA3)
16A - Fixed type
32A - Fixed type
63A - Fixed type
125A - Fixed type
200A - Fixed type
250A - Fixed type
400A - Fixed type
600A - Fixed type
16A - Drawout type
32A - Drawout type
63A - Drawout type
125A - Drawout type
200A - Drawout type
250A - Drawout type
400A - Drawout type
600A - Drawout type
i) | 3-Ph SFU controlled Contactor Changeover Between Two In Coming Supplies Module Type CC
16A - Fixed type
32A - Fixed type
63A - Fixed type
125A - Fixed type
200A - Fixed type
250A - Fixed type
400A - Fixed type
600A - Fixed type
16A - Drawout type
32A - Drawout type
63A - Drawout type
125A - Drawout type
200A - Drawout type
250A - Drawout type
400A - Drawout type
600A - Drawout type
8 | 1-Ph MCB controlled outgoing feeder (H1) from AC MCCB DB
10A
16A
9 | Outgoing Switch-fuse feeders
a) | 220V DC Outgoing SFU feeder (X)
2A - Fixed type
4A - Fixed type
6A - Fixed type
10A - Fixed type
16A - Fixed type
25A - Fixed type
32A - Fixed type
50A - Fixed type
63A - Fixed type
100A - Fixed type
125A - Fixed type
200A - Fixed type
250A - Fixed type
400A - Fixed type
500A - Fixed type
630A - Fixed type
2A - Drawout type
4A - Drawout type
6A - Drawout type
10A - Drawout type
16A - Drawout type
25A - Drawout type
32A - Drawout type
50A - Drawout type
63A - Drawout type
100A - Drawout type
125A - Drawout type
200A - Drawout type
250A - Drawout type
400A - Drawout type
500A - Drawout type
630A - Drawout type
10 | Common Auxiliary Module
a) | PT module
i | Bus PT module for PCC/PMCC-G1 Type
ii | Bus PT module for Emergency MCC-G2 Type
iii | Bus PT DCDB-S Type
iv | Bus PT module for MCC/ACDB-VM Type
b) | Space heater and Power Socket - TT
c.1) | 110V AC control supply module – Type CS (consisting of 415/110V control Trafo.)
1KVA
2KVA
2.5KVA
3KVA
5KVA
7.5KVA
10KVA
c.2) | 240 V AC control supply module – type CS (consisting of 415/240V control Trafo.)
1KVA
2KVA
2.5KVA
3KVA
5KVA
7.5KVA
10KVA
d.1) | 110V AC control supply module – Type CS-A (consisting of 415/110V control Trafo.)
1KVA
2KVA
2.5KVA
3KVA
5KVA
7.5KVA
10KVA
d.2) | 240 V AC control supply module – type CS-A (consisting of 415/240V control Trafo.)
1KVA
2KVA
2.5KVA
3KVA
5KVA
7.5KVA
10KVA
e) | 240V AC motor space heater module
f) | 220V DC supply module
(for receiving 220V DC supply)
g) | 24 V winding heating module
h) | Alarm module
i) | Test supply module
J.1) | 240 V AC Panel Space hetaing supply module – type SH (consisting of 415/240V control Trafo.)
1KVA
2KVA
2.5KVA
3KVA
5KVA
7.5KVA
10KVA
J.2) | 240 V AC Panel Space hetaing supply module – type SH-A (consisting of 415/240V control Trafo.)
1KVA
2KVA
2.5KVA
3KVA
5KVA
7.5KVA
10KVA
11 | Empty Panel with Horizontal & Vertical Busbar, Support & Auxiliary Busbar
a) | MCC Panel (Double Front Drawout Type)
250 / 250A
400 / 400A
630 / 630A
800 / 630A
1000 / 630A
1600 / 630A
2000 / 630A
2500 / 630A
3000 / 630A
4000 / 630A
b) | MCC Panel (Double Front Fixed Type)
250 / 250A
400 / 400A
630 / 630A
800 / 630A
1000 / 630A
1600 / 630A
2000 / 630A
2500 / 630A
3000 / 630A
4000 / 630A
c) | 220V DCDB Panel (Double Front Fixed type)
UPTO 630A (with 630A VBB)
1000A (with 630A VBB)
1600A (with 630A VBB)
d) | 220V DCDB Panel (Double Front Drawout type)
UPTO 630A (with 630A VBB)
1000A (with 630A VBB)
1600A (with 630A VBB)
12 | Empty Panel With Horizontal & Vertical Busbar, Support & Auxiliary Busbar
a) | PCC Panel (Single Front Drawout Type)
1600 / 1600A
2000 / 2000A
2500 / 2500A
3000 / 3000A
4000 / 4000A
b) | MCC Panel (Single Front Drawout Type)
250 / 250A
400 / 400A
630 / 630A
800 / 630A
1000 / 630A
1600 / 630A
2000 / 630A
2500 / 630A
3000 / 630A
4000 / 630A
c) | MCC Panel (Single Front Fixed Type )
250 / 250A
400 / 400A
630 / 630A
800 / 630A
1000 / 630A
1600 / 630A
2000 / 630A
2500 / 630A
3000 / 630A
4000 / 630A
d) | 220V DCDB Panel (Single Front Fixed Type)
UPTO 630A (with 630A VBB)
1000A (with 630A VBB)
1600A (with 630A VBB)
e) | 220V DCDB Panel (Single Front Fixed Type)
UPTO 630A (with 630A VBB)
1000A (with 630A VBB)
1600A (with 630A VBB)
13 | ACB Panel with Horizontal & Vertical Busbar, Support & Auxiliary Busbar
630 / 630A
800 / 630A
800 / 800A
1000 / 630A
1000 / 800A
1000 / 1000A
1600 / 630A
1600 / 800A
1600 / 1000A
1600 / 1600A
2000 / 630A
2000 / 800A
2000 / 1000A
2000 / 1600A
2000 / 2000A
2500 / 630A
2500 / 800A
2500 / 1000A
2500 / 1600A
2500 / 2000A
2500 / 2500A
3000 / 630A
3000 / 800A
3000 / 1000A
3000 / 1600A
3000 / 2000A
3000 / 2500A
3000 / 3000A
4000 / 630A
4000 / 800A
4000 / 1000A
4000 / 1600A
4000 / 2000A
4000 / 2500A
4000 / 3000A
4000 / 4000A
14 | Dummy Panel
UPTO 630A
800A
1000A
1600A
2000A
2500A
3000A
4000A
15 | Unit Prices For Circuit Components
a) | Air Circuit Breaker without releases
630A MDO
800A MDO
1000A MDO
630A ACB, 3P, EDO, AC
800A ACB, 3P, EDO, AC
1000A ACB, 3P, EDO, AC
4000A ACB, 3P, EDO, AC
3200A ACB, 3P, EDO, AC
2500A ACB, 3P, EDO, AC
2000A ACB, 3P, EDO, AC
1600A ACB, 3P, EDO, AC
1250A ACB, 3P, EDO, AC
1250A ACB, 2P, MDO, DC
b) | MCCB, 2NO+2NC AUX, FSC
16A
25A
32A
63A
80A
115A
150A
185A
265A
315A
400A
630A
c) | MCCB, 2NO+2NC AUX, ASC
16A
25A
32A
63A
80A
115A
150A
185A
265A
315A
400A
630A
d) | MCCB with LSIG release
200A
250A
300A
350A
400A
630A
e) | MCCB - Motorized with LSIG release
200A
250A
300A
350A
400A
630A
f) | POWER FUSE LINK FOR SFU (AC) - TPN
Upto 16A
25A
32A
63A
125A
250A
400A
630A
g) | POWER FUSE LINK FOR SFU (DC) - DP
Upto 16A
25A
40A
50A
60A
80A
100A
200A
300A
400A
630A
h) | SFU WITHOUT POWER FUSE LINK (AC) - TPN
Upto 16A
25A
32A
63A
125A
250A
400A
630A
i) | SFU WITHOUT POWER FUSE LINK (DC) - DP
Upto 16A
25A
40A
50A
60A
80A
100A
200A
300A
400A
630A
j) | HRC Fuse Links (Offset tag Type)
Upto 10A
16A
25A
32A
50A
63A
k) | HRC Fuse DIN Type (Blade Contact)
Upto 10A
16A
20A
32A
36A
50A
63A
80A
100A
125A
160A
200A
250A
315A
400A
Control Fuse Link
l) | Power contactor (AC)
16A
25A
32A
63A
80A
115A
150A
185A
265A
315A
400A
m) | Power contactor (DC)
16A
25A
32A
63A
80A
115A
150A
185A
265A
400A
n) | Fuse Base
UPTO 20A
32A
50/63A
100A
250A
400A
630A
o) | Auxiliary contactor AC/DC
i) | AC Aux. contactor
2NO + 2NC
3NO + 3NC
4NO + 4NC
6NO + 6NC
ii) | DC Aux. contactor
2NO + 2NC
3NO + 3NC
4NO + 4NC
6NO + 6NC
p) | Protection Relay
VAGM 23
CTU 12
CTU 32
VTT 11
VAG 11
VAA 11
VAJHM 13
VAJHM 23
CDGM-12
CAG 12
CAG 34
CCUM 21
CDG 11
CDG 31
CDG 61
VDG 14
CDV 62
CAG 14
VAX 31
CAG 37
CAEM-21
VAG-21
VAJC-11
CTMM-501
MOTPRO
VAA21
VTT12
VTIG
VTU21
NUMERICAL RELAY FOR PROTECTION, T/C SUPERVISION, LOGIC, METERING FUNCTION & WITH CHECK SYNCHRONIZATION, REF PROTECTION, FUSE FAILURE, ENERGY METERING, OVER LOAD PROTECTION, 50, 50N, 51, 51N, 27, 98, 86, 25, 95, 30A, 30B, 64R
SEF NUMERICAL RELAY
NUMERICAL RELAY FOR PROTECTION, T/C SUPERVISION, LOGIC, METERING FUNCTION & WITH CHECK SYNCHRONIZATION, FUSE FAILURE, ENERGY METERING, OVER LOAD PROTECTION 50, 50N,51, 51N, 27, 98, 86, 25, 95, 30A, 30B
NUMERICAL RELAY FOR PROTECTION, T/C SUPERVISION, LOGIC, METERING FUNCTION & WITH CHECK SYNCHRONIZATION, FUSE FAILURE, 50, 50N,51, 51N, 27, 98, 86, 25, 95, 30A, 30B
NUMERICAL RELAY FOR PROTECTION, T/C SUPERVISION, LOGIC, METERING FUNCTION & WITH CHECK SYNCHRONIZATION, FUSE FAILURE, ENERGY METERING, OVER LOAD PROTECTION 50, 50N,51, 51N, 27, 98, 86, 25, 95, 30A, 30B, DG PROTECTION (Like Neutral Under-voltage-27N, Power Direction / Reverse Power (Islanding)-32, Negative Phase Sequence Over-current (Phase unbalance, reverse phase sequence) -46, , Negative Sequence Voltage -47, Ground Over-voltage trip or ground over-current trip-51G, Instantaneous Over-voltage trip (ferro-resonance)-59, Over-voltage trip-59T, Neutral over-voltage-59N, Over/Under Frequency trip-81O/ 81U etc.)
NUMERICAL RELAY FOR PROTECTION, T/C SUPERVISION, LOGIC, METERING FUNCTION & FUSE FAILURE, OVER LOAD PROTECTION 50, 50N,51, 51N, 27, 98, 86, 95, 30A, 30B
NUMERICAL RELAY FOR PROTECTION, T/C SUPERVISION-95, LOGIC, METERING FUNCTION & FUSE FAILURE-98, OVER LOAD PROTECTION, LOCKED ROTOR PROTECTION-14, RESTART INHIBIT PROTECTION-49, NEGATIVE SEQUENCE PROTECTION-46, 50, 50N, 51, 51N, 27, 86, 30A, 30B
Communicable type Numerical relay for O/C, E/F, TC Supervision on IEC-61850 protocol
Communicable type Numerical relay for O/C, E/F, Check Synchronization, TC Supervision on IEC-61850 protocol
Communicable type Numerical relay for Voltage control O/C, 3Phase O/C, Reverse power, Differential, Neutral Displacement, E/F, U/V, O/V protection, Check Synchronization, TC Supervision on IEC-61850 protocol
Communicable type Numerical relay for Under voltage, Over voltage etc. on IEC-61850 protocol
Communicable type Numerical relay for E/F protection for DCDB on IEC-61850 protocol
Communicable type Numerical relay for composite motor protection including TC Supervision on IEC-61850 protocol
Communicable type Numerical relay for Neutral Displacement on IEC-61850 protocol
Communicable type Numerical relay for O/C, E/F, TC Supervision on Modbus protocol
Communicable type Numerical relay for O/C, E/F, Check Synchronization, TC Supervision on Modbus protocol
Communicable type Numerical relay for Voltage control O/C, 3Phase O/C, Reverse power, Differential, Neutral Displacement, E/F, U/V, O/V protection, Check Synchronization, TC Supervision on Modbus protocol
Communicable type Numerical relay for Under voltage, Over voltage etc. on Modbus protocol
Communicable type Numerical relay for E/F protection for DCDB on Modbus protocol
Communicable type Numerical relay for composite motor protection including TC Supervision on Modbus protocol
Communicable type Numerical relay for Neutral Displacement on Modbus protocol
Numerical Check synchronising Relay
Check synchronising Relay Type-SKE11 or better
Guard Relay
NUMERICAL RELAY Over current and Earth fault
BATTERY EARTH FAULT RELAY, 1-7mA, NOMINAL VOLTAGE-220V DC, 1DV, 2NO S/R, FLUSH
OVERLOAD RELAY, NOMINAL VOLTAGE-220V DC, O/V VLTAGE SETTING-110%, 1/4NV, 1NO+1NC S/R
UNDER VOLTAGE RELAY, NOMINAL VOLTAGE-220V DC, U/V SETTING-80%, AUX..-240V AC, 1/2NH, 1NO+2NC S/R
JAMING RELAY - CAG17
q) | Bimetal Thermal O/L Relays
i) | Thermal O/L relay with SPP - OLR
Upto 5.5KW
5.6 to 11KW
11.1 to 22KW
22.1 to 45KW
45.1 to 75KW
75 to 110KW
ii) | Heavy Duty Thermal O/L relay with SPP - OLR
Upto 5.5KW
5.6 to 11KW
11.1 to 22KW
22.1 to 45KW
45.1 to 75KW
75 to 110KW
r) | Timer (DC)
ON DELAY TIMER, 0.5-5SEC., 220V DC, 2NO+2NC
ON DELAY TIMER, 1.0-10SEC. 220V DC, 2NO+2NC
240VAC MTR RESTART CONTROL TIMER (.2-60SECS)
240VAC ON DELAY TIMER(1-10SECNS)WITH 1NO
220VDC ON DELAY TIMER(.5-5SECS) WITH 1NO
220VDC 0N DELAY TIMER(0.5-5SECS)WITH 3NO
220VDC ON DELAY TIMER(1-10SECS) WITH 3NO
s) | Meter
AC ammeter (Digital)
AC ammeter (Analog) linear scale
AC ammeter (Analog) compressed scale
DC ammeter (Digital)
DC ammeter (Analog)
AC voltmeter (Digital)
DC voltmeter (Analog)
Wattmeter (3 Phase)
Wattmeter (1 Phase)
TVM meter
DIGITAL ENERGY METER
Frequency meter
Synchroscope
Differential Voltmeter
Differential Frequency meter
Multifunction digital Energy meter with RS485 Port (0.2 Acc. Class)
Multifunction digital Energy meter with RS485 Port (0.5 Acc. Class)
Multifunction digital Energy meter with RS485 Port (1.0 Acc. Class)
t) | Single Phase Preventor Relay
u) | MCB
6A, 4P 415V AC
6A DP, 240V AC
10A DP, 240V AC
16A DP, 240V AC
32A DP, 240V AC
6A DP, 110V AC
10A DP, 110V AC
16A DP, 110V AC
32A DP, 110V AC
16A DP, 220V DC
6A DP, 220V DC
6A DP, 240V AC
10A SP, 240V AC
16A SP, 240V AC
32A SP, 240V AC
6A SP, 110V AC
10A SP, 110V AC
16A SP, 110V AC
32A SP, 110V AC
16A SP, 220V DC
6A SP, 220V DC
v) | SWITCH & PUSH BUTTON
BREAKER CONTROL SWITCH, 16A,220V DC, 2CLOSE+2TRIP
DC ISOLATING SWITCH 16A,220V DC, DP, BASE MTG.
16A,240V AC SELECTOR SWITCH 3WAY, 4POLE, FLUSH MTG
25A,240V AC SELECTOR SWITCH 3WAY, 4POLE, FLUSH MTG
16A,240V AC SELECTOR SWITCH 2WAY, 2POLE, FLUSH MTG
NORMAL/ TRIAL SEL. SWITCH, 2POLE , 2WAY, 10A 240V AC, FLUSH MTG,
MCC/ NORMAL/ TRIAL SEL. SWITCH, 2POLE ,3WAY, 10A 240V AC, FLUSH MTG
SWGR/ REMOTE SEL. SWITCH 3POLE 2WAY,16A 220V DC, FLUSH MTG
SWGR/ NORMAL/ TRIAL SEL. SWITCH, 3POLE, 3WAY, 16A 220V DC, FLUSH MTG.
NORMAL/ TRIAL SEL. SWITCH, 2POLE , 2WAY, 10A 240V AC, FLUSH MTG, LOCKABEL TYPE
MCC/ NORMAL/ TRIAL SEL. SWITCH, 2POLE ,3WAY, 10A 240V AC, FLUSH MTG, LOCKABEL TYPE
SWGR/ REMOTE SEL. SWITCH 3POLE 2WAY,16A 220V DC, FLUSH MTG.LOCKABLE TYPE
SWGR/ NORMAL/ TRIAL SEL. SWITCH, 3POLE, 3WAY, 16A 220V DC, FLUSH MTG., LOCKABLE TYPE
AMMETER SELECTOR SWITCH
VOLTMETER SELECTOR SWITCH
TOGGLE SWITCH 5A, 240V AC
AC SWITCH SPST-5A,240V AC
10A, 220V DC SWITCH
Door Limit switch
Ammeter selector switch
Voltmeter selector switch
Synchronisation selector switch
Trip selector switch
Push Button
2NO + 2NC Shrouded
1NO + 1NC Shrouded
2NO + 2NC Mushroom head stayput
2NO + 2NC Lockable type
w) | Indicating Lamp Assembly (LED Type)
240V AC-GREEN
240V AC-RED
240V AC- AMBER
110V AC-GREEN
110V AC-RED
110V AC- AMBER
220V DC-WHITE
220V DC-RED
220V DC-GREEN
220V DC-BLUE
220V DC- AMBER
63.5V AC-RED
63.5V AC-YELLOW
63.5V AC-BLUE
x) | CT
i) | Metering CT
Upto 75/1A
100/1A
125/1A
150/1A
200/1A
250/1A
300/1A
400/1A
500/1A
630/1A
800/1A
1000/1A
1250/1A
1600/1A
2000/1A
2500/1A
3000/1A
4000/1A
ii) | Protection CT (5P20)
Upto 75/1A
100/1A
125/1A
150/1A
200/1A
250/1A
300/1A
400/1A
500/1A
630/1A
800/1A
1000/1A
1250/1A
1600/1A
2000/1A
2500/1A
3000/1A
4000/1A
630/5A
800/5A
1000/5A
1250/5A
1600/5A
2000/5A
2500/5A
3000/5A
4000/5A
iii) | PS Class CT
1600/1A
2500/1A
3000/1A
4000/1A
1600/5A
2500/5A
3000/5A
4000/5A
y) | Voltage Transformer
i) | 415/Ö3 : 110/Ö3V, 1ph, 50VA
ii) | 415/Ö3 : 110/Ö3V, 1ph, 100VA
iii) | 415/Ö3 : 240/Ö3V, 1ph, 50VA
iv) | 415/Ö3 : 240/Ö3V, 1ph, 100VA
z) | Toggle switch (16A)
aa) | Secondary Isolating Contact Block
ab) | Control Terminal (Fixed)
ac) | Thermostat
ad) | CONTROL TRANSFORMER
415/240V,CL-E, 1 KVA
415/240V,CL-E, 2KVA
415/240V,CL-E, 2.5KVA
415/240V,CL-E, 3KVA
415/240V,CL-E, 5KVA
415/240V,CL-E, 10KVA
415/110V,CL-E, 1 KVA
415/110V,CL-E, 2KVA
415/110V,CL-E, 2.5KVA
415/110V,CL-E, 3KVA
415/110V,CL-E, 5KVA
415/110V,CL-E, 10KVA
ac) | 4-20mA Dual o/p, Aux sup 220V DC, 1A, Current Transducer
4-20mA Dual o/p, Aux sup 240V AC, 1A, Current Transducer
4-20mA Dual o/p, Aux sup 110V AC, 1A, Current Transducer
4-20mA Dual o/p, Aux sup 220V DC, VoltageTransducer, PTR 415/110V
4-20mA Dual o/p, Aux sup 240V AC, VoltageTransducer, PTR 415/110V
4-20mA Dual o/p, Aux sup 110V AC, VoltageTransducer, PTR 415/110V
4-20mA Dual o/p, Aux sup 220V DC, FrequencyTransducer, PTR 415/110V
4-20mA Dual o/p, Aux sup 220V DC, Input 0-75mV DC, Current Transducer-DC
4-20mA Dual o/p, Aux sup 240V AC, Input Voltage 0-220V DC, Voltage Transducer-DC
ad) | 4-20mA Dual Output kW transducer
ae) | 4-20mA Dual Output kVA transducer
af) | 4-20mA Dual Output PF transducer
ag) | 4-20mA Dual Output Frequency transducer
ah) | Interposing relay RE 302 or Eqvt with freewheeling diode & LED
ai) | Laptop PC alongwith software & hardware
aj) | 3 PIN SOCKET - 5A, 110V AC, 3PIN
ak) | THERMOSTATE, DIAL TYPE
am) | SPACE HEATER
an) | CFL WITH HOLDER
ao) | NEUTRAL LINK
20A FOR CONTROL CKT. & POWER CKT. UPTO 25A MCCB RATING
32A FOR 50A MCCB RATING
63A FOR 100A & 125A MCCB RATING
125A FOR 250A MCCB RATING
250A FOR 400A & 500A MCCB RATING
ap) | CASTLE KEY INTERLOCK FOR MCCB - 3LOCK+2KEY
aq) | MECHANICAL INTERLOCK FOR POWER CONTACTOR
16A
25A
32A
63A
80A
115A
150A
185A
265A
315A
400A
ar) | AUX. CONTACTOR
2NO+2NC, CV-220V DC
4NO, CV-220V DC
2NO+2NC, CV-240V AC
3NO+1NC, CV-240V AC
2NO+2NC, CV-110V AC
3NO+1NC, CV-110V AC
1NO + 1NC 240V AC
1NO + 1NC 110V AC
1NO + 1NC 220V DC
1NO 240V AC
1NO 110V AC
1NO 220V DC
as) | ISOLATING TRANSFORMER-15kVA
ISOLATING TRANSFORMER-20kVA
ISOLATING TRANSFORMER-25kVA
ISOLATING TRANSFORMER-30kVA
16 | Foundation Frame
a) | MCC panel
upto 1600A (SF)
2500A (SF)
3000A (SF)
4000A (SF)
upto 1600A (DF)
2500A (DF)
3000A (DF)
4000A (DF)
b) | 220V DCDB panel
SF
DF
c) | PCC / PMCC panel
upto 1600A
2500A
3000A
4000A
17 | Connection from PMCC/MCC panel to PMCC/MCC panel
250A
400A
630A
800A
1000A
1600A
2500A
3000A
4000A
18 | Cable Glands & Lugs:
a) | Single Compression Cable Glands for cable sizes:
2C X 2.5 Sq. mm.
3C X 2.5 Sq. mm.
5C X 2.5 Sq. mm.
7C X 2.5 Sq. mm.
12C X 2.5 Sq. mm.
16C X 2.5 Sq. mm.
2C X 10 Sq. mm.
2C X 16 Sq. mm.
2C X 25 Sq. mm.
2C X 35 Sq. mm.
2C X 50 Sq. mm.
2C X 70 Sq. mm.
2C X 95 Sq. mm.
3C X 2.5 Sq. mm.
3C X 10 Sq. mm.
3C X 16 Sq. mm.
3C X 25 Sq. mm.
3C X 35 Sq. mm.
3C X 50 Sq. mm.
3C X 70 Sq. mm.
3C X 95 Sq. mm.
3C X 150 Sq. mm.
3C X 185 Sq. mm.
3C X 240 Sq. mm.
3.5C X 25 Sq. mm.
3.5C X 50 Sq. mm.
3.5C X 70 Sq. mm.
3.5C X 300 Sq. mm.
3.5C X 240 Sq. mm.
3.5C X 185 Sq. mm.
3.5C X 95 Sq. mm.
4C X 16 Sq. mm.
4C X 35 Sq. mm.
1C X 400 Sq. mm.
1C X 630 Sq. mm.
b) | Double Compression Cable Glands for cable sizes:
2C X 2.5 Sq. mm.
3C X 2.5 Sq. mm.
5C X 2.5 Sq. mm.
7C X 2.5 Sq. mm.
12C X 2.5 Sq. mm.
16C X 2.5 Sq. mm.
2C X 10 Sq. mm.
2C X 16 Sq. mm.
2C X 25 Sq. mm.
2C X 35 Sq. mm.
2C X 50 Sq. mm.
2C X 70 Sq. mm.
2C X 95 Sq. mm.
3C X 2.5 Sq. mm.
3C X 10 Sq. mm.
3C X 16 Sq. mm.
3C X 25 Sq. mm.
3C X 35 Sq. mm.
3C X 50 Sq. mm.
3C X 70 Sq. mm.
3C X 95 Sq. mm.
3C X 150 Sq. mm.
3C X 185 Sq. mm.
3C X 240 Sq. mm.
3.5C X 25 Sq. mm.
3.5C X 50 Sq. mm.
3.5C X 70 Sq. mm.
3.5C X 300 Sq. mm.
3.5C X 240 Sq. mm.
3.5C X 185 Sq. mm.
3.5C X 95 Sq. mm.
4C X 16 Sq. mm.
4C X 35 Sq. mm.
1C X 400 Sq. mm.
1C X 630 Sq. mm.
c) | Cable Lugs for sizes:
2.5 Sq. mm.
10 Sq. mm.
16 Sq. mm.
25 Sq. mm.
35 Sq. mm.
50 Sq. mm.
70 Sq. mm.
95 Sq. mm.
120 Sq. mm.
150 Sq. mm.
185 Sq. mm.
240 Sq. mm.
300 Sq. mm.
400 Sq. mm.
630 Sq. mm.
19 | Daily 8 hour rate deployed at site:
Engineer : (per day)
20 | Module Name plate
21 | Wires for Secondary wiring:
a) | 1.5 Sq. mm. per meter
b) | 2.5 Sq. mm. per meter
c) | 4.0 Sq. mm. per meter
22 | Control Terminal for Secondary wiring suitable for cable size:
a) | 0.5 Sq. mm.
b) | 1.5 Sq. mm.
c) | 2.5 Sq. mm.
23 | Unit price for following tests:
a) | Local Push Button Station - Degree of protection test
b) | Local motor Starter - Degree of protection test
24 | Electrical Junction Boxes (for termination of 0.5 sqmm screened control cables)
a) | 48 ways
b) | 64 ways
c) | 72 ways
a) | 96 ways
25 | ISMC channels
a) | ISMC 75 channel per meter
a) | ISMC 100 channel per meter
26 | ANY OTHER ITEM WHICH MAY BE REQUIRED FOR ADDITION / DELETION DURING DETAILED ENGINEERING
27 | SBMCC
WALL BLOWER FEEDER-0.56 KW
WALL BLOWER FEEDER-0.09 KW
LR BLOWER FEEDER-0.56 KW
LR BLOWER FEEDER-0.736 KW
AH BLOWER FEEDER-0.18 KW
ISOLATION BLOWER VALVE-4 KW
28 | ETHERNET SWITCH
8 PORT
16 PORT
24 PORT