## 2X20 MT LPG PROPANE SYSTEM
M209CG8P0325BDP AMENDED SPECIFICATION Design, Engineering, Supply, Erection, Testing and Commissioning of 2 X 20 MT Above Ground LPG/ PROPANE Storage Yard with necessary LPG/ PROPANE accessories and distribution of LPG/ PROPANE Header pipe line system. (HY:M&S:2x20MT:LPG/PROPANE:SYSTEM)
Sl.No. | Description of Item | Specified & To be confirmed | Offered | Remarks
| PURPOSE | Establishment of 2 X 20 MT LPG/PROPANE Yard and distribution of Header and pipelines to all the blocks for Furnaces, Heating and cutting application as per Tender Sepcs.
1.0 | Specification
1.1 | Design (Basic and detailed Engineering), supply of all materials, equipments items and components with attendant peripherals required with in the Plant battery limits as per sample SITE plan & P&I drawings No.HY/M&S/GS/LPG/01 & HY/M&S/GS/LPG LAYOUT)/ plans approved by the Chief Controller of Explosives, Nagpur under the Satatutory requirements of Static and Mobile Pressure Vessel Rule 1981 and other complying standards, IS:6044 Part II, Including erection, testing and commissioning of LPG / PROPANE Bulk Storage System, Capacity 2X20MT, suitable for Above Ground Storage . | Vendor to confirm
1.2 | Supply and installation of 2X20 MT LPG / PROPANE Storage tank, unloading system, vapourisers, safety fittings, valves, pressure regulating system, instrumentation, electrical system,fire safety system etc. as detailed below. | Vendor to confirm
1.3 | Supply and laying of pipeline from storage yard to different shop as per Drawing No. HY/M&S/GS/LPG HEADER PIPE LINE/ 01( Supply total materials required for laying pipeline except running length of pipelines.Required pipes shall be supplied by BHEL free of cost in standard length. Paint in the scope of vendor). | Vendor to confirm
1.4 | Complete civil work with in the baterry limit is in vendor scope as per CCOE approved layout. | Vendor to confirm
1.5 | All equipments installed in LPG/PROPANE Yard and all fittings in LPG/Propane pipe line distribution system should be desigened for PROPANE vapour use. | Vendor to confirm
1.5 | Operation and comprehensive maintenance Contract for LPG/Propane Yard and Pipe line distribution system for three years as per specification ref. HY:M&S:AMC:2009. | Vendor to confirm
1.6 | Price Bid evaluation will be done on the total cost to BHEL including O&M charges for 3 years i.e.Supply of basic equipment, installation, commissioning and prove-out PLUS operation and Maintenance for three years together. Purchase order for O&M charges will be issued separately and payment will be made on monthly basis after the project is commissioned and put in operation. | Vendor to confirm
Scope of supply
2.0 | PROPANE/LPG storage tank:
2.1.1 | Quantity | 2 nos.
2.1.2 | Tank capacity | 20 MT
2.1.3 | Water capacity | 46,200 Litrs Water Capacity
2.1.4 | Design code | IS: 2825 - 1969, Class 1 and SMPV (U) Rules 1981
2.1.5 | Design Pressure | 21.0 Kg/ sq.cm + Static Head
2.1.6 | Design temperature | 55 deg.C Max / -42 degree C Min.
2.1.7 | Working temperature | Ambient
2.1.8 | Hydro test pressure | 27.5 Kg/sq.cm min./ As per Code of Construction
2.1.9 | Installation configuration | Above Ground
2.1.10 | Corrision Allowance | 1.5 mm
2.1.11 | Radiography | 100%
2.1.12 | Heat treatment | As per Code requirement
2.1.13 | Design approval, OISD norms,Third party inspection certificate for tank and system | CCOE approved
2.1.14 | Material of Construction | SA 516 Gr. 70 or SA 537 Class- I or equivalent Boiler and Pressure Vessel Quality Steel
2.1.15 | Flanges | SA 105 / SA 516 Gr.70 /SA 515 Gr.70
2,1,16 | Couplings | SA 105
2.1.17 | Studs | SA 193 Gr.7
2.1.18 | Nuts | SA 194 Gr.2H
2.1.19 | Size of Manway | 20" NB X 1 No. for A/G
2.1.20 | Estimated Tank Weight | Vendor to give( WITH OUT PRODUCT)
2.1.21 | Surface Protection | Total Dry Film Thickness 140 microns min. With primer & finished paint on outside.
3 | Safety fitting for the Propane/LPG Tanks. Each tank shall have the following safety fittings
3.1.1 | 2"X 3" angle body safety relife valve complete with isolation valves, safety vents and rain hoods etc. | 3 nos or as required vendor to specify
3.1.2 | 1/4" NPT fixed level gauge | 1 No or as required vendor to specify
3.1.3 | 1" NPT Slip Tube Gauge or equiv. | 1 No or as required vendor to specify
3.1.4 | Pressure Gauge Rego-948 or equivalent 6" dial | 1 No or as required vendor to specify
3.1.5 | 0-300 Psig, complete with bank up Excess Flow Check Valve 3/4" NPT Female Presure Gauga Range 0-500 Psig. | 1 No or as required vendor to specify
3.1.6 | 3/4" NPT Thermodial -20 Deg. C to + 100 Deg.C | 1 No or as required vendor to specify
3.1.7 | 2" MGM make or equivalent make but CCOE approved Excess Flow Check (EEFC) Valve for liquid and vapour lines vapour recovery.(Wafer/ sandwhich type) | 5 Nos as required vendor to specify
3.1.8 | High pressure switch interlock for compressor c/w transmitter and alarm | 1 No or as required vendor to specify
3.1.9 | High level switch interlock for unloading pump c/w transmitter and alarm | 1 No or as required vendor to specify
3.1.10 | Special sealless Magnetic level Gauge of Rochester, Belgium for continous reading of Tank's liquid content | 1 No of 8" Dial withTransmitter for Remote Read Out at Control Panel - vendor to specify and confirm
4.0 | PROPANE/ LPG Unloading Pump:( Skid mounted unit)
4.1 | Quantity | 1 no.
4.2 | Function | Liquid transfer from mobile tanker to storage tank
4.3 | Type | Sliding Vane Positive displacement type with built in Relief valve, complete with Flame proof Motor base plate guard etc. As per as per Drawing No. HY/M&S/GS/LPG UP/ 03. 300 LPM @ 2 Kg/Cm2
4.4 | Capacity | 300 LPM
4.5 | Make and model 521/LGL2DE (Croken / Blackmer , USA or Reputed make approved by CCOE) | Vendor to specify
4.6 | Inlet and outlet connection / size | To suit the pipe connection as per design
4.7 | Motor duly coupled:Power rating | Flame Proof suitable for group IIA & IIB Gases: 5HP
4.8 | Starter | DOL Flame proof
4.9 | Drive | V- Belt
4.10 | Duty | Intermittent
4.11 | Special Features | Tested on Propane/LPG
4.12 | Unloading Pump | < 2 Hrs. from 18 MT Tanker
4.13 | Extended Performance Gurantee of 36 months from the date of commissioning or 42 months from FOB date, whichever period is expires earlier as pre-requisite | Vendor to specify
5.0 | Unloading Vapour recovery compressor For LPG/Propane:
5.1 | Quantity | 1 no.
5.2 | Make and model Croken/Blackmer, USA make approved by CCOE | 291-107/LB161LU c/w instrumentation as per tender GA Drawing No. HY/M&S/GS/LPG/COMP/ 04, Croken Blackmer USA make
5.3 | Type of Compressor | Reciprocating Air Cooled Non - Lubricated type special desined for LPG/Propane service
5.4 | Bore | 76.2 mm
5.5 | Stroke | 63.5 mm
5.6 | piston Displacement | 28 MCH at 825 RPM
5.6 | Max working pressure | 350 Psia
5.7 | Motor type and Rating | 7.5 HP at 825 RPM in Flame Proof with local Flame Proof Push button,weatheproof type construction. Construction of compressor shall be as per guidelines given in IS 6044 Part I & II, OSID norms, CMRI specifications. The designed should be pproved by CCOE.
5.8 | Max Compression Ratio Continous Duty | 5
5.9 | Max Compression Ratio Intermittent Duty | 9
5.1 | Protection agaist dry run | Vendor to confirm
5.11 | Provision of liquid sensor at inlet | Vendor to confirm
5.12 | Total Time to evacuate 40CuM LPG/PROPANE Tank lory | 4.5 hrs
5.13 | Total Time to evacuate 25CuM LPG/PROPANE Tank lory | Appx.3 Hrs
5.14 | Furnish Compressor Performance Table | Vendor to confirm
5.15 | Extended Performance Gurantee of 36 months from the date of commissioning or 42 months from FOB date, whichever period is expires earlier as pre-requisite | Vendor to specify
6.0 | LPG/PROPANE Vaporiser:
6.1 | Quantity | 4 nos.
6.2 | Capacity | 300 kg/hr in modular design.
6.3 | Make and model (Reputed make approved by CCOE) | Vendor to specify
6.4 | Design/Type | Electrically heated, hot water bath type, to deliver dry saturated LPG vapour.Design of CCOE approved make and As per GA Drawings No. HY/M&S/GS/LPG/05
6.5 | Inlet and outlet connection / size | To suit the pipe connection as per design for PROPANE
6.6 | Design Pressure | Vendor to specify
6.7 | Test Pressure | Vendor to specify
6.8 | Solenoid valve at liquid inlet | Vendor to confirm
6.9 | Pressure switches | One safety pressure switch each on the vapouriser before the regulator and one pr.switch on the outlet after the regulator to control the solenoid valve.
6.10 | Pressure relief valve | Vendor to confirm
6.11 | Mounting arrangement | Vendor to specify
6.12 | Dimension details | Vendor to specify
6.13 | Shell/ Coil- Design/MOC | ASME/TEMA R; C S / SS 316
6.14 | Power | Vendor to specify
6.15 | Controls : Inlet Safety Solenoid Valve - Hugh Level Float / Hi. Pr. Switch - RTD's for temp controls - Digital Temp. Indicator Controller | Vendor to confirm
6.16 | Electrical | 415 V /3PH/50 Hz/required capacity CCOE Nagpur approved
7.0 | Valves & Fittings for the (PROPANE )Pipeline per tender drawing No.HY/M&S/GS/LPGYARD/01
7.1 | Fire Safe & Antistatic design Full Bore Ball Valves | Vendor to calculate as per P&ID
7.2 | Pop action valve, NRV's,Instruments,controls etc. (Required quantity and size as per design) | Vendor to confirm
7.3 | Pipe fittings for the valves / pipelines (required quantity and size as per design.) | Vendor to specify
7.4 | Make and material of the valves, gauges, fittings | Vendor to specify
8.0 | Piping system inside yard for LPG/Propane liquid and Vapour line as per tender drawing No.HY/M&S/GS/LPGYARD/01/
8.1 | Seamless sch. 80 heavy duty pipelines - Liquid inlet / outlet, vapour balance / outlet,, drain line. (required size and quantity over and above the existing piping as per desig,) | Vendor to confirm
9.0 | Structural steel:
9.1 | Steel required for approach platforms ( chequered plates / floor grills ) on the tank, piping supports and other requirements as per design | Vendor to confirm
10.0 | Accessories for LPG/PROPANE Piping System. With in yard:-
10.1 | Strainers for Vaporizers (Qty. & size as per design) | Vendor to confirm
10.2 | Strainer for LPG/PROPANE Pump (quantity and size as per design) | Vendor to confirm
10.3 | Non - return valve for LPG/ Propane Pump (quantity and size as per design) | Vendor to confirm
10.4 | Make, material, test pressure of the above Items | Vendor to confirm
11.0 | Pressure Regulating Station: | Vendor to confirm
11.1 | Pressure Regulators (required quantity and size as per design) | Vendor to confirm
11.2 | Type : Director Actuating Type with auto change over Range of Inlet : 14.5 KG/Cm2 (Max) 3.5 Kg/Cm2 ( Min) Capacity : 900 Kg/ hr. max./ 300 Kg/Hr. min. on continous basis Out let Pressure : 1.5 - 2.0 KCSG adjustable) with +/_ 0.5 KCSG Model/Make : Fischer/Elster/RMG/COPRIM/NIRMAL/ Equ. Approved by CCOE | Vendor to specify and confirm
11.3 | Filters for pressure requlator ( Required quantity and size as per design) | Vendor to confirm
11.4 | Slam shut - off for pressure regulator (Required quantity and size as per design) | Vendor to confirm
11.5 | Make and end connections | Vendor to confirm
11.6 | FLAME ARRESTOR – • Construction of flame arrestor shall be as per guidelines given in IS 6044 Part I & II / OISD norms / CCOE requirements / CMRI specifications which ever applicable. • To be supplied along with test certificate. • Properly sized SS mesh layers are to be provided as per norms. • With flanged ends. • Easy to maintain & clean. • Quantity – 2 Nos. (1No.at LPG/Propane installation & 1No.at shop entrance.) | Vendor to confirm
11.7 | Leak detection system at LPG/Propane installation & supply pipeline upto shop entrance - No. of sensors: 1.Bullet area - 4 Nos. 2.Vaporiser shed - 2 Nos.3. PRV station area- 1 Nos.4. Decanting area - 1 No.Total at LPG installation - 8 Nos. * Control Panels: - 1 Nos.Remaining details – as per enclosed Data sheet. Required cable laying from sensors to control panel will be in suppliers scope. It includes supply, errection & commissioning. Leak indication should be in digital form at field as well as Control Panel. | Vendor to confirm
11.8 | Portable leak detectors shall be supplied along with valid calibration certificate. Make - Cosmos / equivalent. | Vendor to confirm
12.0 | Decanting Hoses:
12.1 | Double ply wire braided neoprene hose for liquid and vapour (Required quantity and size as per design) 1 No. hose for vapor(1. 1/2") 1 No. for Liquid (2") for each station and one set spare to each (liqud and vapou). | Vendor to confirm
12.2 | Make and pressure rating of the hoses | Vendor to confirm
12.3 | Conection 2" & 1 1/2" ACME Nuts, Construction of Hose shall be as per guidelines given in IS 6044 Part I & II. (Test Presure- 30 Kg / cm sq | Vendor to confirm
12.4 | " Y " Type Strainer- Cast steel body construction, Flaged end type and as per ISI 9001 Size: 2" flanged end 300# | Vendor to confirm
13.0 | Fire Fighting System ( As per SMPV Rules, OISD 169 & TAC )
13.1 | Fire Extinguishers of DCP type. ( Location - 2 Nos. Main Control Room, 4 Nos.-Tank Area, 4 Nos. - Vaporiser shed, 4 Nos. - Decanting area. 2 Nos - Opposite corner inside yard) | Vendor to confirm
13.2 | Sand buckets with top cover (Location at both gates, 4 buckets mounted on each stand. Proper shed to be provided for each stand to avoid rain water) | Vendor to confirm
13.3 | 2 nosFire hydrant system as per OISD 169 norms, fire hydrants Nozzles, fire hydrant hoses, fire hose boxes of required specifiaction and quantity | Vendor to confirm
13.4 | Ring main pipe for fire hydrant and sprinkler system, nozzles on tank, unloading area, pump, compressor shed. | Vendor to confirm
13.5 | Total piping from storage water tank to yard and all necessary pumps,piping etc. | Vendor to confirm
13.6 | Make of the fire fighting system components | Vendor to confirm
13.7 | Fire water manually operated main control valve - 1 No | Vendor to confirm
13.8 | HD fire make Fire monitors - 4 Nos. (centre of each side), The length of jet shall be 45 mtr. & Fire hydrant single headed valve with 1 NO. canvas hose reels - 4 Nos. Legth of hoses should be min. 15 mtr. Hose boxes to be provided. All the system & equipment should be as per CCOE norms. The supplier shall provide - Water storage required for fire Hydrant system as per the CCOE / factory inspector rules with pumping capacity & required number of Pumps. | Vendor to confirm
13.9 | Medium Velocity Water Sprinkler system 1.Design, supply, installation & commissioning of MVWS system as per SMPV rule & CCOE approval. 2.The system should be provided at Bullet area, Vaporizer shed & decanting area. 3.The water capacity 10.5 liters / min / m2 of surface area of bullet. The pipeline sizes shall be designed to have min pressure drop in entire system. 7.0 Kg/cm2 water pressure should be maintain in the yard. 2 Nos. Remote operated valve & "Y" strainer alongwith isolation valves shall be provided for each area. Remote operated valve shall operate incase of abnormal temperature, pressure of gas.There should be two main rings for each bullets & in decanting area for each road tanker. a) Remote Operated valves (FLP) - b) Piping System - MS ERW Pipes for sprinkler system c) Medium Velocity Water Sprinklers,Accessories, valves & pipe fittings | Vendor to confirm
13.1 | Pumping station for Fire Fighting & MVWS system for LPG installation Pump kirloskar make With EEF - 1 TEFC motor - Electrical motor driven Main 171 Cum/ Hr -Head 88 m (Party to confirm suitability of pump with head an discharge based on own design) - Bronze impeller | Vendor to confirm
13.11 | Electrical motor driven Jockey Pump 70 Cum/Hr -Suitable head (Pump Model DB 65/26) | Vendor to confirm
13.12 | The rating and design of motors and switchgear shall conform to the relevant Indian Standards Specification. The Motor shall be of continous rating type and its rating shall be equivalent to the horse power required to drive the pump at 150% of its rated discharge. | Vendor to confirm
12.13 | Diesel engine driven Main pump 171 Cum/ Hr -Head 88 m- PUMP - KIRLOSKAR -, ENGINE Make - M/s. GREAVES / Ms. KIRLOSKAR OIL - Fuel storage tank & fuel pipeing in the suppliers scope. The fuel tank shall be of welded steel constructed to relevant Indian or foreign standard for Mild Steel Drums. The tank shall be mounted above the engine fuel pump to provide a gravity feed unless otherwise recommended by the manufacturers. The tank shall be fitted with an indicator showing the level of fuel in the tank. The capacity of the tank shall be sufficient to allow the engine to run on full load for 3 hours in case of Medium Velocity Water Spray Systems. The battery capacity shall be adequate for ten consecutive starts without recharging with a cold engine under full compression. | Vendor to confirm
13.14 | Capable of operating continuously on full load at the site elevation for a period of six hours. | Vendor to confirm
13.15 | Air Vessel, Pressure switch Make : Switzer, Pressure Gauge, Pressure relief valve, Air release valve , CI Strainer SS Jali, CI NRV with Bronze internals - IS approved, CI Isolation valve with Bronze internals - IS approved - PN 1.6 etc with a reputed make & as per PID. Approval for PID should be taken from BHEL. | Vendor to confirm
13.16 | MS Pipe IS 1239 - Heavy / IS 3589 - ERW class Tata,Zenith, ITC , Jindal (For above ground work), MS Pipe IS 3589 - ERW Tata, Zenith , ITC (For Below ground work with Wrapping coating 4mm thk Std Coal Tar based.*Radigraphy test - A) 10% of all the welded joints B) 50% of all field joints. | Vendor to confirm
13.17 | Seperate MCC - For electrical driven pump, Diesel engine driven pump, Auto-changeover Panel for two source operation, Motor control panel - With Std internals.With protection IP 55 - and With Auto Change over panel (In line with enclosed ref format.Formats for panel are only for ref purpose to indicate BHEL Std requirements and BHEL Electrical division approval is to be taken before supply ) | Vendor to confirm
13.18 | 6" NB Water piping from the water pump room to the fenced area, ERW 'B' Class piping coated / wrapped as per standard. | Vendor to confirm
13.19 | Construction of RCC 320CuM Storage water tank as required by CCOE Nagapur | Vendor to confirm
14.0 | Instrumentation:
14.1 | Remote opearted valves (Required quantity and size as per design) | Vendor to confirm
14.1.1 | Mode of operation of Remote Operated Valve (ROV) | Vendor to specify
14.1.2 | Make, model,material of the valves | Vendor to specify
14.1.3 | Vendor to supply required Air compressor or equivalent system for operation of ROV's and any other equipment | Vendor to Confirm
14.2 | Pressure gauges (Required quantity and size as per design) | Vendor to confirm
14.3 | Level switches (flame proof) for high LPG level alarm | Vendor to confirm
14.3.1 | Make, model, accuracy | Vendor to specify
14.4 | Level switches (flame proof) for low LPG level alarm | Vendor to confirm
14.4.1 | Make, model, accuracy | Vendor to specify
14.5 | Emergency shut - down switches | Vendor to confirm
14.6 | Gas Flow meter with Flow Computer | Vendor to confirm
14.6.1 | Model DN 80 - G 100 Turbine Meter with Mechanical Register Mounted with Electronic Volume Concverter (EVC) OR Intelligent Turbine Gas Meter Model DN 80- G100 complete with Gas inlet filter, upstream & down stream stragtness and by-pass line with isolation valve | Vendor to confirm
14.6.2 | The flow meter shall register both the line flow as also complete flow in SCMH . SCMH shall be used to manually calculate the mass of propane flowing thro' the meter | Vendor to confirm
14.7 | Crash Post:- 3 Nos X 4" NB class C Protection Crash Post to Protect the unloading area from accidental damage by tank lorry a per NEPA 58 | Vendor to confirm
14.8 | Bluck Head: Structural steel fabricated bulk head of adequate strength to withstand rigidity and pull away force of the LPG Tank Lorry and with out pulling away the valves, piping, pump and tank down stream of the unloading hose as per NFPA 58 | Vendor to confirm
15.0 | MCC / Instrumentation control panel:( For Safe Area and in NON- Flame Proof design).
15.1 | Non - flame proof, free standing, dust and vermin proof, compartmentalized, made out of CRCA sheet steel. | Vender to specify and confirm
15.2 | Panel to comprise of all switchgears, indicationg lamps, instruments, push buttons, wiring, MCB, Terminal blocks, busbars, painting etc., | Vendor to confirm
15.3 | Electrical power and control cabling with cable trays, terminations as required | Vendor to confirm
15.4 | The Apparatus and circuits in the Panels shall be so arranged as to facilitate operation and maintenance and at the same time to ensure the necessary degree of safety. | Vendor to confirm
15.5 | Provision shall be made in the panel for terminating the incoming cables as required as single line diagram. | Vendor to confirm
15.6 | Provision shall be made for permanently earthing the frames and other metal parts by two independent connection. | Vendor to confirm
15.7 | Incoming Feeder: 1 No. TP MCCB for Incomer. One set of 96 mm square Ammeter(Amps) complete with selector switch and CT's.One set of 96 MM square voltmeter ( 0-500) Complete with control fuses and selector switch. One set of phse indicating lights with control fuses . | Vendor to confirm
15.8 | Out going Feeder: Separate outgoing feeder shall be provide for the following equipments. Compressor 7.5 HP - 1 No Unloading Pump Motor 5 HP - 1 No. Spare Feeder - 1 No Vaporizer 36 Kw each - 4 No's TP MCCB, S P Preventer shall be provided. Contaractor for DOL starting , start and stop push buttons, Auxillary contactors for interlocking/ sequence of operation, contol terminals complete in all respect with interconnections. Control wiring for sequence of operation shall be inculed to complete the system/ safety shall be incorporated by providing for triping and or alrm annuncian. The wiring shall be PVC insulated aluminium conductor cable of 650/1100 volts grade confirming to IS: 1554 as required. All enclosurees , terminals, cnnection shall be explosive proof. Provision will be made for remote/ local control of all equipments. | Vendor to specify
15.9 | Electronic Main Control Panel • Mimic display of Installation indicating status of valves, Bullet in service & supply system pressure, temperature, gas level in each bullet, gas flow & consumption to shop. • All the indications shall be in digital form. • Annunciation panel for operation of all equipments indicating fault, audio / visual alarm, trip. • Operation & status of remote operated valves on water sprinkler system, gas supply line, ROV’s on bullets, compressors, and liquid filling & booster pumps, vaporizers. • Leak detection panel should be mounted seperately. It should be indicating the location of sensors installed in the yard as well as on the supply pipeline. Panel should indicate fault, audio / visual, alarm system. Other features are mentioned in the leak detection data sheet. • 2 set of Electrical drawing of control panel, list of items with manufacturer & its addresses shall be provided. | Vendor to specify
16.0 | Earthing:
16.1 | As per IS 3043 from to independent earthing pits | Vendor to confirm
16.2 | Earth strips of required size for tank, unloading pump, compressors, vapourisers, MCC and other electrical items | Vendor to confirm
16.3 | Copper jumpers for all LPG pipeline flanges | Vendor to confirm
17.0 | Hardware items: | Vendor to confirm
17.1 | Flanges, bends, tees, reducers, gaskets, nuts, bolts etc., required in LPG and water piping system | Vendor to confirm
18.0 | Painting | Vendor to confirm
18.1 | Anti corrosive primer painting of tanks as per code, pipelines, unloading pump, compressor, Vaporizer, Regulating Station, Valves and finish paint in different colours as per colour code for vapour and liquid lines. | Vendor to confirm
18.2 | HAZARD & WARNING BOARDS - • Displays at locations as required by BHEL • License board to be displayed at yard & control room. • Displays board’s viz. operating instructions at decanting area, vaporizer shed, bullet area, specification of equipments, layout & PID drawings, visual control boards etc. • Safety instructions like "No Smoking" boards, "Do not run in the yard", "Switch OFF Mobile Phones"etc. Operating Instructions, equipment Nos. & details in pump house. | Vendor to confirm
18.3 | Fabrication of walkway / railing / cross over * Fabrication of maintenance platform (lengthwise) on each bullet with railing. Walkway size should be min. 600 mm.* Common walkway (width wise) & flat plate ladder over bullets from four sides.* 1 mtr width Crossover with railing over the pipeline wherever required. * Safety railing at decanting area, main road tanker parking area (while decanting) , Maintenance platform for MVWS system ROV's, railing for air receiver, Hot water generator area, etc. One No. Maintenance platform with railing for ROV's & by pass alongwith staircase at shop entrance to be provided. Large size pipeline will be installed in pump house, to cross this pipeline staircase, maintenance platforms, should provided by supplier. | Vendor to confirm
18.4 | Miscellaneous: - Providing FLP lighting with FLP fittings inside LPG installation considering night decanting, pump / vaporiser / decanting area / Tank area /pump house etc. Considered total illumination level 35 Lux of LPG installation. Halogens / High mast considered.Constuction of sheds for Liquid filling Pump, Decating and Vapour recovery compressor & Vaporisers stations. | Vendor to confirm
18.5 | Chain pulley block- Make - M/s. Consolidated / Reputed . Supply & Erection of suitable capacity non spark proof chain pulley block inside vaporiser shed. Travel span of chain pulley block throughout the vaporiser shed for pump, compressor liquid trap & vaporiser. | Vendor to confirm
18.6 | Supplier should provide following tool kits & safety gadgets: - Make - Reputed make, *Non sparking Tool kit - open end spanner, ring spanner, pliers, pipe wrenches, hammers, screw drivers etc - 2 Set. *Safety gadgets - SCBA suit, Oxygen Masks- 2 Nos, fire suit, face shield -2 Nos. | Vendor to confirm
18.7 | Supply & errection, installation of wind sock at Proper location as per safety requirement. | Vendor to confirm
18.9 | 2 M High Industrial Chain link,4"X4" fencing with 2 Nos. Gates, wicket gate etc. | Vendor to confirm
19.0 | Installation of LPG/Propane distribution pipeline outside yard:HY/M&S/GS/LPG HEADER PIPE LINE/ 01
19.1 | Installation of LPG/Propane distribution pipeline on existing trestle, size 4"(100 mm) NB x sch.40 with necessary clamps, welding and painting with one coat of red oxide paint and two coats of synthetic enamel paint. This line to be laid from LPG storage yard upto all Production blocks. Required pipes shall be supplied by BHEL free of cost in standard length. All the remaining required materials are in the scope of vendor. | 1800 RM for main Distributor Header
19.2 | Installation of LPG/Propane distribution pipeline on existing trestle, size 2 1/2 "(62.5 mm) NB x sch. 40 with necessary clamps, welding and painting with one coat of red oxide paint and two coats of synthetic enamel paint. This line to be laid from LPG storage header at sr.no.19.1 above and upto various Production blocks. Required pipes shall be supplied by BHEL free of cost in standard length. All the remaining required materials are in the scope of vendor. | 850 RM for 02 block, for Block 04 and for Block 06
19.3 | Installation of LPG/Propane distribution pipeline on existing trestle and structure inside block 04 & 05 with necessay support, size 2"(50 mm) NB x Sch.40 with necessary clamps, welding and painting with one coat of red oxide paint and two coats of synthetic enamel paint. This line to be laid as sub distrubution line in each product block. Required pipes shall be supplied by BHEL free of cost in standard length.All the remaining required materials are in the scope of vendor. | 2500 RM for 02 Block, for Block 04 & 360 RM for Block 05
19.4 | Installation of LPG/Propane distribution pipeline on the trestle and steel columns inside block 08, line size 1.5" NB x sch. 40 with necessary clamps, welding and painting with one coat of red oxide paint and two coats of synthetic enamel paint. Required pipes shall be supplied by BHEL free of cost in standard length. All the remaining required materials are in the scope of vendor. | 225 RM for Block 08
19.5 | Installation of LPG/Propane Distribution pipe on existing trestles and steel columns inside various blocks, 1" NB x Sch.40 with necessary supports and clamps, welding and painting with one coat of red oxide paint and two coats of synthetic enamel paint. Required pipes shall be supplied by BHEL free of cost in standard length. All the remaining required materials are in the scope of vendor. | 5750 RM Please see attached pipeline schedule.
19.6 | Supply and installation of required Valves( 4" valves 4 nos, 2" valves 15 nos, 1/1/2 valves 2nos and 1" valves 5 nos),bends,elbows, flanges, metallic gaskets of various sizes as required for for the installation of the above pipelines. | Pls see Tender SLD and pipeline schedule
19.7 | Installation of 125 nos. Downcomers of 1" pipe and 6 mts drop length with 1" ball valve with each downcomer on existing trestles and steel columns inside various blocks, 1" NB x Sch.40 with necessary supports and clamps, welding and painting with one coat of red oxide paint and two coats of synthetic enamel paint. Required pipes shall be supplied by BHEL free of cost in standard length. All the remaining required materials are in the scope of vendor. | Vendor to confirm
19.8 | Erection and painting of Pre-fabricated trestles that support the LPG/Propane pipelines( from LPG /PropaneYard to exisiting producer gas plant approximaately 100mts ). The trestles will be of 7.5m in height and fabricated out of M.S. pipes. The foundation for the trestle including the bolts and fabrication of trestle are in the scope of BHEL. The trestles to be painted with one coat of red oxide paint and two coats of synthetic enamel paint. Paint in the scope of vendor. | Vendor to confirm
20.0 | Control elements, Instruments and gauges:
20.1 | Supply and installation of safety control / isolation valves, flange type non return valves in the distribution header lines for safety and maintenance purpose as per safety norms. Details and quantity as per design to be furnished in the offer. | Vendor to confirm
20.2 | Minimum the following materials to be supplied by vender for Header ppe line . 1). 4" NB Ball Valve - 5 Nos 2). 2.1/2" NB Ball Valve - 6 Nos 3). 2" NB Ball Valve - 12 Nos 4). 1 1/2" NB Ball Valve - 5 Nos 5). 1" NB Ball Valve -200 Nos( Including down comer requirement) 6). Flame Arrestor 4" NB - 2 Nos 7). 4" NB Back pressure Check valve - 2 Nos 8). 4" NB Liquid Trap with Gas Desludger -4 Nos 9). 2 1/2" NB Liquid Trap with Gas Desludger -2 Nos 10). 2" NB Liquid Trap with Gas Desludger -4 Nos | Vendor to confirm and specify
20.3 | Supply and installation of Pressure gauges with isolation valves and end fittings at suitable locations in the pipeline. Specification and make to be furnished in the offer. | Vendor to specify
20.4 | Supply of Structural Support (per Kg) With necessary flanges, bends and elbows tees, pipeline brackets, U clamps, nuts, bolts and gaskets , safety fitting and traps as required any other which are not mentioned which are required laying of pipeline on existing support structure | Vendor to specify
21 | Design, Erection and commissioning:
21.1 | Approval and licence from CCOE, Nagpur (Liason services) | Vendor to confirm
21.2 | Preparation of layout drawings for storage yard showing the location of various items / P.I. diagram / civil design and drawings | Vendor to confirm
21.3 | Preparation of calibration chart on the basis of tank capacity for liquid level measurement | Vendor to confirm
21.4 | Drawing for vapouriser, Compressor and pump sheds | Vendor to confirm
21.5 | Plan of surrounding facilities as per SMPV (U) Rules | Vendor to confirm
21.6 | Design calculation for all equipments | Vendor to confirm
21.7 | Design of safety / control elements in the LPG/Propane distribution system meeting the safety norms. | Vendor to confirm
21.8 | Third party inspection certificate for LPG/Propane tanks, Safety Fittings | Vendor to confirm
21.9 | Erection of complete system comprising LPG/Propane Tanks, vaporisers, pump, compressor, Piping & Valves, Instrumentation / Electrical systems and all other Items included in completion of system within yard. | Vendor to confirm
21.10 | The vendor should arrange necessary equipments, tools to carry out the erection and commisssioning. If necessary welding machine and cutogen torch to carry out welding and cutting operation. | Vendor to confirm
21.11 | Conducting leak test in the LPG/Propane disdtribution system pipelines in accordance with the provisions made in IS: 6044 part II. | Vendor to confirm
21.12 | Complete civil works with in the yard and Fire Water Storage Tank , fencut drg. as approved layout. | Vendor to confirm
21.13 | Construction of Sheds for vapouriser, pumps,compressor and MCC room. | Vendor to confirm
21.14 | Flood lighting of the fenced area. | Vendor to confirm
21.15 | Required crane facility with lifting tackles. | Vender to inform
21.16 | Statutory fees payable to Explosives authorities towards drawing approval and final licencing fees on behaf of BHEL. | Vendor to confirm
21.17 | Obtaining NOC from the local Govt. / administration on behaf of BHEL | Vendor to confirm
21.18 | Inspection by competent person and issuance of safety certificate | Vendor to confirm
21.19 | Commissioning service and handing over | Vendor to confirm
21.2 | Training of personnel on operation and maintenance | Vendor to confirm
21.21 | Design and Construction of RCC water tank of 320 CuM required for fire fighting system as requred by CCOE. | Vendor to inform details
21.22 | PCC Flooring, with side walls as per layout drg./CCOE requirements/SMPV Rules | Vendor to confirm
21.23 | 2 M High Industrial Chain link,4"X4" fencing with 2 Nos. Gates, wicket gate etc. | Vendor to confirm
21.24 | Bulk Head & Crash Post as per layout drg. | Vendor to confirm
21.25 | Internal service Road For Tanker Platform as per drg. | Vendor to confirm
21.26 | All civil works required for outside Piping | Vendor to confirm
21.27 | Compressed air/ Nitrogen required for inside LPG/PROPANE Yard for ROVs and any other use supplier scope only. | Vendor to confirm
21.28 | Vendors are requested to visit the site before quoting for supply, installation & commissioning of the LPG gas installation. | Vendor
22.0 | BHEL Scope:
22.1 | Supply Input power to power distribution board ( non flameproof) | Vendor to note
22.2 | Free electricity and water for erection purpose. | Vendor to note
22.3 | Required quantity of Water supply for testing | Vendor to note
23.0 | Qualifying conditions:
23.1 | The Vendor should be approved as ALDS Installer by the Department of Explosives, Government of India or an experience & established Installer of Bulk LPG/PROPANE Systems , which are approved by CCOE. | Vendor to confirm and furnish details.
23.2 | The bidder/vendor shall have a minimum of FIVE Years of continuous experience in the field of Design, supply, erection, testing and commissioning of the complete LPG/Propane gas installation of capacity of 2X 20 Tons or 40 Tons above LPG/Propane Installation (on the date of opening of tender) and such installation is presently working satisfactorily for more than one year after commissioning (on the date of opening tender), should quote | Vendor to confirm
23.3 | Performance certificate from the customers regarding satisfactory performance of installation supplied to them in attached format to be enclosed along with technical offer. | Vendor to confirm
23.4 | BHEL reserves the right to verify the information provided by Bidder/vendor. Incase the information provided by Bidder/Vendor is found to be false / incorrect the offer shall be rejected. | Vendor to confirm
23.5 | The Bidder/Vendor to furnish reference list of customer, with full address, details of contract person, where similar system or Higher rating has been supplied in the past. | Vendor to confirm
23.6 | The LPG/Propane installation shall be of Above Ground Storage type. | Vendor to confirm
23.7 | The vendors are requested to quote their offer for Design, supply, erection, testing & commissioning of the complete LPG/Propane gas installation duly certified by CCOE, Nagpur on turn key basis. | Vendor to confirm
24 | The make of the items wherever not specified shall correspond as follows: - a) LPG/Propane Storage Tank (Above Ground) : IS-2825 with 2 MH, each 500 mm b) Cathodic Protection System for A/G : Raychem/ CCOE approved / UG Storage Tanks Manufacturer c) Safety Fittings : CCOE approved manufacturer d) Decanting Pump LPG : Blackmer, USA/ Corken, USA e) Compressor Bulk Plant LPG : Blackmer, USA/ Corken, USA f) Vaporizer LPG : CCOE approved Makes only g) Pipe/Pipe Fitting : Tata/ Jindal / MSL/P.K.Forging/ Priya Engg./Equivalaent h) Valves : Flowchem/Audco/BDK/Equivalaent i) Rochester Gauges : Rochester, Belgium/USA j) High Level Switch : Bliss Anand/ Pune Techtral/Equivalaent k) High Pr. Switch : Switzer l) ROV : Flow Chem/ BDK/ Audco/Equivalaent m) Pressure Regulators 1st Stage suitable for : Elster Jeavons/ Fisher/Elster GmbH/ Min. 21 KCSG Pr. Comap/ Nirmal n) Decanting Hoses : Senior Flexonics/ Equivalent o) Liquid & Gas Flow Indicators : OGPE Design/ Process Equipment make Chemical Ind. Engrs./Equivalaent p) DCP Extinguisher /Bucket : Minimax/Equivalent q) MCC : Vidut Control/ Pryaas/Milstone /Equivalaent r) Power & Control Cables : Skytone/Gem/Grandlay/Gouster./Lap cable s) Demister/ Filtaire : Established design/ Proprietary t) Pressure / Temp. Gauges : Waree/ H.Guru/Equivalaent u) Electric Motors : Siemens/Bharat Bijee/Crompton
| Note. 1) Please note that the offered system shall be operative on both the gases; LPG and Propane. 2) Before quoting for above, new vendor can visit our unit to understand the requirement of the facility and quote accordingly. Vendor's responsibility is to give total Detailed Project Report (DPR) which is required for replacement of Producer Gas system with LPG/ Propane system. | Vendor to specify

## HY M&S AMC 2009
Annual Contract for Operation & Maintenance of LPG/PROPANE Installation at LPG Yard & LPG/PROPANE Distribution pipe line of BHEL, R.C.Puram HY:M&S:AMC:2009
Sl.No. | Description of Item | Specified & To be confirmed | Offered | Remarks
A | PURPOSE | Annual Contract for Operation & Maintenance of LPG/PROPANE Installation at LPG/PROPANE Yard & Distribution pipe line of BHEL, R.C.Puram
B | Scope of supply | To Operate & Maintenance of the LPG/PROPANE installation & LPG/PROPANE Distribution system to all production shops at BHEL, R.C.Puram for three years with Comprehensive maintenance.
1 | Operational Functions | Vendor to Confirm
1.1 | For the operation of the system , the following aspects shall be covered | Vendor to Confirm
1.2 | To supply LPG/PROPANE gas to the various users from the stock of LPG/PROPANE installation for 24 Hours, all 365 days. | Vendor to Confirm
1.3 | Safety of operation: The following Safety precautions shall be taken: 1. All safetuy Precautions as are required as per the SMPV(U) Rules. 2. No Hazardous materials shall be alowed in the installation. 3. Safety gadgets shall be used during the operation. 4. The operators shall be trained and shall undergo refresher training at least once in a year. | Vendor to Confirm Vendor to Confirm Vendor to Confirm Vendor to Confirm
1.4 | To check & record stock of LPG/PROPANE every day morning, at a fixed time, of every individual tank and inform to stores. | Vendor to Confirm
1.5 | To maintain the cumulative readings of LPG/PROPANE consumption for various users Control the flow rate, vapour temperature of LPG supplying to the shops. | Vendor to Confirm
1.6 | To maintain the proper stock of LPG/PROPANE, storage tanks in rotation. As per the stock position to avoid interruptions in vapour supply | Vendor to Confirm
1.7 | Type of compressor - Integrally Geared Centrifugal | Vendor to specify
1.8 | Controlling, Checking & recording of line vapour pressure, Hourly. | Vendor to specify
1.9 | Maintaining the required LPG/PROPANE pressure by operating suitably vaporizers. | Vendor to specify
1.1 | Maintaining the required LPG/PROPANE pressure by operating suitably vaporizers. | Vendor to specify
1.11 | Checking & recording of pressure & temperature of the tanks and as well as Vapourisers. | Vendor to specify
1.12 | Water sprinkler system is to be operated & periodical check up as and whenever required. | Vendor to confirm
1.13 | Ensuring the smooth LPG supply and attending any malfunctioning of vaporisors. | Vendor to confirm
1.14 | While unloading the LPG/PROPANE from outsides Tankers, Recording the initial & final stock readings of the LPG/PROPANE tankers, & to ensure entire LPG/PROPANE quantity is transferred in our bullets. | Vendor to specify
1.15 | Decanting of LPG/PROPANE tankers as per the safety norms & checking with soap solution for leakage & also with explosive meter while decanting process. | Vendor to confirm
1.16 | To ensure that the tanker is completely emptied while decanting before the departure of the tankers, and to obtain confirmation with MPL & PUR personnel | Vendor
1.17 | Scope of the contract is operation & maintenance of LPG/PROPANE supply from the bullet up to the entry of the various users. | Vendor
2 | MECHANICAL | Vendor
2.1 | Periodical maintenance / cleaning of valves & replacement of the same if necessary. | Vendor to specify
2.2 | Changing Valve Gaskets. | Vendor to specify
| Replacement of any mechanical parts/spares if necessary of Water pumps of Vaporizers. | Vendor to confirm
2.4 | Periodical maintenance / cleaning of LPG decanting & water recirculation pumps. | Vendor to confirm
2.5 | Periodical cleaning of Vaporizers. | Vendor to specify
2.6 | Periodical maintenance & cleaning of Pressure regulators, Liquid traps & Strainers on LPG/PROPANE - liquid, Vapour & water lines. | Vendor to specify
2.7 | Maintenance of Water Sprinkler system & Fire hydrant system & its Water pumps. | Vendor to specify
2.8 | Periodical maintenance of ambient water recirculation of Vaporizers. | Vendor to specify
2.9 | Periodical checking functioning of LPG/PROPANE leak detectors. | Vendor to specify
2.1 | Replacement of sensors of LPG/PROPANE leak detectors. | Vendor to specify
3 | ELECTRICAL | Vendor to specify
3.1 | Maintenance of all Electrical equipment | Vendor to specify
3.2 | Replacement of relays lamps etc. in the Control Panel and to keep the control panel in good working conditioning. | Vendor to specify
3.3 | Periodical checking of the ROV Function & Terminals of Solenoid Switches. | Vendor to specify
3.4 | Checking of limit switches of different ROV’s. | Vendor to specify
3.5 | Periodical servicing of solenoids valves of vaporizers & ROV’s | Vendor to specify
3.6 | Cam adjustment of different ROV’s for proper indication, on control panel. | Vendor to specify
3.7 | Replacement of Indication lamps, bulbs, switches, fuses, etc. in the Control panel. | Vendor to specify
3.8 | Weekly checking of all “Auto Controls “& Display on Display Panel in Control Room. | Vendor to specify
3.9 | Maintenance of the Control Panel installed in Control Room. | Vendor to specify
4 | MISCELLENEOUS, HOUSE KEEPING, RECORD TO BE MAINTAINED | Vendor to specify
4.1 | Daily Log Book should be maintained for the operation of pumps & vaporizer in the formats approved by BHEL. A monthly-summarized report Indicating salient points to be submitted. | Vendor to specify
4.2 | Daily logbook should be maintained to note down the shift wise activities.
4.3 | Preventive maintenance schedules other than above mentioned if found necessary | Vendor to specify
4.4 | Monthly work schedule & Monthly narrative report to be submitted to BHEL every month. | Vendor to specify
4.5 | Party has to ensure the cleanliness of the equipment’s inside the yard including tanks, | Vendor to specify
4.6 | Painting of different display boards related to LPG/PROPANE installation to be prepared by your people. (Consumables like Paint, brush, thinner will be provided by VENDOR.) | Vendor to specify
4.7 | Party’s staff should be trained and have adequate knowledge to Act on emergencies. In addition, to handle CO2/DCP Fire Extinguishers & Fire Monitors. | Vendor to specify
4.8 | Periodical painting of the equipments viz. Vapourisors, Pump, Water circulation Pumps Flow meter etc. should be carried out (Consumables like Paint, Cloth etc. will be provided by BHEL). | Vendor to specify
ROUTINE CHECKS AND RECORD KEEPING
5 | HOURLY ROUTINE CHECK UP
5.1 | Tank Pressure. | Vendor to specify
5.2 | Tank Temperature | Vendor to specify
5.3 | Pressure before regulator & after regulator | Vendor to specify
5.4 | Liquid line pressure. | Vendor to specify
5.5 | Flow rate of vapour. | Vendor to specify
5.6 | Vapour temperature | Vendor to specify
5.7 | Water pressure. | Vendor to specify
5.8 | Hydrant line pressure | Vendor to specify
5.9 | Compressed Air Pressure. | Vendor to specify
5.1 | Ambient Temperature
6 | DAILY CHECK UP | Vendor to specify
6.1 | To check the operation of ROV’S for LPG/PROPANE Installation. | Vendor to specify
6.2 | To check with Explosion Meter for leakage inside yard, if any rectify it. | Vendor to specify
6.3 | To check the stock level in the bullets. | Vendor to specify
6.4 | To check the water level in water storage tank. | Vendor to specify
6.5 | Water level in vaporizers | Vendor to specify
| PREVENTIVE MAINTENANCE SCHEDULE | Vendor to specify
7 | FORTNIGHTLY MAINTENANCE
7.1 | To drain the moisture from storage tanks
7.2 | Evacuate liquid if any from the liquid traps | Vendor to specify
7.3 | To check the setting of Thermostats | Vendor to specify
7.4 | To check the setting of Pressure Regulators | Vendor to specify
7.5 | To Check The Setting of flushing valve | Vendor to specify
7.6 | To check the Tension of ‘V’ Belts of pumps | Vendor to specify
7.8 | To check the tightness of Pulleys of pumps | Vendor to specify
7.9 | To check the condition of Vaporizers | Vendor to specify
7.1 | Change over of water recirculation pump & strainer servicing | Vendor to specify
7.11 | To check the operation of sprinklers & fire Hydrants & blockage of Nozzles | Vendor to specify
7.12 | To check & rectify for leakage of the joints on tanks. i) Inlet ii) Outlet iii) Manhole cover iv) Safety Valve. | Vendor to specify
7.13 | To check the function of pressure regulators. | Vendor to specify
7.14 | Cleaning of the filter/strainer in the vapour eliniator of LPG/PROPANE Dispenser | Vendor to specify
7.15 | Checking Temperature setting of the LPG vapouriser. | Vendor to specify
7.16 | Checkingthe present function of the LPG Vapouriser | Vendor to specify
7.17 | Checking Low Flow Rate cutout of the LPG Vapouriser. | Vendor to specify
7.18 | Cheking level Monitoring system and alarms | Vendor to specify
7.19 | Leak test of all the hydraulic joints of the LPG Vapouriser and the total piping system. | Vendor to specify
7.2 | Visual checking of the LPG piping both above ground and in trenches. | Vendor to specify
7.21 | Pneumatic Circuit air line to be checked for any Kinks/Leaks etc. | Vendor to specify
7.22 | Function of the ROV's and lubricating of the actuators. | Vendor to specify
7.23 | Condition of the electrical cables. | Vendor to specify
7.24 | Checking of the condition of the presure relif valve, temperature relif valves provided on the LPG tank and piping. | Vendor to specify
8 | MONTHLY MAINTENANCE | Vendor to specify
8.1 | To check the function of Flushing valve | Vendor to specify
8.2 | To check the functioning of pressure gauges. | Vendor to specify
8.3 | To check the entire ball valves | Vendor to specify
8.4 | To check all the liquid lines from Tank to Vaporizers & Tank to Decanting Area. | Vendor to specify
8.5 | To check the earthing joints & jumpers on liquid & vapour lines. | Vendor to specify
8.6 | To check the foundation bolts of Pumps. | Vendor to specify
8.7 | To check the earthing resistance & record should be maintained (To maintain earth resistance value below 0.5-ohm necessary watering shall be done.) | Vendor to specify
8.8 | Check the Safety Measures at Yard & Control Room. | Vendor to specify
8.9 | Control Panel in Control Room Operation & Maintenance Monthly report to be made & signed by BHEL. | Vendor to specify
9 | QUARTERLY
9.1 | To provide labour assistance for Hydraulic Testing of Safety valves & hoses.(Certification will be obtained through Competent Authority. Deputed by our Safety Dept.) | Vendor to specify
9.2 | Checking, Setting & Calibration of Pressure Switches & Pressure gauges Temperature Switches | Vendor to specify
9.3 | Overhauling of vapourisors, & Pumps. (Period may be decided base on condition.) | Vendor to specify
10 | ATTENDING THE BREAK DOWN / REPAIRS
10.1 | All equipments in the yard and LPG /Propane distribution system to be maintained and repaired by the vendor. Supply and replacement of all defective components are in the scope of Vendor only. Insurance and Emergency spares should stocked at BHEL works by Vendor. | Vendor to specify
10.2 | Operation and Maintenance contract comprises of following equipment and with its accessories of LPG/PROPANE Yard & LPG/PROPANE Distribution system. | Vendor to specify
10.3 | LPG/PROPANE Storage Tanks. 2 nos with its accessories. | Vendor to specify
10.4 | LPG/PROPANE Unloading Vapour recovery Compressor and its accessories. | Vendor to specify
10.5 | LPG/PROPANE uloading Decanting Pumps | Vendor to specify
10.6 | Vaporiser 4 nos. | Vendor to specify
10.7 | Water recirculation pumps, Electrical, Deisel pump and Jock pump. | Vendor to specify
10.8 | Flushing valve | Vendor to specify
10.9 | Fire hydrant pump | Vendor to specify
10.1 | Regulators | Vendor to specify
10.11 | ROV’S | Vendor to specify
10.12 | NRV’s | Vendor to specify
10.13 | Solenoid valve | Vendor to specify
10.14 | Water Flow Indicators | Vendor to specify
10.15 | Safety Valves | Vendor to specify
10.16 | Pressure switch | Vendor to specify
10.17 | Thermostat | Vendor to specify
10.18 | Flow meter | Vendor to specify
10.19 | Ball Valves | Vendor to specify
10.2 | ROV’S with Ball Valves | Vendor to specify
10.21 | Fixed Level Gauges | Vendor to specify
10.22 | Roto Gauges | Vendor to specify
10.23 | Safety Valves | Vendor to specify
10.24 | Sprinkler Nozzles | Vendor to specify
10.25 | Excess flow valves | Vendor to specify
10.26 | Gauges | Vendor to specify
10.27 | Strainers | Vendor to specify
10.28 | Belts | Vendor to specify
11 | CONSUMABLES
11.1 | The fpllowing consumables which required for Operation & Comprehensive Maintenance shall be in the scope of Vendor | Vendor to Confirm
11.2 | All 'O' Rings | Vendor to Confirm
11.3 | All Gaskets | Vendor to Confirm
11.4 | All washers | Vendor to Confirm
11.5 | Studs & Nuts | Vendor to Confirm
11.6 | Earthing wire | Vendor to Confirm
11.7 | Contactors | Vendor to Confirm
11.8 | Relays | Vendor to Confirm
11.9 | Earthing Jumpers | Vendor to Confirm
11.1 | All emergency/ insurance spare for all equipment should available at site. | Vendor to Confirm
12 | SATUTORY OBLIGATIONS
12.1 | The following statutory obligations shall be under the scope of the Vendor. | Vendor to Confirm
12.2 | Licence fees payable, but these fees shall be paid by the company . | Vendor to Confirm
12.3 | Any other obligations to the company, the vendor shall assist the company. | Vendor to Confirm
13 | Administrative Functions
13.1 | Contract Period: For Three years | Vendor to Confirm
13.2
13.3 | Terms of Payment
13.4 | a. Monthly Bill should be submitted in triplicate after satisfactory completion of the work. | Vendor to specify
13.5 | b. Payments will be released against bills certified by BHEL. | Vendor to specify
13.6 | Shift wise manpower expected at site round the clock , all the days of the year | Vendor to specify
13.7 | A- Shift , Two operators, 1 supervisor | Vendor to specify
13.8 | B- Shift , Two operators | Vendor to specify
13.9 | C- Shift , Two operators | Vendor to specify
13.1 | In - charge of Plant 1 person
13.11 | Operatives Reliever 1 (Installation should not be kept unmanned any Time | Vendor to specify
13.12 | Operatives: - Should have qualification min ITI / NCVT Mechanic | Vendor to specify
13.13 | Supervisors: - Minimum qualified as Diploma in Mechanical / Chemical Engineering. (Preferably one Supervisor should have Mechanical background) | Vendor to specify
13.14 | It is also expected that staff and operatives at LPG/PROPANE yard /control room should have knowledge and background about LPG/PROPANE handling, maintenance and precautions. Knowledge about Fire fighting is also essential. | Vendor to specify
14 | TRAINING
14.1 | Repetitive training should be given to all the operating staff in respect of | Vendor to specify
14.2 | Operation of ROVS | Vendor to specify
14.3 | Operation of sprinkler system. | Vendor to specify
14.4 | Mock Trial. | Vendor to specify
14.5 | Decanting process & record should be maintained. | Vendor to specify
14.6 | Disaster control plan | Vendor to specify
14.7 | Safety while handling liquid LPG/PROPANE. | Vendor to specify
15 | SAFETY | Vendor to specify
15.1 | All safety rules/ Precautions are to be taken by the contractor. Safety rules are available at our office for reference. | Vendor to specify
15.2 | The rules of CCE, Factories Inspectorate and recommendation of TRMS & Company safety rules would be the guiding factors for ensuring the safety. | Vendor to specify
15.3 | A senior person would be available at site during the inspections/planned visits to the installation by the Government | Vendor to specify
16 | OBLIGATIONS OF THE CONTRACTOR | Vendor to specify
16.1 | Price Price quoted should be firm during contract period. Contractor should take care while quoting unit rates: contractor labour rate comprising of daily unit rate consisting of daily wage rate, bonus, leave wage, leaves, PF&ESI contributions, uniform, allowance per day, DA future increase. Service Tax: The tenderer should bring out service tax is applicable or not applicable in the opposite box. If not optioned , offer will be treated as nil taxes, If service tax is applicable - credits availed by BHEL | Vendor to Confirm
16.2 | The agency is responsible for all the statutory requirements & documentations for ESI / PF etc as per prevailing Government Rules / Labour Rules. Any amount payable by BHEL on account of these requirements shall be recovered from contractors bills / deposits. | Vendor to Confirm
16.3 | Payment Terms: Monthly Payment on submission of bill with contracting officer certification. Bill should be recorded in measurement book with details of work carried out. Release of bill payments will take minimum 30/ 45 days. | Vendor to Confirm
16.4 | If the agency fails to engage staff as per the scope and unable to run the LPG /Propane Yard as per the requirement intimated by In charge a penalty of RS. 5000.00 per shift will be imposed, if the reasons for failure of shift operation are attributable to the contractor | Vendor to Confirm
16.5 | In addition to the above any penalties levied by statutory authorities for the deficient operation & maintenance of LPG yard and distribution pipe lines during the inspection, the same amount will be recovered from the Agency. | Vendor to Confirm
16.6 | Decision of BHEL Representative shall be final in the matter of inspection of work or material at any stage | Vendor to Confirm
16.7 | The contractor agrees to comply with the provision of all laws and more particularly with the contract Labour (Regulation & Abolition) Rules, 1971, the provisions of Bonus Act 1965, employees Provident Fund Act 1952, Employees State Insurance Act 1948 and such other enactment in so far as they are applicable to his workers. The contractor shall make such payments & contributions as required under the said enactment. | Vendor to Confirm
16.8 | The contractor also undertakes to comply with the provisions of Minimum wages Act, 1948 and the Minimum Wages for Engineering Industry 1974(in Maharashtra) and the rules framed there under as well as related notifications / orders /rules issued by the appropriate authorities. Further, the contractor shall maintain such registers and forms prescribed under aforesaid Act and relevant rules framed thereunder. The contractor further agrees to absolve M/s BHEL for all the liabilities in regard to the contract Labour as envisaged in the aforementioned Acts & the rules there under. | Vendor to Confirm