## Pre-bid replies
PRE BID QUERIES FROM SPECIFICATION
PROJECT: 2 x 660 MW Ennore
PACKAGE: Supply and Supervision of E&C for Inert Gas Extinguishing system
ENQUIRY NO. : T7B1R10090 |  |  |  | Date: 13/07/2018
Sl. No. | Cl. No. of Tender Specification (PY51297, Rev 00) | Description | Queries By Bidder | BHEL Replies
1 | Clause No.2.7 DOC No.PY51297, Page No.3 of 46 | Bidder to note that the Purchase Order for the entire IGES system for the project shall be placed on lump sum fixed prices based as per tender specification requirements. | Lumpsum price is quoted by us on the basis of Tender Specification & Drawings. In case of any variation in Specification & Drawings, the price will be adjusted accordingly | The changes/ revisions in tender specification & input drawings which has a bearing on material quantities shall be considered on mutual agreement basis.
2 | Clause No.7.10 Erection & Commissioning Spares DOC No.PY51297, Page No.45 of 46 | Erection and Commissioning Spares | We request BHEL to provide the list of Erection & Commissioning Spares | The list shall be generated by bidder as complete engineering is in the scope of bidder.
3 | Clause No.7.13 Mandatory Spares DOC No.PY51297, Page No.8 of 46 | Mandatory Spares List | We request BHEL to provide the list of Mandatory Spares | Mandatory spares are not applicable. Bidder to quote accordingly.
4 | Clause No.7 BIDDERS SCOPE OF SUPPLY DOC No.PY51297, Page No.7 of 46 | The Inert Gas Extinguishing System (IGES) of this project shall cover the following areas which are included in bidder’s scope of supply and supervision of erection & commissioning: - Central Equipment Room (CER) - Unit Control room, C&I Engg. room, Shift, Shift Incharge room & Computer room Computer room | We are providing inert gas system for areas as per Clause No.10 "Design of IG System iv)" and which is also Red marked in Dwg. No.PE-DG-412-145-1401 Rev.02 ( CCR/CER/COMPUTER ROOM LAYOUT AT EL 17M ) | UPS/Charger room is included. Please refer "CORRIGENDUM TO TECHNICAL PURCHASE SPECIFICATION FOR SUPPLY OF INERT GAS EXTINGUISHING SYSTEM (PY51297, Rev – 00) ".
5 | Clause No.10.1 iv) Design of IGES System DOC No.PY51297, Page No.17 of 46 | The areas to be protected by inert gas extinguishing system shall be divided into the following zones (refer Annexure-10) each: Control Equipment Room-1 (CER-1) Control Equipment Room-2 (CER-2) Control Equipment Room-3 (CER-3) Control Equipment Room-4 (CER-4) Computer room Common Control Room (CCR) PADO rooms, BMS room, Server/Network room, C&I Engr room and Incharge rooms |  | UPS/Charger room is included. Please refer "CORRIGENDUM TO TECHNICAL PURCHASE SPECIFICATION FOR SUPPLY OF INERT GAS EXTINGUISHING SYSTEM (PY51297, Rev – 00) ".
6 | Clause No.21 LIST OF ANNEXURES DOC No.PY51297, Page No.45 of 46 | 8. INPUT DRAWING LIST Dwg.No.PE-DG-412-100-M004 Rev.3 ( in PDF Format ) ( UPS / CHARGER ROOM MARKED ) | We are not considering Inert Gas Extinguishing system for UPS Room, since it is not in the List of areas to be protected by Inert Gas Extinguishing system ( as per Clause No.10 Design of IG System iv) Page No.18 of 46 ). Please review & clarify | UPS/Charger room is included. Please refer "CORRIGENDUM TO TECHNICAL PURCHASE SPECIFICATION FOR SUPPLY OF INERT GAS EXTINGUISHING SYSTEM (PY51297, Rev – 00) ".
7 | Clause No.21 LIST OF ANNEXURES DOC No.PY51297, Page No.45of 46 | 8. INPUT DRAWING LIST | Kindly provide the Sectional Drawings (indicating height) of Control Rooms and other areas to be protected by Inert Gas System (along with Ceiling Void, Room void and floor void details ) | Sectional drawings are not available at this stage. Please consider a height of 7 mtrs for Control room floor and height of 3.5mtrs for UPS/charger room.
8 | Clause No.21 LIST OF ANNEXURES DOC No.PY51297, Page No.45of 46 | Sub Vendor List ( Annexure - 12 ) | Sub- Vendor list not attached. Kindly provide the same | Noted. Sub-vendor list(Annexure-12) is furnished along with pre-bid replies.For items where no definite “make/brand” is indicated, the same shall be procured only from makes & models having proven track records. Prior approval by furnishing necessary documents shall be taken during detail engineering.
9 | Clause No.10.1.3 ii),DOC No.PY51297, Page No.20 of 46 | In addition to the concentration requirement as specified, 20% of the gas quantity as computed above , shall be added to compensate for leakages and extinguishing efficiency. | Normal Leakage allowance is already considered in the agent quantity calculation as per NFPA Clause No.5.5.2.1 Hence, additional 20% leakage allowance is not required. Kindly review and clarify. | Leakage allowances as indicated in NFPA-2001 shall be considered.
10 | General | - | We request to provide 2 no Potential free contact from FDA Panel / System (Provided by others) to Gas release Panel for below areas- 1- Control Equipment Room-1 (CER-1) 2- Control Equipment Room-2 (CER-2) 3- Control Equipment Room-3 (CER-3) 4- Control Equipment Room-4 (CER-4) 5-Computer room 6- Common Control Room (CCR) 7- PADO room,PADO room Unit#1,BMS Room Unit#1,BMS Room Unit#2, Server /Network Room,C & I Engineer Room 8- Incharge Room Unit#1, Incharge Room Unit#2,Station Incharge Room | Noted. 2 nos. of potential free contacts shall be provided for actuation of inert gas extinguishing system.
11 | 5.8 | If at any stage of work, any dismantling or modification or relocation of any facilities is required to be done to complete the work in bidder's scope and which has been agreed by the Purchaser, the same shall be done by the bidder at no extra cost or time implication to the Purchaser. | Kindly note that we are Clean agent system Vendor. Any dismantling or modification or relocation of any facilities is not part of our system. We request you to give the concern team. | Noted. Bidder's understanding is correct.
12 | 7.4 | One lot of Cables including interface cables with Fire Alarm panel , Conduit and related erection hardware. | By this clause, we understood that Fire Alarm & Detection system is not in Clean agent system vendors scope. | Bidder's understanding is correct.
13 | 10.1.3 | In addition to the concentration requirement as specified, 20% of the gas quantity as computed above , shall be added to compensate for leakages and extinguishing efficiency. | Addition of 20% gas quantity will reduce the oxygen concentration percentage below 12 during the discharge of IGES clean agents, which is not recommended by NFPA-2001 (clause no. 1.5.1.3 (1)) Hence addition of 20% is not required for IGES suppression systems. | Leakage allowances as indicated in NFPA-2001 shall be considered.
14 | CCR LAYOUT | CCR/CER/COMPUTER Layout at EL 17m, Dwg no. PE-DG-412-145-I401, Rev-02 | The Elevation & Sectional details are not provided with tender documents. Kindly provide it. | Sectional drawings are not available at this stage. Please consider a height of 7 mtrs for Control room floor and height of 3.5mtrs for UPS/charger room.
15 |  |  | For estimation purpose we have considered total height of Common Control Room is 7.00m including Room void and ceiling void. | Sectional drawings are not available at this stage. Please consider a height of 7 mtrs for Control room floor and height of 3.5mtrs for UPS/charger room.
16 |  |  | We have considered PADO rooms, BMS room, Server/Network room, C&I Engr room and Incharge rooms in Common Control Room, because of Aluminum framed partial glass walls. | UPS/Charger room is included. Please refer "CORRIGENDUM TO TECHNICAL PURCHASE SPECIFICATION FOR SUPPLY OF INERT GAS EXTINGUISHING SYSTEM (PY51297, Rev – 00) ".
17 | Annx-16 | Painting Schedule. | As per this Annexure-16, We have considered Fire Services Colour as Fire Red ( IS:5, Shade:536 ) | Bidder to follow the paint schedule as per Annexure-16 furnished. The color of the paint for inert gas piping shall be finalised during detail engineering.
18 | UPS Room | UPS room proposed partitions T.G. Equipment Layout plan at El. 8.50m Dwg. No. PE-DG-412-100-M004. | As per technical specification Cl. No. 7 & Cl.no. 10.1, requirement of system for UPS Room is not mentioned. Kindly confirm if the same need to be considered or not. | UPS/Charger room is included. Please refer "CORRIGENDUM TO TECHNICAL PURCHASE SPECIFICATION FOR SUPPLY OF INERT GAS EXTINGUISHING SYSTEM (PY51297, Rev – 00) ".
19 |  | Cylinder Storage Room | The location of Cylinder storage room is not shown in drawing. Hence we have considered it at ground floor level within 10m distance of the protected area. | Inert gas cylinder storage room is indicated in the drawings. Please refer PE-DG-412-611-C035 & C036-R0-PH BLDG-ARCH PLAN AT EL(+) 0.00M (1) drawing of Annexure-10 for details.