Corrigendum to tender No. BHEL/JHS/FCX/08-09/28 dated 09/12/2008, NIT No. 5710

Name of Work : Construction of Work-shops, Allied Structures, Machine Foundations, Services & Allied Civil Works

at bhel, JHANSI (U.p.)

The following clarifications regarding specifications are issued regarding the following two items of Price Bid.

Section "A"

| Sl No. | CPWD DSR 2007 item No. | Short discription of items( Refer DSR 07 for detailed description) | Clarification regardings specification |
| --- | --- | --- | --- |
| 6. | 1.1.2/54 | Carrige of earth | Lead 1 Km |

Section "B"

| Sl No. | Item No. | Discription of items | Clarification regardings specification |
| --- | --- | --- | --- |
| 83 | Ex. - 13 | Transparent Polycarborate Sheet | Transparent Polycarbonate sheet. The section cover requirements of providing, erecting and fixing of polycarbonate sheet of approved colour and approved transparency on roof for the purpose of roof lighting. The material to be used shall not be less than 3mm thick and shall be profiled to exactly match the profile of pre quoted metal sheet to be used for general roof side cladding. Sheet shall be supplied in maximum length that can be transported and erected without causing damage the sheet, but in any case the length shall not be less than 10m materials shall be free from scratches and other surface damage. Material shall be U-V treated and shall be tested quality. Test procedure Results Flammability Self ignition ASTM 1929-3 570º C Smoke density ASTM D 2843 54% Burning extent ASTM D 635 Less than 1.0 Weathering Evaluation ASTM D 4364-84 Successful exposure to concentrated Sunlight Radiation. Colour change ASTM D 2244 Not more than 3 units after 60 months. Light transmission ASTM D 1003 Shall not decrease more than 10 points after 60 months. Shall not decrease more than 6% after 10 years. Heat exposure 300Of/25MINS No darkening effect. Water penetration ASTM E 331 No penetration. Impact ASTM E 822-81 Repels hail storm of 25 mm at Velocity of 21m/sec. Expansion/contraction Linear thermal change of 0.065 mm/m/ºC. U-V Filteration Australian Standard Transmission less no. 1067 than 0.1% Modulus of Elasticity DIN53457 24000 Kg/Sq cm INSTALLATION Sheet shall be installed in sequence and fixed to purlin with polymer quoted galvanised hexagon heated self drilling self tamping screw side lap shall be as per manufacturer specification end lap shall 225mm joints with metal sheet shall be shield with butyl- based adhesive the edge shall be shield with silicon sealamnt as per manufacturer specification and than covered with butyl- based adhesive tap. All materials and product shall confirm to the relevant standard specification IS codes ASTM and other relevant codes etc. |

The quantities of the above items remain unchanged.

The above clarifications are issued to aid / enable the contractors to understand items clearly and fill rates accordingly.

AGM (WEX)