ANNEXURE – 1 Clarification of Electrical Scope

PART 1 - SCOPE OF ELECTRICAL WORK FOR CHP & AHP PACKAGE

This electrical scope is applicable for the following packages

- Annexure-A Sno. 2,3,4,5,6,7;

- Annexure–B Sno 1,2,3,4

1.a	Power & Control Distribution battery limits for Motor feeders:

BHEL will provide power (HT/LT) from BHEL MCC/PDB located in electrical room to the vendor’s power Junction Box provided for the equipment.

Power Cabling from BHEL MCC /PDB up to Power Junction box is in BHEL scope. The design & supply of power Junction box, cabling from power JB to field, copper flexible cables (if any) & termination of all cables at power junction box, equipment etc., as required is in vendor’s scope.

Any further interconnection within the equipments supplied is also in vendor scope. Any further power distribution/generation for down line equipment in this tender is in vendor's scope. This includes generation of 110Vac, 24V dc/ac, and 240V ac etc., required for individual equipment.

All the signals as per specification and system requirement shall be wired upto respective LCS/CJB of the equipment by the bidder. Supply of the same LCS/CJB is in bidder’s scope.

1.b	Power & Control Distribution battery limits for Power feeders:

BHEL will provide power (HT/LT) from BHEL MCC/PDB located in electrical room to the vendor’s local panel provided for the equipment.

Power Cabling from BHEL MCC /PDB up to local panel is in BHEL scope. The design & supply of local panel, cabling from local panel to field , termination of all cables at local panel etc., as required is in vendor’s scope.

Any further interconnection within the equipments supplied is also in vendor scope. Any further power distribution/generation for down line equipment in this tender is in vendor's scope. This includes generation of 110Vac, 24V dc/ac, and 240V ac etc., required for individual equipment.

All the signals as per specification and system requirement shall be wired upto respective Local panel/CJB of the equipment by the bidder. Supply of the same local panel/CJB is in bidder’s scope. Requirement of any Load break isolator as applicable shall be included in bidder’s scope.

1.c	Also in addition to 1.a & 1.b above ,the following panels are included in scope of  bidder:

  - VVVF drives and all cabling from field to drives

  - Scoop coupling / Fluid coupling/ Lubrication / Hydraulic / Auxiliary panels for HT motor & crushers . BHEL will provide  power & control upto main panel only & further distribution by bidder

  - Belt watch panels (addressable type) and all cabling from field to Belt watch panels

  - PLC/Control relay panel for standalone systems like Dust extraction, DSS, AC & ventilation, Coal sampling, coal analyzer, ash handling system etc. and signal interfacing with BHEL DCS including cabling upto bidder’s CJB if these panels are located in field .Else cabling from field to panel (located in MCC building) to be considered

  - Local UPS in field if any required.

  - Local control panels, Local Control Stations, Control desk, Control Panel, etc., for equipment in bidder’s scope

  - All instruments, field switches, limit switches, safety switches such as Pull cord, Belt sway, ZSS, optical sensors, belt slip switches, chute jamming detectors, RF Switches, encoders etc.,

  - CRD , Festoon arrangement etc.,

  - Special cables as required other than power & control cables mentioned above.

  - Load break isolators

  - Any illumination required for the moving equipments shall be included in bidder’s scope.

- Earthing protection: The vendor will ensure earthing of their individual equipment/motors/instruments etc. and connect to main earth grid being laid by BHEL. BHEL earth grid will be available at a maximum distance of 20m from any equipment.  Rail earthing (if applicable) is also included in bidder’s scope. Bidder shall provide separate electrical & electronic earthing provision for the equipment as applicable.

- Cable trays & cable tray accessories : On moving machine by Bidder .Else supply shall be by BHEL .Bidder to provide BOQ

- General Points to be considered in bidders scope:

  - HT motors except HT motors for compressors shall be supplied by BHEL

  - Temperature & vibration measurement – For HT motors supplied by BHEL, temperature & vibration measurement shall be included in BHEL scope.

For HT motors supplied by bidder temperature measurement shall be supplied by bidder and vibration measurement shall be supplied by BHEL.

Bidder shall make suitable mounting arrangement for installing the vibration sensors (supplied by BHEL) on the HT motor supplied by bidder. Temperature &Vibration measurement for crushers shall be provided by bidder.

  - Bidder shall supply machine mounted auxiliary systems (with complete electrics) like dust suppression, dust extraction, AC, ventilation etc. for mobile machines as mentioned in the technical specification.

  - Coal  analyser control system with UPS.

  - A Master Clock System (MCS) shall be provided at main DCS system. Bidder shall provide necessary hardware & software for interfacing and synchronization of bidder’s PLC (if any) with the master clock system.

  - All relevant spares as required in Contract shall be supplied by vendor after approval of Spares List from Customer/consultant. Bidder shall provide all the necessary commissioning & mandatory spares, tools & tackles for the equipment supplied by bidder.

  - 415V AC Welding sockets: Supply of Welding receptacles for machine mounted equipments is in bidder’s scope.

  - Cranes/Hoists/Elevator: BHEL shall arrange Power Supply including cable up to wall mounted Local Isolator near hoist. Supply and E&C of the equipment of wall mounted Local Isolator, laying of power cable from Isolator to Bus bar/Trailing/Festoon Cables with necessary hardware. Required Statutory clearance shall be obtained for all the Cranes ,Elevators & Hoists.

PART II - SCOPE OF ELECTRICAL WORK FOR YARD MACHINES, SHIP LOADER

2.a	Power & Control Distribution battery limits:

- BHEL will provide power from 1 no Feeder from BHEL HTMCC (3.3KV board) for each of the machines (1 no for each stacker & 1 no for each reclaimer). The power will provided to the bidder’s power Junction Box / Load Break Switch located near the machine.

- Similarly BHEL will provide power from 1 no Feeder for ship loader. The power will provided to the bidder’s power Junction Box / Load Break Switch located near the machine.

- Termination of this cable in vendor’s power Junction Box / Load Break Switch is in vendor’s scope.

- Any further power distribution for down line equipment in this tender is in vendor's scope. This includes generation of 415V, 110Vac, 24V dc/ac, and 240V ac etc., required for individual equipment. Etc., This also includes JBs ,different types of cables, transformers ,MCC, UPS, cables, cable trays etc. as required for proper operation of equipment.

2.b	Signal Interface & Automation System: The signal interface with BHEL PLC/DCS shall be through both radio and Control CRD.

Regarding hardware for this signal interface, bidder may note the following:

- For Control CRD: The CRD cable shall be wired upto land mounted JB (also in bidder’s scope). The control cable from this CJB to PLC/DCS shall be by BHEL.

- For radio: The entire radio communication system including repeaters and trans-receiver at BHEL PLC/DCS end by bidders. This shall include any Wireless Planning Commission clearances required.

2.c	The coal yard management system shall be provided by the stacker/reclaimer bidder including all necessary PLC ,PC ,software, hardware etc., Suitable interface shall be provided to BHEL DCS system also

2.d	Machine mounted fire fighting ,FDA ,DSS etc., in Bidder’s scope

2.e	Implementation of Man-less operation of Yard Machines in Bidder’s scope

.