## Sheet2
Electrical Clarifications to Bidder queries for the: EOI: IS-1-15-2004-EOI-CHP/AHP (to the Coal Handling Sys.)
Sl No | Section | Sub Section | Bidder query | BHEL-ISG clarification
1 | Electrical-LS, Gyp, BA | General | Please clarify scope, terminal points to be considered for electrical and C&I pertaining limestone, gypsum & bottom ash conveying system | Please refer the attached scope matrix mentioned n Annexure-1
2 | Electrical-LS, Gyp, BA | General | Please furnish power supply, voltage levels to be considered for limestone, gypsum & bottom ash conveying system | Same as that of CHP and AHP
3 | Electrical-CHP | General | Kindly provide the technical specification for Coal Handling conveyor package including electrical and instrumentation requirement. Nothing clearly mentioned regarding safety switches, types etc. | Technical specification as mentioned in the contract document.
4 | Electrical-CHP | General | Kindly provide the scope matrix and Battery limit for coal handling conveyor package for electrical and instrumentation. | Please refer the attached scope matrix mentioned n Annexure-1
5 | Electrical-CHP | General | Motors below 160 kW(including 160 kW) is considered LT motor suitable for 415 V. | Agreed
6 | Electrical-CHP | General | For motors rating 160 kW to 1500 kW 3.3 kV is considered. In the same document is mentioned as 11 kV. Please clarify. | Motors< 1500 kW and> 160 kW shall be supplied by a 3.3 kV medium voltage system.
7 | Electrical-CHP | General | Kindly specify the scope of the same. | Please refer the attached scope matrix mentioned n Annexure-1
8 | Electrical-CHP | General | Also clarify the requirement for temperature/vibration measurement for HT/MV motors.
9 | Electrical-CHP | General | As per our understanding HT/MCC switchgear/MCC/PMCC is excluded from bidder scope. | Agreed. But for Standalone systems like Stacker/reclaimer, Ship unloader etc. it is included in bidder scope. For further clarity please refer the attached scope matrix as mentioned in Annexure-1
10 | Electrical-CHP | General | As per our understanding any type of power/control/instrumentation cable and cable carrier system is excluded from bidder scope. | Please refer the attached scope matrix mentioned n Annexure-1
11 | Electrical-CHP | General | The belt safety switches (PCS/BSS/ZSS etc.) should be addressable/non addressable type. Please specify. | Safety switches shall be addressable type shall be compatible with Profibus/Modbus protocol.
12 | Electrical-CHP | General | Requirement of flameproof instrument is envisaged or not | As per contract
13 | Electrical-CHP | General | Kindly provide the electrical requirement for Crusher and Travelling tripper. | Electrical requirement shall match the mechanical design.
14 | Electrical-CHP | General | For travelling tripper CRD/Festoon arrangement to be considered. Please clarify. | Agreed. CRD/Festoon arrangement shall be accepted. However Composite or Separate Power & Control CRD shall be decided during detail engineering.
15 | Electrical-CHP | General | Also specify whether composite trailing cable or separate flexible cables to be considered.
16 | Electrical-CHP | General | Please clarify the illumination (outdoor/indoor) scope and type of illumination system required. | Please refer the attached scope matrix mentioned n Annexure-1
17 | Electrical-CHP | General | Please clarify earthing (above ground/below ground) scope. | Please refer the attached scope matrix mentioned n Annexure-1
18 | Electrical-Compressed air | General | Motor LT and HT limitations to be considered | Motors< 1500 kW and> 160 kW shall preferably be supplied by a 3.3 kV medium voltage system. Also Supply of motor <1500kW and >160kW by 11kV medium voltage Motors <=160 kW and other electrical consumers will be supplied by the 415 V LV system.
19 | Electrical-Compressed air | General | Motor Electrical data sheet to be submitted to study the actual requirement of the Tender and their limitations | Motor shall be selected as per IEC standard defined in the contract
20 | Electrical-Compressed air | General | Motor margin to be generalized either 10% or 15% on shaft BKW, based on the same either LT or HT can be confirmed, please clarify | Motor margin shall be designed as per mechanical design philosophy
21 | Electrical-Compressed air | General | All instruments type, make and quantity will be as per manufacturer’s standards only please clarify | Follow contract technical specification
22 | Electrical-Compressed air | General | Control system technical data sheet to be submitted to study the actual requirement of the Tender and their limitations | Follow contract technical specification
23 | Electrical-Compressed air | General | Proposal for interfacing system with BHEL PLC/DCS – please elaborate the complete scope of word desired by BHEL | Necessary data exchange for safe operation,control & monitoring of system shall be interfaced by bidder to BHEL DCS.
24 | Electrical-Yard machines | 1. a) Proven reference for unmanned yard machine used earlier | Will be furnished during firm offer submission | Shall be provided along with EOI offer
25 | Electrical-Yard machines | b) Operational philosophy for:
26 | Electrical-Yard machines | · Automatic Stacking / Automatic Reclaiming from central control room | Will be furnished during firm offer submission. However, regarding Automatic Stacking/Reclaiming, we would like to have a detailed understanding of the operation & control requirements from central control room in order to propose a system which meets customer’s expectations/requirements. | Shall be provided along with EOI offer
27 | Electrical-Yard machines | · Automatic relocation to parking position from central control room
28 | Electrical-Yard machines | · Manual movement to any position from operator cabin
29 | Electrical-Yard machines | · Manual Stacking / Manual reclaiming from operator cabin
30 | Electrical-Yard machines | 2. The yard machine will be provided with control CRD (for critical signals) & radio (for other signals) .In this regard ,please provide :
31 | Electrical-Yard machines | a) Proven reference for radio system used earlier | Will be furnished during firm offer submission | Shall be provided along with EOI offer
32 | Electrical-Yard machines | b) List of signals exchanged through CRD | Will be furnished during detail engineering. However, the list will be a generalized one which can be modified as per client/project specific requirement. | Tentative list shall be submitted by bidder with EOI offer
33 | Electrical-Yard machines | 4. Proposal for anti-collision system to be executed among the machines & where the software for this will be housed | – Anti-collision system between the stackers & reclaimers under same shed can be implemented. Details of such anti-collision system will be furnished along with firm offer submission. | Shall be provided along with EOI offer
34 | Electrical-Yard machines | 5. Proposal for synchronising BHEL master Clock with PLC clock in Yard machine | Same can be provided. Details will be furnished during firm offer submission | Shall be provided along with EOI offer
35 | Electrical-Yard machines | 6. Proposal for maintaining stock inventory in the yard | System for maintaining stock inventory can be provided. Details will be furnished during firm offer submission | Shall be provided along with EOI offer
36 | Electrical-Yard machines | 8. Power feeder requirement for each yard machine | Will be furnished during firm offer submission | Tentative Load shall be submitted by bidder with EOI offer
37 | Electrical-Yard machines | work excluded | 1) land power supply cable from the land switchgear to the cable anchor junction box | Please refer the attached scope matrix mentioned n Annexure-1
2) land based PLC hardware, software and logic programming
3) all auxiliaries like fire fighting, fire detection
4) earthing of rails, including supply of necessary hardware
5) area lighting / high mast
6) man-less operation for mobile machines