## ELGI
2X660 MW Maitree
ELGI
Sl No. | Bidder's Query | BHEL's Reply dated 27.08.2016
1 | Scope of supply is limited to supply of skid mounted Oil Free compressed air systems only? | Yes
2 | FAD mentioned in RFQ is in m3/min, the same to be read as m3/min or Nm3/min. If it has to be read as Nm3/min then Avg Ambient Air Temp, Avg Ambient | Bidder to read "Minimum Discharge Volume (FAD)" as "Minimum Discharge Volume (FAD) at site conditions" at Clause No. 4.0 of Annexure-10.
3 | Discharge Pressure Mentioned is Min of 7.5 kg/cm2. | Bidder's understanding is correct
4 | Is it the gauge pressure or Absolute Pressure | Gauge pressure
5 | What is the desired Max Discharge Pressure | Above 7.5 kg/cm2
6 | What is the desired Operating Pressure | 7.0 to 7.5 Kg/cm2
7 | Motor LT and HT limitations to be considered | Electrical dept to specify
8 | Motor Electrical data sheet to be submitted to study the actual requirement of the Tender and their limitations | Electrical dept to specify
9 | Motor margin to be generalized either 10% or 15% on shaft BKW, based on the same either LT or HT can be confirmed, please clarify | Electrical dept to specify
10 | All instruments type, make and quantity will be as per manufacturer’s standards only please clarify | Electrical dept to specify
11 | Control system technical data sheet to be submitted to study the actual requirement of the Tender and their limitations | Electrical dept to specify
12 | Proposal for interfacing system with BHEL PLC/DCS – please elaborate the complete scope of word desired by BHEL | Electrical dept to specify
13 | After cooler to be part of compressor skid or external to compressor skid – please clarify | Internal/External Aftercooler shall be as per manufacturer standard

## DECO Consul
2X660 MW Maitree Project
DECO Consul
Sl No. | Bidder's Query | BHEL's Reply dated 27.08.2016
1 | For the ANNEXURE-2 LIMESTONE, GYPSUM & BOTTOM ASH CONVEYING SYSTEM, we have rich experience and qualified for the belt conveyor and pipe conveyor | Please refer Pre Qualification Criteria of the Specification, if you are meeting the same, you can qoute and submit your offer.
2 | For the ANNEXURE -08 ASH HANDLING SYSTEM, we have rich experience and qualified for the ash handling system in using our own DTS@ technology. Would it be possible to provide us the dwg version plat plan drawing which it can show the real distance for our scope of supply, also it will be grateful if possible to reconfirm the ash rate of each equipment. | Please refer Pre Qualification Criteria of the Specification (Annexure-08), if you are meeting the same, you can qoute and submit your offer. The uploaded plot plan is to the scale. Measurement can be taken. Please follow specification for the ash rate. However, the horizontal distance between 1st field of ESP of Unit 2 to Intermediate Silos is approximately 440 Mtrs. The horizontal distance between Intermediate silo to Silos near Jetty is approximately1200 Mtrs.
3 | For the ANNEXURE -09 DRY BOTTOM ASH HANDLING SYSTEM, we have rich experience and qualified for Dry bottom ash handling system in using our own technology. We were wondering if it will be probable to provide the section view of boiler which can show us the boiler throat dimensions and elevations, also for the distance from boiler CL to Silo CL, it will be grateful if possible to reconfrim the bottom ash rate and let us make a suitable and accurate quotation for you. | Please refer Pre Qualification Criteria of the Specification, if you are meeting the same, you can qoute and submit your offer. At this stage, throat dimension and elevation is not available with us. However, the tentative throat dimension for reference shall be taken as 18.4 Mtrs(L) X 1.3 Mtrs(W)and boiler ring header elevation at is 12.5 mtrs. The horizontal distance from boiler CL to Bottom Ash Intermediate Silo CL is approximately 54 Mtrs. Please follow specification for bottom ash rate.

## Megale Pneumatis
2X660 MW Maitree Project
Megale Pneumatics
A.Technical
S No | Section/Clause no | As per Tender Document | Pre Bid Queries | BHEL Reply dated 27.08.2016
1 | Section-4 | List of Encloures, Annexure-A,B,C&D | The cited Annexure were not received at our end,request you to kindly provide the same | Annexure A, B, C and D is previously uploaded. Please download the same.
2 | Section-5,CL.5 | Requirement from Bidder,item (i) Weight of equipment, oversize item list (j) Storage plan & storage space requirement (I) Dwg. list & submission schedule Item (m) Painting schedule | The cited details / documents shall be submitted during detailing | Please follow specifications and submit the data asked in the enquiry.
3 | Annexure-8, CL 3& 5.1 | Brief Scope of Work, Ash removal and recovery water system methodology | We have noted that the ash handling plant shall opt for High concentration slurry disposal system for bottom ash & fly ash and hence we are not sure about your requirement of recovery water system, please confirm about your exact requirement. | The recovery water system is provided to cater to rain water collected in the dyke.
4 | Annexure-8,CL 4 | Design Inputs | · Please provide particle size distribution for APH & Duct zone also. · Please provide us the zone wise temperature and Bulk density (volume / power / load) details to be considered for system sizing. · Please provide us the available APH, Duct & ESP hopper bottom elevation wrt. Outlet flange & FFL. If possible please provide clear details on the terminal points wrt ash handling system package as covered under Annexure - 8 | Please follow higher range of Sieve Analysis of fly ash for APH and Duct hopper ash. The hopper bottom elevation of APH, DUCT and ESP shall be at El(+) 3.5 Mtrs. FFL shall be (-) 200 MM.
5 | Annexure-8,CL 5.2 | Brief System description of ash handling system . (8140A01/FICHT-14366345- v19 BIFPCL/EPC-Main Plant / 2015/01) B4.3.4, B4.3.5,Flow diagram and Plot Plan | The cited documents / dwg. were not received at our end, request you to kindly provide the same | 1. Refer Annexure A for (8140A01/FICHT-14366345- v19 BIFPCL/EPC-Main Plant / 2015/01). 2. Annexure B for Plot Plan. 3. Annexure C for Flow Diagrams.
6 | Annexure-8,CL 7.0 | General, item 7 Erection & Commissioning of BHEL supplied items | We shall provide supervision of Erection & Commissioning and Supervision of PG Test & handing over. This is in line with Section – 5, Cl. 4, Scope of co – operation | BHEL supplied items like comprerssor, ash pipes etc. excpet the Dry bottom ash hanlding system shall be in the scope of the bidder. Follow specification.
7 | General | Delivery,Commissioning & Handing over | The EOI is silent about the requirement of completion period of the project, request you to kindly share the plant planned schedule | MM/Commercial Dept to clarify
(A) Points related to Pre Qualification requirement
8 | Annexure-8,CL 2.0 | Clause related to PQR Item (ii) 40 TPH > 500 Mtrs including Fly Storage Silo | We request you to kindly allow 40 TPH > 500 Mtr. and Fly Ash Storage Silo. For purpose of qualification, such installations in two separate plants (i.e. 40 TPH > 500 Mtr. in one plant and Fly Ash Storage Silo in a separate plant) is allowed. | Noted.
9 | Annexure-8,CL 2.0 | Clause related to PQR Item (iii) | Kindly note that all HCSD Pump suppliers (which is a specialized equipment) are not into EPC of HCSD system, they only supply the Pumps which form heart of the system and balance engineering is done by engineering companies. Thereafter, EPC companies do complete execution of the HCSD system, hence we request you to kindly modify the cited clause as requested below; “Engineering consultant for High Concentration Slurry Disposal System (HCSD) who in past have done engineering consultancy for HCSD system for selection of pipe, pump capacity for a capacity not less than 40 TPH of coal ash on dry basis for at least one plant which should have been in successful operation for at least two (2) years prior to date 22.09.2015”. | Pre Qualifiaction Criteria clearly indicates the HCSD requirment. Bidder to follow specification.

## WIER
2X660MW Maitree
WEIR
Sl No. | Bidder's Query | BHEL's Reply dated 27.08.2016
1 | We have expressed our interest in your portal already. Please advise the way forward now. Can we expect the tender enquiry from you and we can submit an offer to the extent that we can handle? | The EOI document does not call for HCSD system separately as HCSD system package is with the Ash Handling System. Please refer Pre-Qualification Criteria