A)  Specification  for Solar Street Lights for use in factory area

| S.No | Item | Type / Make | Suppliers Comments |
| --- | --- | --- | --- |
| 1 | Solar street light 14 W LED Lamp model I Beam with minimum of 1300 Light output , Auto Dusk to Dawn Operation, 4m height pole | Tata BP |  |
| 1.1 | High efficiency PV Module 12V-75W | Tata BP |  |
| 1.2 | Battery: Low maintenance tubular plate battery | 12V-60AH Tata BP |  |
| 1.3 | Autonomy | 5 Days |  |
| 1.4 | Lamp: 14 W LED Lamp, minimum 1300 Lumens STC rated output , Aluminium housing with glass/acrylic cover, Aluminum reflector. | GE/Osram/ Philips |  |
| 1.5 | Luminaire: Outdoor Aluminium luminaire with transparent glass/acrylic cover | -- |  |
| 1.6 | Electronics as below ECU with inverter & DDC | Tata BP |  |
| 1.6.1 | Solar charge controller: Auto DDC separately located inside battery box with indications Green LED-On charge, Yellow LED- Battery Low, Red LED-Battery Low Load Cut | Tata BP |  |
| 1.6.2 | LED Driver: High efficiency Constant current driver working on high frequency giving constant illumination. Operating temp: 5- 50C, Humidity: 95 % rh (N.C.) | Tata BP |  |
| 1.7 | Pole and structure: 4m GI Pole with corrosion resistant paint with module bracket . Battery Enclosure: MS | --- |  |
| 1.8 | Module mounting structure | --- |  |
| 1.9 | Battery Box | --- |  |
| 1.10 | Installation kit & manual | --- |  |
| 1.11 | Protections: - Overcharge & deep discharge disconnect - Short circuit protection for lamps - Battery reverse connection - Against discharge through array by blocking diode | --- |  |
| 1.12 | Features: - Rugged design to operate under high variations of temperature and humidity. - Automatic ON at dusk and OFF at dawn, with manual on/off switch - Insect proof luminaire - 14 m Light spread | --- |  |
| 1.13 | SCOPE: Supply comprises Lamp Pole, Battery, Battery Box, Electrolyte, Solar Module, and Module mounting structure, Luminaries, Luminaries assembly, connectivity within the system along with cables. Civil works like digging pits and concrete grouting for the pole is in vendor’s scope . The vendor has to take complete responsibility for installation and commissioning of solar street light in our premises. | ------------ |  |

B) General terms and conditions

| sl | item | type | Supplier’s comment |
| --- | --- | --- | --- |
| 2.1 | Spares : Following spare to be included in the scope : a) PV modules (make TataBP) - 1 no b) Luminaire with assembly - 3 nos. c) Electronic card - ECU with inverter & DDC - 5 nos d) Electronic card - LED Driver - 5 nos | TataBP GE/Osram/ Philips TataBP TataBP |  |
| 2.2 | THE PRICE OF SPARES TO BE QUOTED SEPERATELY AGAINST EACH ITEM. | ---- |  |
| 2.3 | The supplier shall depute their representative at least once every 3 months to check functioning of all solar street lights , Maintenance of batteries, cleaning of PV panels Free of cost. | ---- |  |
| 2.4 | All equipment shall be suitable for outdoor conditions like rain and sun for temperature variations between 5° to 50°C. | ---- |  |
| 2.5 | The equipment shall be offered for inspection before dispatch at Tata BP works, Bangalore. Only after obtaining clearance in writing the solar street lights can be shipped. 1 week prior information has to be given for deputation BHEL personnel for inspection. | ---- |  |
| 2.6 | The vendor is required to submit test certificates of PV modules, Luminaires, battery, ECU,DDC etc at the time of inspection. | -- |  |
| 2.7 | The vendor is required to submit drawings and quality plan before commencement of manufacturing. | -- |  |
| 2.8 | Bidder is required to select one of the make of items mentioned under S.No. 1.4, 2.1(b). Incase the Bidder is offering a make other than those indicated, the offer is liable for rejection. For Other supplies and spares where only one make is indicated, the bidder is required to offer only that particular make. Bidder offering other or equivalent makes is liable for rejection. | -- |  |

ECU – Electronic Charger Unit.

DDC- Dusk to Dawn Controller

Pre Qualification

- Bidder must have successfully executed atleast 2 similar work contracts of supply and installation

of solar street lights ( 11W or above) out of which 1 must be on Govt / PSU undertakings during the

last 2 years. In this respect, necessary purchase orders and performance certificates to be enclosed

along with technical bid failing which offer may not be considered for acceptance.

- In case the bidder is a distributor or dealer for any organization supplying solar street lights.

Valid proof that the bidder is distributor / dealer needs to be furnished.