PR No 6000000281 ( NIT_7940)

A)  Specification  for Solar Street Lights for use in factory area                          Rev.: 02

| S.No | Item | Type / Make | Suppliers Comments |
| --- | --- | --- | --- |
| 1 | Solar street light 14 W LED Lamp model I Beam with minimum of 1300 Light output , Auto Dusk to Dawn Operation, 4m height pole |  |  |
| 1.1 | High efficiency PV Module 12V-75W | BHEL |  |
| 1.2 | Battery: Low maintenance tubular plate battery 12V-75AH | Exide / HBL / AmarRaja |  |
| 1.3 | Autonomy | 5 Days |  |
| 1.4 | Lamp: 14 W LED Lamp, minimum 1300 Lumens STC rated output , Aluminium housing with glass/acrylic cover, Aluminum reflector. | GE/Osram/ Philips |  |
| 1.5 | Luminaire: Outdoor Aluminium luminaire with transparent glass/acrylic cover | -- |  |
| 1.6 | Electronics as below ECU with inverter & DDC | Any reputed make |  |
| 1.6.1 | Solar charge controller: Auto DDC separately located inside battery box with indications Green LED-On charge, Yellow LED- Battery Low, Red LED-Battery Low Load Cut | Any reputed make |  |
| 1.6.2 | LED Driver: High efficiency Constant current driver working on high frequency giving constant illumination. Operating temp: 5- 50C, Humidity: 95 % rh (N.C.) | Any reputed make |  |
| 1.7 | Pole and structure: 4m GI Pole with corrosion resistant paint with module bracket . Battery Enclosure: MS | --- |  |
| 1.8 | Module mounting structure | --- |  |
| 1.9 | Battery Box 20SWG,MS sheet | --- |  |
| 1.10 | Installation kit & manual | --- |  |
| 1.11 | Protections: - Overcharge & deep discharge disconnect - Short circuit protection for lamps - Battery reverse connection - Against discharge through array by blocking diode | --- |  |
| 1.12 | Features: - Rugged design to operate under high variations of temperature and humidity. - Automatic ON at dusk and OFF at dawn, with manual on/off switch - Insect proof luminaire - 14 m Light spread | --- |  |
| 1.13 | SCOPE: Supply comprises Lamp Pole, Battery, Battery Box, Electrolyte, Solar Module, and Module mounting structure, Luminaries, Luminaries assembly, connectivity within the system along with cables. Civil works like digging pits and concrete grouting for the pole is in vendor’s scope . The vendor has to take complete responsibility for installation and commissioning of solar street lights in BHEL premises. | ------------ |  |

B) General terms and conditions

| sl | item | type | Supplier’s comment |
| --- | --- | --- | --- |
| 2.1 | Spares : Following spare to be included in the scope : a) PV modules - 1 no b) Luminaire with assembly - 3 nos. c) Electronic card - ECU with inverter & DDC - 5 nos d) Electronic card - LED Driver - 5 nos | BHEL GE/Osram/ Philips Reputed make Reputed make |  |
| 2.2 | THE PRICE OF SPARES TO BE QUOTED SEPERATELY AGAINST EACH ITEM. | ---- |  |
| 2.3 | The supplier shall depute their representative at least once every 3 months to check functioning of all solar street lights , Maintenance of batteries, cleaning of PV panels Free of cost. | ---- |  |
| 2.4 | All equipment shall be suitable for outdoor conditions like rain and sun for temperature variations between 5° to 50°C. | ---- |  |
| 2.5 | The equipment shall be offered for inspection before dispatch at Bidder’s works. Only after obtaining clearance in writing from BHEL , the solar street lights can be shipped. 1 week prior information has to be given for deputation BHEL personnel for inspection. | ---- |  |
| 2.6 | The vendor is required to submit test certificates of PV modules, Luminaires, battery, ECU,DDC etc at the time of inspection. | -- |  |
| 2.7 | The vendor is required to submit drawings and quality plan before commencement of manufacturing. | -- |  |
| 2.8 | Bidder is required to select one of the make of items mentioned under S.No. 1.2,1.4, 2.1(b). Incase the Bidder is offering a make other than those indicated, the offer is liable for rejection. For other supplies and spares where only one make is indicated, the bidder is required to offer only that particular make. Bidder offering other or equivalent makes is liable for rejection. | -- |  |

ECU – Electronic Charger Unit.

DDC- Dusk to Dawn Controller

Pre Qualification

- Bidder must be MNRE - Govt of India approved vendor under the category SPV Lighting Systems

( LED based ).

- The bidder must have  successfully executed atleast 2 similar work contracts of supply and installation

of solar street lights ( 11W or above) out of which 1 must be on Govt / PSU undertakings during the

last 3 years. In this respect, necessary purchase orders and performance certificates to be enclosed

along with technical bid failing which offer may not be considered for acceptance.

- In case the bidder is a distributor or dealer for any organization supplying solar street lights.

Valid proof that the bidder is distributor / dealer needs to be furnished.

- Submission of documentary evidence for pre qualification requirements  mentioned under sl no 1 to 3

is mandatory. Offers of bidders without documentary evidences will be rejected.