## BOM- Lara 2x800 MW
Enquiry No 4202600002 dt 14.01.2026 Procurement of TG Cycle Piping of IBR & Non IBR Systems for NTPC projects Annexure C- Detailed Piping System BOM (R01)
Schedule No | Project | Piping System | IBR / Non IBR | PGMA | Drawing No | Item Description | UOM | Quantity per Boiler of the project (refer Note 1) | Total Quantity for 2 Boilers | *Weight per Boiler of the project (kg) (refer Note 1) | Total Weight for 2 Boilers (kg)
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD355.6X9.53 SA106GRB | M | 4 | 4 | 325.32 | 325.32
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD219.1X6.35 SA106GRB | M | 5 | 5 | 166.55 | 166.55
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD168.3X7.11 SA106GRB | M | 5.5 | 5.5 | 155.43 | 155.43
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD88.9X5.49 SA106GRB | M | 5.5 | 5.5 | 62.095 | 62.095
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD355.6X9.53 SA234WPB | NO | 1 | 1 | 70 | 70
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 45DEG ELL OD355.6x9.53 SA234WPB | NO | 1 | 1 | 34.03 | 34.03
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 1 | 1 | 16.7 | 16.7
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 45DEG ELL OD219.1x6.35 SA234WPB | NO | 1 | 1 | 7.97 | 7.97
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 1 | 1 | 10.14 | 10.14
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 1 | 1 | 2.02 | 2.02
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 45DEG ELL OD88.9X5.49 SA234WPB | NO | 1 | 1 | 1.01 | 1.01
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PIPE OD 219.1 x 6.35 - SA106GRB | M | 60 | 60 | 1998.6 | 1998.6
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PIPE OD 219.1 x 12.7 - SA106GRC | M | 15 | 15 | 969.6 | 969.6
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PIPE DIA 114.3 X 6.02 SA106GRB | M | 1 | 1 | 16.07 | 16.07
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SUPPORT PIPE OD168.3x7.11 SA106GRB | M | 2.5 | 2.5 | 70.655 | 70.655
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 90DEG ELL OD219.1X6.35 SA234WPB | NO | 11 | 11 | 183.7 | 183.7
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 45DEG ELL OD219.1X6.35 SA234WPB | NO | 2 | 2 | 15.96 | 15.96
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 90DEG ELL OD219.1X12.7 SA234WPC | NO | 1 | 1 | 30.97 | 30.97
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 45DEG ELL OD219.1X12.7 SA234WPC | NO | 2 | 2 | 30.96 | 30.96
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW REDUCER - OD273x12.7/OD219.1x12.7 SA234WPC | NO | 1 | 1 | 13.29 | 13.29
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | FLAT END CLOSURE OD114.3X6.02 SA515GR70 | NO | 1 | 1 | 2.2 | 2.2
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW UEQT 219.1X6.35/114.3X6.02 SA234WPB | NO | 1 | 1 | 17.18 | 17.18
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW EQT 219.1X6.35 SA234WPB | NO | 1 | 1 | 19.27 | 19.27
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | ASME B16.11 SW STUB NB40 CL:6000-SA105 | NO | 2 | 2 | 2.14 | 2.14
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | ASME B16.11 SW STUB NB25 CL:6000-SA105 | NO | 2 | 2 | 1.14 | 1.14
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | TEMPERATURE STUB M33x2 L=45 OD-78 -SA105 | NO | 1 | 1 | 1.12 | 1.12
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SCREW PLUG M33 X 2-SA105 | NO | 1 | 1 | 0.8 | 0.8
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PACKING RING M33x2 | NO | 1 | 1 | 0.01 | 0.01
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | CARRIER PLATE T=8X50X80-SA515GR70 | NO | 8 | 8 | 2.009 | 2.009
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SUPPORT PIPE 168.3X7.11 SA106GRB | M | 3 | 3 | 84.78 | 84.78
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SUPPORT PLATE 10X200X200-SA515GR70 | NO | 8 | 8 | 25.12 | 25.12
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 508x9.53 - SA106 GRB | M | 15 | 15 | 1757.25 | 1757.25
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 355.6x9.53 - SA106 GRB | M | 4 | 4 | 325.2 | 325.2
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 273x9.27 - SA106 GRB | M | 40 | 40 | 2411.52 | 2411.52
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 168.3x7.11 - SA106 GRB | M | 8 | 8 | 226.096 | 226.096
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 219.1x6.35 - SA106 GRB | M | 1 | 1 | 33.31 | 33.31
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 114.3x6.02 - SA106 GRB | M | 1 | 1 | 16.0733 | 16.0733
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 3 | 3 | 420.69 | 420.69
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 45DEG ELL OD508X9.53 SA234WPB | NO | 1 | 1 | 70.07 | 70.07
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD355.6X9.53 SA234WPB | NO | 2 | 2 | 136.2 | 136.2
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD273X9.27 SA234WPB | NO | 10 | 10 | 370 | 370
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 3 | 3 | 30.42 | 30.42
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW UEQT 273X9.27/114.3x6.02 SA234WPB | NO | 1 | 1 | 34.4 | 34.4
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW UEQT 273X9.27/168.3x7.11 SA234WPB | NO | 1 | 1 | 35.46 | 35.46
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW UEQT 508X9.53/219.1x6.35 SA234WPB | NO | 1 | 1 | 120.7 | 120.7
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW EQT 273X9.27 SA234WPB | NO | 1 | 1 | 38.83 | 38.83
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW EQT 508X9.53 SA234WPB | NO | 1 | 1 | 141.95 | 141.95
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 508X9.53/273x9.27 SA234WPB | NO | 2 | 2 | 93.28 | 93.28
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 355.6X9.53/168.3x7.11 SA234WPB | NO | 1 | 1 | 18.49 | 18.49
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 406.4x9.53/355.6X9.53 SA234WPB | NO | 1 | 1 | 31.21 | 31.21
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 965X9.53/508X9.53 SA234WPB | NO | 1 | 1 | 117.84 | 117.84
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 8 | 8 | 3.44 | 3.44
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | FLAT END CLOSURE OD219.1X6.35 SA515GR70 | NO | 1 | 1 | 8.5 | 8.5
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | FLAT END CLOSURE OD114.3X6.02 SA515GR70 | NO | 1 | 1 | 2.2 | 2.2
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | CARRIER PLATE 16X120X50-SA515GR70 | NO | 8 | 8 | 7.04 | 7.04
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | CARRIER PLATE 16X80X50-SA515GR70 | NO | 8 | 8 | 3.84 | 3.84
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | LUG PLATE 16 THK 443x260 -SA515 GR70 | NO | 1 | 1 | 9.4 | 9.4
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | SUPPORT PLATE 12x500x500-SA515GR70 | NO | 4 | 4 | 94.2 | 94.2
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | SUPPORT PIPE OD 457 X 9.53 L=1000-SA106GRB | M | 1 | 1 | 105.3 | 105.3
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | ORIFICE PLATE ASSY-NB350 -SA515GR70 | NO | 1 | 1 | 30.788 | 30.788
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | SOW FLANGE NB350CL150 SA515GR70 | NO | 2 | 2 | 179.75 | 179.75
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | STUD M27 X 3 X 160 SA193B7 | NO | 12 | 12 | 8.1 | 8.1
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | NUT -M27 -2H | NO | 24 | 24 | 4.08 | 4.08
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | NON-ASBESTOS JOINTING SHEET 3.0MM | NO | 1 | 1 | 5.69 | 5.69
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | PIPE DIA 88.9 X 5.49 SA106GRB | M | 68 | 68 | 767.72 | 767.72
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 14 | 14 | 28.28 | 28.28
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | ASMEB16.9 BWLR 45DEG ELBOW OD88.9X5.49 SA234WPB | NO | 2 | 2 | 2.02 | 2.02
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | TEMP STUB M33X2; L=64 SA105 | NO | 1 | 1 | 0.72 | 0.72
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | COPPER PACKING RING M33X2 IS1972 | NO | 1 | 1 | 0.01 | 0.01
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SCREW PLUG CS (M33X2) SA105 | NO | 1 | 1 | 0.4 | 0.4
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 4 | 4 | 4.3 | 4.3
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SW STUB NB15 CL 3000 SA105 | NO | 2 | 2 | 0.546 | 0.546
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SW STUB NB40 CL3000 CS SA105 | NO | 1 | 1 | 0.75 | 0.75
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | CARRIER PLATE 16X50X80 SA515GR70 | NO | 4 | 4 | 2.01 | 2.01
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SUPPORT PIPE OD60.3X5.54 L=4000 SA106GRB | M | 4 | 4 | 29.92 | 29.92
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | PLATE 10.0 MM 1000X1000 SA515GR70 | NO | 1 | 1 | 78.5 | 78.5
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | TEMP STUB RC 1" L=64-SA105 | NO | 3 | 3 | 1.8375 | 1.8375
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SCREW PLUG RC 1" SA105 | NO | 3 | 3 | 0.525 | 0.525
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | PIPE DIA 273.0 X 9.27 SA106GRB | M | 240 | 240 | 14469.12 | 14469.12
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BRANCH PIPE OD 168.30 x 7.11 X 6500 - SA106GRB | M | 3 | 3 | 84.78 | 84.78
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BRANCH PIPE DIA 114.3 X 6.02 SA106GRB | M | 3 | 3 | 48.21 | 48.21
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW LR 90DEG ELL OD273X9.27 SA234WPB | NO | 44 | 44 | 1587.52 | 1587.52
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW RED 355.6X9.53/273X9.27 SA234WPB | NO | 1 | 1 | 23.67 | 23.67
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW UEQT 355.6X9.53/273X9.27 SA234WPB | NO | 1 | 1 | 68.37 | 68.37
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW EQT OD273X9.27 SA234WPB | NO | 4 | 4 | 168.12 | 168.12
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW UEQT 273X9.27/114.3X6.02 SA234WPB | NO | 6 | 6 | 219.24 | 219.24
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | FLAT END CLOSURE FOR OD114.3X6.02 SA515GR70 | NO | 6 | 6 | 16.2 | 16.2
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | TEMP STUB M33X2; L=64 SA105 | NO | 4 | 4 | 2.88 | 2.88
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | COPPER PACKING RING M33X2 IS1972 | NO | 4 | 4 | 0.04 | 0.04
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | SCREW PLUG CS (M33X2) SA105 | NO | 4 | 4 | 1.6 | 1.6
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | SW STUB NB25 CL3000 SA105 | NO | 2 | 2 | 1.66 | 1.66
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | FLAT END CLOSURE OD273x9.27 SA515 GR70 | NO | 2 | 2 | 34.92 | 34.92
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | CARRIER PLATE 16X50X80 SA515GR70 | NO | 8 | 8 | 4.02 | 4.02
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | SUPPORT PIPE OD219.1X8.18 L=5M SA106GRB | M | 5 | 5 | 212.7 | 212.7
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | PLATE TH 10.0X2000X2500 SA515 GR70 | NO | 1 | 1 | 392.5 | 392.5
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | TEMPERATURE STUB RC 1" L=45 CS-SA105 | NO | 3 | 3 | 1.5 | 1.5
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | PLUG R 1" CS SA105 | NO | 3 | 3 | 0.6 | 0.6
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW UEQT 273X9.27/168.3X7.11 SA234WPB | NO | 2 | 2 | 75.42 | 75.42
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | SUPPORT PIPE OD114.3X6.02 L=5M SA106GRB | NO | 5 | 5 | 80.35 | 80.35
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | FLAT END CLOSURE OD168.3x7.11 SA515 GR70 | NO | 2 | 2 | 9.3 | 9.3
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | PIPE DIA 457 X 9.53 - SA335P22 | M | 7 | 7 | 736.12 | 736.12
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | PIPE DIA 457 X 9.53 - SA335P11 | M | 1.5 | 1.5 | 157.74 | 157.74
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | PIPE DIA 457 X 9.53 - SA106 GR.B | M | 30 | 30 | 3154.8 | 3154.8
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SPARE PIPE DIA 457 X 9.53 - SA106 GR.B | M | 1 | 1 | 105.16 | 105.16
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SUPPORT PIPE OD323.9x9.53 SA335 P11 | M | 1.5 | 1.5 | 110.82 | 110.82
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SUPPORT PIPE OD406.4x12.7 SA106 GR.B | M | 3.5 | 3.5 | 431.55 | 431.55
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD457x9.53 SA234WPB | NO | 4 | 4 | 453.48 | 453.48
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD457x9.53 SA234WP22 | NO | 1 | 1 | 116.5 | 116.5
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW UEQT OD457x9.53/OD219.1x6.35 SA234WPB | NO | 9 | 9 | 913.68 | 913.68
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW UEQT OD457x9.53/OD273x9.27 SA234WPB | NO | 2 | 2 | 209.8 | 209.8
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW UEQT OD457x9.53/OD355.6x9.53 SA234WPB | NO | 2 | 2 | 220 | 220
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW RED OD457x9.53/OD219.1x8.18 SA234WP22 | NO | 1 | 1 | 30.787 | 30.787
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BRANCH PIPE OD114.3x13.49 SA106 GR.B | M | 2 | 2 | 67.08 | 67.08
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BRANCH PIPE OD168.3x10.97 SA106 GR.B | M | 2 | 2 | 85.12 | 85.12
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BRANCH PIPE OD88.9x11.13 SA106 GR.B | M | 2 | 2 | 30.54 | 30.54
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SPARE CONNN.PIPE DIA 114.3x6.02 SA106GRB | M | 2 | 2 | 32.14 | 32.14
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB15 CL:3000-SA105 | NO | 8 | 8 | 1.44 | 1.44
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 3 | 3 | 1.29 | 1.29
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | TEMP STUB RC 1" L=45 - CS SA105 | NO | 7 | 7 | 3.5 | 3.5
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SCREW PLUG RC 1" CS SA105 | NO | 7 | 7 | 1.4 | 1.4
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW END CAP OD114.3x6.02 SA515GR70 | NO | 4 | 4 | 8.8 | 8.8
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | FLAT ENDCLOSURE OD219.1x6.35 SA515GR70 | NO | 2 | 2 | 17.86 | 17.86
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW END CAP OD457x9.53 SA234WPB | NO | 1 | 1 | 77.77 | 77.77
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | CARRIER PLATE 20x50x120 SA515 GR70 | NO | 16 | 16 | 14.08 | 14.08
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BOTTOM PLATE 16THK 2000x1500 SA515 GR70 | NO | 1 | 1 | 376.8 | 376.8
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 114.3x8.56 SA106GRC | M | 45 | 45 | 1004.445 | 1004.445
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SPARE PIPE DIA 114.3x8.56 SA106GRC | M | 1 | 1 | 22.321 | 22.321
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SPARE PIPE DIA 219.1x6.35 SA106GRB | M | 1 | 1 | 33.31 | 33.31
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 219.1x12.7 SA106GRC | M | 1 | 1 | 64.641 | 64.641
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 219.1x6.35 SA106GRB | M | 30 | 30 | 999.3 | 999.3
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 114.3x6.02 SA106GRB | M | 0.5 | 0.5 | 8.035 | 8.035
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SUPP. PIPE OD88.9x7.62 SA106 GR.B | M | 3 | 3 | 45.81 | 45.81
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD114.3x8.56 SA234WPC | NO | 9 | 9 | 49.5 | 49.5
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD219.1x6.35 SA234WPB | NO | 8 | 8 | 133.6 | 133.6
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW EQT OD114.3x8.56 SA234WPC | NO | 1 | 1 | 7.7 | 7.7
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW EQT OD219.1x6.35 SA234WPC | NO | 1 | 1 | 19.27 | 19.27
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW UEQT OD219.1x6.35/OD114.3x6.02 SA234WPB | NO | 2 | 2 | 34.36 | 34.36
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW REDUCER OD219.1x12.7/114.3x8.56 SA234 WPC | NO | 2 | 2 | 18 | 18
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW REDUCER OD114.3x8.56/OD88.9x7.62 SA234 WPC | NO | 2 | 2 | 3.86 | 3.86
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW END CAP OD114.3x6.02 SA234WPB | NO | 2 | 2 | 4.4 | 4.4
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | CARRIER PLATE 16x50x80 SA515 GR70 | NO | 4 | 4 | 1.92 | 1.92
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BOTTOM PLATE 16THK 1000x1000 SA515 GR 70 | NO | 1 | 1 | 125 | 125
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB25 CL:6000-SA105 | NO | 12 | 12 | 6.84 | 6.84
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB50 CL:6000-SA105 | NO | 5 | 5 | 9.8 | 9.8
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | TEMP STUB RC 1.5" OD78 L=64 - CS SA105 | NO | 5 | 5 | 7.5 | 7.5
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SCREW PLUG RC 1.5" SA105 | NO | 5 | 5 | 2.5 | 2.5
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | GI -SHEET FOR RAIN HOOD 0.63 THKx1000x2000 IS277 | NO | 1 | 1 | 9.892 | 9.892
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | PIPE OD711X10, SA672GRB70 | M | 27 | 27 | 4668.3 | 4668.3
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SPARE PIPE OD508x9.53 SA106 GRB | M | 2 | 2 | 234.3 | 234.3
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | PIPE OD508X9.53, SA106GRB | M | 84 | 84 | 9840.6 | 9840.6
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BRANCH PIPE OD219.1X16 , SA106GRB | M | 2 | 2 | 160.26 | 160.26
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW LR 90DEG ELL OD711X10 SA234WPB(W) | NO | 3 | 3 | 939 | 939
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW LR 45DEG ELL OD711X10 SA234WPB(W) | NO | 3 | 3 | 432.93 | 432.93
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 12 | 12 | 1682.76 | 1682.76
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW RED OD711X9.53/610X9.53 SA234WPB | NO | 1 | 1 | 93.9 | 93.9
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW RED OD711X10/508X9.53 SA234WPB | NO | 2 | 2 | 180.86 | 180.86
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW UNEQT OD711X10/610X9.53 SA234WPB | NO | 1 | 1 | 274.85 | 274.85
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | FLAT END CLOSURE OD219.1X8.18 SA515GR70 | NO | 2 | 2 | 17.26 | 17.26
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SW STUB NB25 CL6000 CS SA105 | NO | 8 | 8 | 4.56 | 4.56
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SW STUB NB25 CL3000 CS SA105 OD50 H=54 | NO | 5 | 5 | 2.15 | 2.15
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SW STUB NB15 CL3000 CS SA105 OD36 H=44 | NO | 14 | 14 | 2.52 | 2.52
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | TEMPERATURE STUB M33X2 (CS) SA105 ( D-78 , H-45) (ROD-80) | NO | 3 | 3 | 3.36 | 3.36
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SCREW PLUG M33X2 CS SA105 | NO | 3 | 3 | 1.2 | 1.2
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | PACKING RING IS1972 | NO | 3 | 3 | 0.03 | 0.03
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | TEMP.STUB L=45 SA105 ( HWR ) ROD-80 DIA | NO | 2 | 2 | 1.3 | 1.3
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | TEMP.STUB RC 1 "(CS) D55 , L=45 SA105 (ROD-D63) | NO | 8 | 8 | 5.6 | 5.6
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SCREW PLUG R 1 " (CS) SA105 (ROD-D40) | NO | 8 | 8 | 1.6 | 1.6
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | CARRIER PLATE 20X50X120 SA515GR70 | NO | 24 | 24 | 21.12 | 21.12
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD914X9.53 L=800 SA106GRB | M | 0.8 | 0.8 | 170 | 170
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD660X9.53 L=1000 SA106GRB | M | 1 | 1 | 152.876 | 152.876
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD457X9.53 L=1500 SA106GRB | M | 1.5 | 1.5 | 157.74 | 157.74
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | LUG PLATE 16X559X325 SA515GR70 | NO | 2 | 2 | 29.6 | 29.6
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PLATE 20X1500X2000 SA515GR70 | NO | 1 | 1 | 471 | 471
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PLATE 10X2000X1000 SA515GR70 | NO | 2 | 2 | 157 | 157
1 | Lara 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | THERMOWELL STUB SA105 OD-70, H-80 (ROD-80) | NO | 5 | 5 | 8.5 | 8.5
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD355.6X9.53 SA106GRB | M | 4 | 4 | 325.32 | 325.32
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD219.1X6.35 SA106GRB | M | 5 | 5 | 166.55 | 166.55
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD168.3X7.11 SA106GRB | M | 5.5 | 5.5 | 155.43 | 155.43
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD88.9X5.49 SA106GRB | M | 5.5 | 5.5 | 62.095 | 62.095
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD355.6X9.53 SA234WPB | NO | 1 | 1 | 70 | 70
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 45DEG ELL OD355.6x9.53 SA234WPB | NO | 1 | 1 | 34.03 | 34.03
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 1 | 1 | 16.7 | 16.7
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 45DEG ELL OD219.1x6.35 SA234WPB | NO | 1 | 1 | 7.97 | 7.97
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 1 | 1 | 10.14 | 10.14
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 1 | 1 | 2.02 | 2.02
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 45DEG ELL OD88.9X5.49 SA234WPB | NO | 1 | 1 | 1.01 | 1.01
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PIPE OD 219.1 x 6.35 - SA106GRB | M | 60 | 60 | 1998.6 | 1998.6
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PIPE OD 219.1 x 12.7 - SA106GRC | M | 15 | 15 | 969.6 | 969.6
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PIPE DIA 114.3 X 6.02 SA106GRB | M | 1 | 1 | 16.07 | 16.07
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SUPPORT PIPE OD168.3x7.11 SA106GRB | M | 2.5 | 2.5 | 70.655 | 70.655
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 90DEG ELL OD219.1X6.35 SA234WPB | NO | 11 | 11 | 183.7 | 183.7
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 45DEG ELL OD219.1X6.35 SA234WPB | NO | 2 | 2 | 15.96 | 15.96
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 90DEG ELL OD219.1X12.7 SA234WPC | NO | 1 | 1 | 30.97 | 30.97
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 45DEG ELL OD219.1X12.7 SA234WPC | NO | 2 | 2 | 30.96 | 30.96
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW REDUCER - OD273x12.7/OD219.1x12.7 SA234WPC | NO | 1 | 1 | 13.29 | 13.29
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | FLAT END CLOSURE OD114.3X6.02 SA515GR70 | NO | 1 | 1 | 2.2 | 2.2
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW UEQT 219.1X6.35/114.3X6.02 SA234WPB | NO | 1 | 1 | 17.18 | 17.18
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW EQT 219.1X6.35 SA234WPB | NO | 1 | 1 | 19.27 | 19.27
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | ASME B16.11 SW STUB NB40 CL:6000-SA105 | NO | 2 | 2 | 2.14 | 2.14
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | ASME B16.11 SW STUB NB25 CL:6000-SA105 | NO | 2 | 2 | 1.14 | 1.14
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | TEMPERATURE STUB M33x2 L=45 OD-78 -SA105 | NO | 1 | 1 | 1.12 | 1.12
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SCREW PLUG M33 X 2-SA105 | NO | 1 | 1 | 0.8 | 0.8
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PACKING RING M33x2 | NO | 1 | 1 | 0.01 | 0.01
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | CARRIER PLATE T=8X50X80-SA515GR70 | NO | 8 | 8 | 2.009 | 2.009
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SUPPORT PIPE 168.3X7.11 SA106GRB | M | 3 | 3 | 84.78 | 84.78
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SUPPORT PLATE 10X200X200-SA515GR70 | NO | 8 | 8 | 25.12 | 25.12
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 508x9.53 - SA106 GRB | M | 15 | 15 | 1757.25 | 1757.25
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 355.6x9.53 - SA106 GRB | M | 4 | 4 | 325.2 | 325.2
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 273x9.27 - SA106 GRB | M | 40 | 40 | 2411.52 | 2411.52
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 168.3x7.11 - SA106 GRB | M | 8 | 8 | 226.096 | 226.096
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 219.1x6.35 - SA106 GRB | M | 1 | 1 | 33.31 | 33.31
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 114.3x6.02 - SA106 GRB | M | 1 | 1 | 16.0733 | 16.0733
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 3 | 3 | 420.69 | 420.69
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 45DEG ELL OD508X9.53 SA234WPB | NO | 1 | 1 | 70.07 | 70.07
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD355.6X9.53 SA234WPB | NO | 2 | 2 | 136.2 | 136.2
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD273X9.27 SA234WPB | NO | 10 | 10 | 370 | 370
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 3 | 3 | 30.42 | 30.42
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW UEQT 273X9.27/114.3x6.02 SA234WPB | NO | 1 | 1 | 34.4 | 34.4
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW UEQT 273X9.27/168.3x7.11 SA234WPB | NO | 1 | 1 | 35.46 | 35.46
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW UEQT 508X9.53/219.1x6.35 SA234WPB | NO | 1 | 1 | 120.7 | 120.7
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW EQT 273X9.27 SA234WPB | NO | 1 | 1 | 38.83 | 38.83
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW EQT 508X9.53 SA234WPB | NO | 1 | 1 | 141.95 | 141.95
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 508X9.53/273x9.27 SA234WPB | NO | 2 | 2 | 93.28 | 93.28
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 355.6X9.53/168.3x7.11 SA234WPB | NO | 1 | 1 | 18.49 | 18.49
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 406.4x9.53/355.6X9.53 SA234WPB | NO | 1 | 1 | 31.21 | 31.21
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 965X9.53/508X9.53 SA234WPB | NO | 1 | 1 | 117.84 | 117.84
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 8 | 8 | 3.44 | 3.44
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | FLAT END CLOSURE OD219.1X6.35 SA515GR70 | NO | 1 | 1 | 8.5 | 8.5
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | FLAT END CLOSURE OD114.3X6.02 SA515GR70 | NO | 1 | 1 | 2.2 | 2.2
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | CARRIER PLATE 16X120X50-SA515GR70 | NO | 8 | 8 | 7.04 | 7.04
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | CARRIER PLATE 16X80X50-SA515GR70 | NO | 8 | 8 | 3.84 | 3.84
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | LUG PLATE 16 THK 443x260 -SA515 GR70 | NO | 1 | 1 | 9.4 | 9.4
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | SUPPORT PLATE 12x500x500-SA515GR70 | NO | 4 | 4 | 94.2 | 94.2
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | SUPPORT PIPE OD 457 X 9.53 L=1000-SA106GRB | M | 1 | 1 | 105.3 | 105.3
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | ORIFICE PLATE ASSY-NB350 SA515GR70 | NO | 1 | 1 | 30.788 | 30.788
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | SOW FLANGE NB350CL150 OD535X40 SA515GR70 | NO | 2 | 2 | 179.75 | 179.75
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | STUD M27 X 3 X 160 SA193B7 | NO | 12 | 12 | 8.1 | 8.1
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | NUT -M27 -2H | NO | 24 | 24 | 4.08 | 4.08
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | NON-ASBESTOS JOINTING SHEET 3.0MM | NO | 1 | 1 | 5.69 | 5.69
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | PIPE DIA 88.9 X 5.49 SA106GRB | M | 68 | 68 | 767.72 | 767.72
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 14 | 14 | 28.28 | 28.28
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | ASMEB16.9 BWLR 45DEG ELBOW OD88.9X5.49 SA234WPB | NO | 2 | 2 | 2.02 | 2.02
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | TEMP STUB M33X2; L=64 SA105 | NO | 1 | 1 | 0.72 | 0.72
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | COPPER PACKING RING M33X2 IS1972 | NO | 1 | 1 | 0.01 | 0.01
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SCREW PLUG CS (M33X2) SA105 | NO | 1 | 1 | 0.4 | 0.4
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 4 | 4 | 4.3 | 4.3
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SW STUB NB15 CL 3000 SA105 | NO | 2 | 2 | 0.546 | 0.546
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SW STUB NB40 CL3000 CS SA105 | NO | 1 | 1 | 0.75 | 0.75
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | CARRIER PLATE 16X50X80 SA105 | NO | 4 | 4 | 2.01 | 2.01
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SUPPORT PIPE OD60.3X5.54 L=4000 SA106GRB | M | 4 | 4 | 29.92 | 29.92
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | PLATE 10.0 MM 1000X1000 SA515GR70 | NO | 1 | 1 | 78.5 | 78.5
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | TEMP STUB RC 1" L=64-SA105 | NO | 3 | 3 | 1.8375 | 1.8375
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SCREW PLUG RC 1" SA105 | NO | 3 | 3 | 0.525 | 0.525
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | PIPE DIA 457 X 9.53 - SA335P22 | M | 7 | 7 | 736.12 | 736.12
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | PIPE DIA 457 X 9.53 - SA335P11 | M | 1.5 | 1.5 | 157.74 | 157.74
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | PIPE DIA 457 X 9.53 - SA106 GR.B | M | 30 | 30 | 3154.8 | 3154.8
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SPARE PIPE DIA 457 X 9.53 - SA106 GR.B | M | 1 | 1 | 105.16 | 105.16
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SUPPORT PIPE OD323.9x9.53 SA335 P11 | M | 1.5 | 1.5 | 110.82 | 110.82
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SUPPORT PIPE OD406.4x12.7 SA106 GR.B | M | 3.5 | 3.5 | 431.55 | 431.55
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD457x9.53 SA234WPB | NO | 4 | 4 | 453.48 | 453.48
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD457x9.53 SA234WP22 | NO | 1 | 1 | 116.5 | 116.5
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW UEQT OD457x9.53/OD219.1x6.35 SA234WPB | NO | 9 | 9 | 913.68 | 913.68
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW UEQT OD457x9.53/OD273x9.27 SA234WPB | NO | 2 | 2 | 209.8 | 209.8
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW UEQT OD457x9.53/OD355.6x9.53 SA234WPB | NO | 2 | 2 | 220 | 220
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW RED OD457x9.53/OD219.1x8.18 SA234WP22 | NO | 1 | 1 | 30.787 | 30.787
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BRANCH PIPE OD114.3x13.49 SA106 GR.B | M | 2 | 2 | 67.08 | 67.08
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BRANCH PIPE OD168.3x10.97 SA106 GR.B | M | 2 | 2 | 85.12 | 85.12
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BRANCH PIPE OD88.9x11.13 SA106 GR.B | M | 2 | 2 | 30.54 | 30.54
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SPARE CONNN.PIPE DIA 114.3x6.02 SA106GRB | M | 2 | 2 | 32.14 | 32.14
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB15 CL:3000-SA105 | NO | 8 | 8 | 1.44 | 1.44
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 3 | 3 | 1.29 | 1.29
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | TEMP STUB RC 1" L=45 - CS SA105 | NO | 7 | 7 | 3.5 | 3.5
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SCREW PLUG RC 1" CS SA105 | NO | 7 | 7 | 1.4 | 1.4
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW END CAP OD114.3x6.02 SA234WPB | NO | 4 | 4 | 8.8 | 8.8
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | FLAT ENDCLOSURE OD219.1x6.35 SA515GR70 | NO | 2 | 2 | 17.86 | 17.86
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW END CAP OD457x9.53 SA234WPB | NO | 1 | 1 | 77.77 | 77.77
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | CARRIER PLATE 20x50x120 SA515 GR70 | NO | 16 | 16 | 14.08 | 14.08
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BOTTOM PLATE 16THK 2000x1500 SA515 GR70 | NO | 1 | 1 | 376.8 | 376.8
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 114.3x8.56 SA106GRC | M | 45 | 45 | 1004.445 | 1004.445
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SPARE PIPE DIA 114.3x8.56 SA106GRC | M | 1 | 1 | 22.321 | 22.321
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SPARE PIPE DIA 219.1x6.35 SA106GRB | M | 1 | 1 | 33.31 | 33.31
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 219.1x12.7 SA106GRC | M | 1 | 1 | 64.641 | 64.641
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 219.1x6.35 SA106GRB | M | 30 | 30 | 999.3 | 999.3
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 114.3x6.02 SA106GRB | M | 0.5 | 0.5 | 8.035 | 8.035
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SUPP. PIPE OD88.9x7.62 SA106 GR.B | M | 3 | 3 | 45.81 | 45.81
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD114.3x8.56 SA234WPC | NO | 9 | 9 | 49.5 | 49.5
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD219.1x6.35 SA234WPB | NO | 8 | 8 | 133.6 | 133.6
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW EQT OD114.3x8.56 SA234WPC | NO | 1 | 1 | 7.7 | 7.7
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW EQT OD219.1x6.35 SA234WPC | NO | 1 | 1 | 19.27 | 19.27
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW UEQT OD219.1x6.35/OD114.3x6.02 SA234WPB | NO | 2 | 2 | 34.36 | 34.36
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW REDUCER OD219.1x12.7/114.3x8.56 SA234 WPC | NO | 2 | 2 | 18 | 18
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW REDUCER OD114.3x8.56/OD88.9x7.62 SA234 WPC | NO | 2 | 2 | 3.86 | 3.86
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW END CAP OD114.3x6.02 SA234WPB | NO | 2 | 2 | 4.4 | 4.4
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | CARRIER PLATE 16x50x80 SA515 GR70 | NO | 4 | 4 | 1.92 | 1.92
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BOTTOM PLATE 16THK 1000x1000 SA515 GR 70 | NO | 1 | 1 | 125 | 125
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB25 CL:6000-SA105 | NO | 12 | 12 | 6.84 | 6.84
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB50 CL:6000-SA105 | NO | 5 | 5 | 9.8 | 9.8
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | TEMP STUB RC 1.5" OD78 L=64 - CS SA105 | NO | 5 | 5 | 7.5 | 7.5
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SCREW PLUG RC 1.5" SA105 | NO | 5 | 5 | 2.5 | 2.5
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | GI -SHEET FOR RAIN HOOD 0.63 THKx1000x2000 IS277 | NO | 1 | 1 | 9.892 | 9.892
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | PIPE OD711X10, SA672GRB70 | M | 27 | 27 | 4668.3 | 4668.3
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SPARE PIPE OD508x9.53 SA106 GRB | M | 2 | 2 | 234.3 | 234.3
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | PIPE OD508X9.53, SA106GRB | M | 84 | 84 | 9840.6 | 9840.6
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BRANCH PIPE OD219.1X16 , SA106GRB | M | 2 | 2 | 160.26 | 160.26
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW LR 90DEG ELL OD711X10 SA234WPB(W) | NO | 3 | 3 | 939 | 939
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW LR 45DEG ELL OD711X10 SA234WPB(W) | NO | 3 | 3 | 432.93 | 432.93
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 12 | 12 | 1682.76 | 1682.76
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW RED OD711X9.53/610X9.53 SA234WPB | NO | 1 | 1 | 93.9 | 93.9
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW RED OD711X10/508X9.53 SA234WPB | NO | 2 | 2 | 180.86 | 180.86
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW UNEQT OD711X10/610X9.53 SA234WPB | NO | 1 | 1 | 274.85 | 274.85
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | FLAT END CLOSURE OD219.1X8.18 SA515GR70 | NO | 2 | 2 | 17.26 | 17.26
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SW STUB NB25 CL6000 CS SA105 | NO | 8 | 8 | 4.56 | 4.56
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SW STUB NB25 CL3000 CS SA105 OD50 H=54 | NO | 5 | 5 | 2.15 | 2.15
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SW STUB NB15 CL3000 CS SA105 OD36 H=44 | NO | 14 | 14 | 2.52 | 2.52
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | TEMPERATURE STUB M33X2 (CS) SA105 ( D-78 , H-45) (ROD-80) | NO | 3 | 3 | 3.36 | 3.36
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SCREW PLUG M33X2 CS SA105 | NO | 3 | 3 | 1.2 | 1.2
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | PACKING RING IS1972 | NO | 3 | 3 | 0.03 | 0.03
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | TEMP.STUB L=45 SA105 ( HWR ) ROD-80 DIA | NO | 2 | 2 | 1.3 | 1.3
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | TEMP.STUB RC 1 "(CS) D55 , L=45 SA105 (ROD-D63) | NO | 8 | 8 | 5.6 | 5.6
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SCREW PLUG R 1 " (CS) SA105 (ROD-D40) | NO | 8 | 8 | 1.6 | 1.6
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | CARRIER PLATE 20X50X120 SA515GR70 | NO | 24 | 24 | 21.12 | 21.12
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD914X9.53 L=800 SA106GRB | M | 0.8 | 0.8 | 170 | 170
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD660X9.53 L=1000 SA106GRB | M | 1 | 1 | 152.876 | 152.876
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD457X9.53 L=1500 SA106GRB | M | 1.5 | 1.5 | 157.74 | 157.74
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | LUG PLATE 16X559X325 SA515GR70 | NO | 2 | 2 | 29.6 | 29.6
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PLATE 20X1500X2000 SA515GR70 | NO | 1 | 1 | 471 | 471
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PLATE 10X2000X1000 SA515GR70 | NO | 2 | 2 | 157 | 157
1 | Lara 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | THERMOWELL STUB SA105 OD-70, H-80 (ROD-80) | NO | 5 | 5 | 8.5 | 8.5
1 Total | [10 empty] | 101164.9837
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | PIPE OD2032x16 L=14980 SA672 GRB70 | M | 21 | 42 | 16704.03 | 33408.06
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | 90DEG MITRE BEND OD2032x16 R=1500 SA387GR12CL2(CERT) | NO | 6 | 12 | 12905.652 | 25811.304
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | 13.6DEG MITRE BEND OD2032x16 R=1500 SA387GR12CL2(CERT) | NO | 2 | 4 | 1863.592 | 3727.184
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | ASME B16.11 SW STUB NB15,CL:3000-SA105 OD36 H=44 | NO | 10 | 20 | 1.8 | 3.6
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | ASME B16.11 SW STUB NB50,CL:3000-SA105 OD80 H=60 | NO | 4 | 8 | 5.32 | 10.64
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | TEMP STUB RC 1" L=45-SA105 | NO | 8 | 16 | 4.9 | 9.8
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | SCREW PLUG RC 1" SA105 | NO | 8 | 16 | 1.4 | 2.8
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | BLIND FLANGE ASSY NB500 CL150 SA515GR70 | NO | 2 | 4 | 126 | 252
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | BRANCH PIPE OD508x12.7 L=500 SA106GRB | M | 1 | 2 | 155.1 | 310.2
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | SOW FLANGE NB500 CL150 SA515GR70 | NO | 2 | 4 | 108 | 216
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | BRANCH PIPE OD323.9x9.53 L=500 SA106GRB | M | 1 | 2 | 73.88 | 147.76
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | FLAT FACED FLANGE NB2000 SA515GR70 | NO | 4 | 8 | 546.656 | 1093.312
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | NON ASBESTOS GASKET NB2000 PN10 NON-ASBESTOS | NO | 2 | 4 | 13.656 | 27.312
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | BOTTOM PLATE 20 THK 450X350-SA515GR70 | NO | 16 | 32 | 395.632 | 791.264
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | PAD PLATE 840x400x12 SA515GR70 | NO | 16 | 32 | 506.416 | 1012.832
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | STIFFNER PLATE 607x427x16 SA515GR70 | NO | 32 | 64 | 1041.728 | 2083.456
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | STIFFNER PLATE 740x275x16 SA515GR70 | NO | 16 | 32 | 408.96 | 817.92
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | BOTTOM PLATE 25 THK 750X474-SA515GR70 | NO | 4 | 8 | 279.068 | 558.136
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | PAD PLATE 717x375x12 SA515GR70 | NO | 4 | 8 | 101.312 | 202.624
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | STUD M 30 X200 SA193B16 | NO | 44 | 88 | 37.4 | 74.8
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | HEX . NUT M30 SA194GR2H | NO | 88 | 176 | 20.328 | 40.656
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | STUD M 52 X5X340 SA193B7 | NO | 100 | 200 | 560 | 1120
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | HEX . NUT M52x5 SA194GR2H | NO | 200 | 400 | 310 | 620
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | PIPE OD-323.9X9.53 SA106GRC | M | 54 | 108 | 3989.52 | 7979.04
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | BW LR 90DEG ELL OD323.9X9.53 SA234WPC | NO | 4 | 8 | 212.16 | 424.32
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | 45° BW LR ELBOW 323.9X9.53 SA234WPB | NO | 2 | 4 | 54 | 108
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | SUPPORT PIPE OD219.1X6.35 L=1000 SA106GRB | NO | 3 | 6 | 99.93 | 199.86
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | BOTTOM PLATE 10X1000X1000MM SA515GR70 | NO | 1 | 2 | 78.5 | 157
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | GAL WIRE MESH 1.2 X1200X2000 IS280 | NO | 1 | 2 | 6.24 | 12.48
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | SOW FLANGE NB 300 CL150 SA515GR70 | NO | 4 | 8 | 94.88 | 189.76
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | BOLT-M24X120 -4.6-IS1363P1 | NO | 26 | 52 | 13.676 | 27.352
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | NUT -M24 -CL4-IS1363 | NO | 26 | 52 | 2.86 | 5.72
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | NON-ASBESTOS JOINTING SHEET 3.0MMX500X500 | NO | 1 | 2 | 2.47 | 4.94
2 | Lara 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | SPARE PIPE OD-323.9X9.53X6000-SA106GRC | M | 2 | 4 | 147.76 | 295.52
2 Total | [10 empty] | 81745.652
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PIPE DIA 114.3 X 6.02 SA106GRB | M | 4 | 8 | 64.3 | 128.6
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PIPE DIA 323.9x9.53 SA106GRB | M | 17 | 34 | 1255.96 | 2511.92
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PIPE DIA 508 X 9.53 SA106GRB | M | 14 | 28 | 1640.0944 | 3280.1888
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PIPE DIA 660 X 10 SA672 B70 | M | 18 | 36 | 2865.15 | 5730.3
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PIPE DIA60.3x5.54 L=20000MM SA106 GRB | M | 20 | 40 | 149.62 | 299.24
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BW LR 49.2 DEG ELL OD660x9.53 SA234WPB | NO | 2 | 4 | 272.66 | 545.32
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BW LR 90DEG ELL OD323.9X9.53 SA234WPB | NO | 5 | 10 | 265.05 | 530.1
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BW UEQT OD660.4x9.53/323.9x9.53 SA234WPB | NO | 4 | 8 | 1052 | 2104
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BW UEQT OD660x9.53/508x9.53 SA234WPB | NO | 3 | 6 | 679.95 | 1359.9
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BW C.RED 610x9.53/508x9.53 SA234WPB | NO | 3 | 6 | 198.6 | 397.2
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 9 | 18 | 3.87 | 7.74
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | ASME B16.11 SW STUB NB50,CL:3000 SA105 | NO | 5 | 10 | 6.65 | 13.3
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | ASME B16.11 SW STUB NB15,CL:3000 SA105 | NO | 9 | 18 | 1.62 | 3.24
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | TEMPERATURE STUB M33X2, L=64 SA105 | NO | 10 | 20 | 7 | 14
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PACKING RING M33x2 IS1972 | NO | 10 | 20 | 10.1 | 20.2
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | SCREW PLUG M33 x 2 SA105 | NO | 10 | 20 | 8 | 16
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | FLAT END CLOSURE OD114.3x6.02 SA515 GR70( PLATE 120x120X8THK) | NO | 1 | 2 | 2.19 | 4.38
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | FLAT END CLOSURE OD660x10 SA515 GR70 (PLATE 660X660X10THK) | NO | 2 | 4 | 320 | 640
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | SOW FLANGE NB25 CL150 IS2062 | NO | 3 | 6 | 2.7 | 5.4
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | STUD M12X70 SA193GRB7 | NO | 20 | 40 | 1.2 | 2.4
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | HEX,NUT M12 SA194GR2H | NO | 40 | 80 | 0.8 | 1.6
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | SOW FLANGE NB50 CL150 IS2062 | NO | 3 | 6 | 6 | 12
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | STUD M16X100 SA193GRB7 | NO | 20 | 40 | 2.8 | 5.6
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | HEX,NUT M16 SA194GR2H | NO | 40 | 80 | 1.32 | 2.64
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | GASKET T=1.5MM 1000X1000 NON ASBESTOS | NO | 1 | 2 | 2.47 | 4.94
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BOTTOM SUPPORT PIPE OD406.4x9.53 L=5000 SA106 GRB | M | 5 | 10 | 466.35 | 932.7
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BOTTOM SUPPORT PIPE OD508x9.53 L=5000 SA106 GRB | M | 5 | 10 | 585.75 | 1171.5
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | SUPPORT PIPE OD88.9x5.49 SA106 GRB | M | 1 | 2 | 11.29 | 22.58
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BOTTEM PLATE 10 THK 120x120 SA515 GR70 | NO | 2 | 4 | 2.26 | 4.52
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BOTTOM SUPPORT PIPE OD273X9.27 L=4000MM SA106 GRB | M | 4 | 8 | 241.5 | 483
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BOTTOM SUPPORT PLATE 10x1500x3500 SA515 GR70 | NO | 1 | 2 | 412.125 | 824.25
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | TEMP STUB RC1 INCH SA105 | NO | 6 | 12 | 5.064 | 10.128
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | CARBON STEEL PLUG 1" SA105 | NO | 6 | 12 | 1.2 | 2.4
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | PIPE DIA 323.9 X 9.53 SA106GRC | M | 3 | 6 | 221.64 | 443.28
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | PIPE OD-323.9X9.53-SA106GRB | M | 40 | 80 | 2955.2 | 5910.4
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | PIPE DIA 273.0 X 9.27 SA106GRB | M | 7 | 14 | 422.17 | 844.34
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | BW LR 90DEG ELL OD323.9X9.53 SA234WPB | NO | 9 | 18 | 506.34 | 1012.68
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | BW LR 90DEG ELL OD273X9.27 SA234WPB | NO | 3 | 6 | 116.43 | 232.86
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | BW UEQT 323.9X9.53/273X9.27 SA234WPB | NO | 2 | 4 | 108.92 | 217.84
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | BW RED 323.9X9.53/168.3X10.97 SA234WPC | NO | 2 | 4 | 24.14 | 48.28
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | SW STUB NB25 CL3000 CS OD34XH44 SA105 | NO | 6 | 12 | 2.58 | 5.16
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | SUPPORT PIPE OD273.0X9.27 L=2500 SA106GRB | M | 2.5 | 5 | 180.85 | 361.7
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | BOTTOM SUPPORT PLATE 10x500x1000 SA515 GR70 | NO | 1 | 2 | 39.25 | 78.5
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 48.3X5.08 SA106GRB | M | 26 | 52 | 140.66 | 281.32
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 73.0X5.16 SA106GRB | M | 6 | 12 | 51.78 | 103.56
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | BW LR 90DEG ELL OD48.3X5.08 SA234WPB | NO | 9 | 18 | 5.58 | 11.16
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | BW LR 90DEG ELL OD73.0X5.16 SA234WPB | NO | 6 | 12 | 8.88 | 17.76
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | UNIONS 1/2"S.W.-1/2"NPT SA106GRB (OD21.3X3.73 L=200MM) | NO | 60 | 120 | 19.2 | 38.4
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | HEXAGONAL NIPPLES 1/2"NPT (M) -1/2"NPT (M) (OD21.3X3.73 L=200MM)SA106GRB | NO | 60 | 120 | 70.2 | 140.4
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 60.3X3.91 SA312TP304 | M | 120 | 240 | 651.6 | 1303.2
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 60.3X5.54 SA106GRB | M | 230 | 460 | 1720.63 | 3441.26
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 33.4X4.55 SA106GRB | M | 175 | 350 | 567 | 1134
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 21.3X3.73 SA106GRB | M | 500 | 1000 | 810 | 1620
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ELBOW 90DEG OD60.3X3.91 SA312WP304 | NO | 20 | 40 | 15.4 | 30.8
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ELBOW 90DEG OD60.3X5.54 SA234WPB | NO | 42 | 84 | 44.52 | 89.04
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ELBOW 90DEG OD33.4X4.55 SA234WPB | NO | 23 | 46 | 5.75 | 11.5
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ELBOW 90DEG OD21.3X3.73 SA234WPB | NO | 60 | 120 | 4.8 | 9.6
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | REDUCER 60.3X5.54/33.4X4.55 SA234WPB | NO | 2 | 4 | 1.14 | 2.28
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | REDUCER 33.4X4.55/21.3X3.73 SA234WPB | NO | 30 | 60 | 5.1 | 10.2
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | UEQT 60.3X5.54/33.4X4.55 SA234WPB | NO | 10 | 20 | 14.2 | 28.4
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | EQT 60.3X5.54 SA234WPB | NO | 4 | 8 | 6.32 | 12.64
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | EQT 33.4X4.55 SA234WPB | NO | 26 | 52 | 11.18 | 22.36
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | UEQT 33.4X4.55/21.3x3.73 SA234WPB | NO | 40 | 80 | 15.2 | 30.4
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | EQT 33.4X3.73 SA234WPB | NO | 20 | 40 | 7.2 | 14.4
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | EQT 60.3X3.91 SA312WP304 | NO | 6 | 12 | 7.2 | 14.4
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ROUND DIA 63 L=70 SA105 (ORIFICE PLATE NB50) | NO | 1 | 2 | 0.665 | 1.33
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ROUND DIA 40 L=60 SA105 (ORIFICE PLATE NB25) | NO | 1 | 2 | 0.25 | 0.5
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | EQT 21.3X3.73 SA234WPB | NO | 15 | 30 | 3.45 | 6.9
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | PIPE OD 219.1 x 12.7 - SA106GRB | M | 52 | 104 | 3361.2797 | 6722.5595
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | PIPE DIA 33.4X4.55 SA106GRB | M | 7 | 14 | 22.519 | 45.038
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | BW LR 90DEG ELL OD219.1X12.7 SA234WPB | NO | 15 | 30 | 464.55 | 929.1
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | BW EQT OD219.1x12.7 SA234WPB | NO | 2 | 4 | 74.8 | 149.6
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | BW RED OD219.1x12.7/168.3x7.11 SA234WPB | NO | 2 | 4 | 17.456 | 34.912
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 3 | 6 | 1.29 | 2.58
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | LUG PLATE 16 THK 428X240 -SA515GR.70 | NO | 2 | 4 | 16.8 | 33.6
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | SUPPORT PIPE OD168.3x7.11 SA106 GRB | M | 4 | 8 | 113.048 | 226.096
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | BOTTOM PLATE 10 THK 1000x1000 SA515 GR70 | NO | 1 | 2 | 78.5 | 157
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | SPARE PIPE OD 219.1 x 12.7 - SA106GRB | M | 2 | 4 | 129.28 | 258.56
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | PIPE DIA 168.3 X 7.11 SA106GRB | M | 62 | 124 | 1752.1205 | 3504.2409
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 30 | 60 | 304.2 | 608.4
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | BW LR 45DEG ELL OD168.3X7.11 SA234WPB | NO | 4 | 8 | 20.32 | 40.64
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | SUPPORT PIPE OD114.3X6.02 SA106 GRB | M | 3.5 | 7 | 56.261 | 112.522
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | BOTTOM PLATE 10 THK 1000x1000 SA515 GR70 | NO | 1 | 2 | 78.5 | 157
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | SPARE PIPE DIA 168.3 X 7.11 SA106GRB | M | 2 | 4 | 56.52 | 113.04
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 323.9 X 9.53 SA106GRB | M | 49 | 98 | 3620.12 | 7240.24
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 88.9 X 5.49 SA106GRB | M | 6 | 12 | 67.74 | 135.48
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 406.4 X 12.7 SA106GRB | M | 230 | 460 | 28359 | 56718
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 406.4 X 12.7 SA106GRC | M | 40 | 80 | 4932 | 9864
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 457.0 X 12.7 SA106GRC | M | 110 | 220 | 15306.17 | 30612.34
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 114.3 X 6.02 SA106GRB | M | 5 | 10 | 80.35 | 160.7
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 323.9 X 12.7 SA106GRB | M | 18 | 36 | 1754.28 | 3508.56
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 273 X 9.27 SA106GRB | M | 30 | 60 | 1808.64 | 3617.28
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD273x9.27 SA234WPB | NO | 7 | 14 | 259 | 518
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD88.9x5.49 SA234WPB | NO | 6 | 12 | 12.18 | 24.36
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD114.3x6.02 SA234WPB | NO | 1 | 2 | 3.84 | 7.68
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD323.9x9.53 SA234WPB | NO | 12 | 24 | 648 | 1296
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD323.9x9.53 SA234WPC | NO | 5 | 10 | 270 | 540
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 45DEG ELL OD323.9x9.53 SA234WPB | NO | 2 | 4 | 54 | 108
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD406.4x12.7 SA234WPB | NO | 53 | 106 | 5857.56 | 11715.12
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 60DEG ELL OD406.4x12.7 SA234WPB | NO | 1 | 2 | 73.68 | 147.36
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 45DEG ELL OD406.4x12.7 SA234WPB | NO | 9 | 18 | 497.34 | 994.68
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW SR 90DEG ELL OD406.4x12.7 SA234WPB | NO | 1 | 2 | 110.52 | 221.04
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD406.4x12.7 SA234WPC | NO | 6 | 12 | 663.12 | 1326.24
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD457.2x12.7 SA234WPC | NO | 24 | 48 | 3395.76 | 6791.52
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 45DEG ELL OD457.2x12.7 SA234WPC | NO | 3 | 6 | 212.22 | 424.44
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 60DEG ELL OD457.2x12.7 SA234WPC | NO | 1 | 2 | 94.33 | 188.66
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW SR 90DEG ELL OD457.2x12.7 SA234WPC | NO | 2 | 4 | 282.38 | 564.76
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW SR 90DEG ELL OD508x9.53 SA234WPB | NO | 1 | 2 | 93.48 | 186.96
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD406.4x12.7/OD273x9.27 SA234WPB | NO | 1 | 2 | 37.06 | 74.12
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD850 NB/OD406.4x12.7 SA234WPB | NO | 2 | 4 | 250.04 | 500.08
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD406.4X12.7/OD323.9x9.53 SA234WPB | NO | 1 | 2 | 39.53 | 79.06
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD508x12.7/OD406.4X12.7 SA234WPB | NO | 4 | 8 | 284.04 | 568.08
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD508x14.27/OD457x12.7 SA234WPC | NO | 4 | 8 | 334.96 | 669.92
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD457x12.7/OD406.4X12.7 SA234WPC | NO | 2 | 4 | 100.14 | 200.28
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD457x12.7/OD323.9x9.53 SA234WPC | NO | 6 | 12 | 274.32 | 548.64
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD323.9x9.53/OD273x9.27 SA234WPB | NO | 2 | 4 | 27.76 | 55.52
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW EQT OD406.4x12.7 SA234WPB | NO | 7 | 14 | 837.34 | 1674.68
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW EQT OD457x12.7 SA234WPC | NO | 4 | 8 | 607.48 | 1214.96
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT 323.9X9.53/168.3x7.11 SA234WPB | NO | 3 | 6 | 154.17 | 308.34
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT 406.4x12.7/323.9X9.53SA234WPB | NO | 5 | 10 | 538.15 | 1076.3
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT 406.4x12.7/219.1X12.7 SA234WPB | NO | 3 | 6 | 300.87 | 601.74
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT- OD457x12.7/OD406.4X12.7 SA234WPC | NO | 3 | 6 | 428.88 | 857.76
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT- OD457x12.7/OD323.9x9.53 SA234WPC | NO | 1 | 2 | 132.67 | 265.34
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT- OD457x12.7/OD219.1x12.7 SA234WPC | NO | 1 | 2 | 125.66 | 251.32
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | ASME16.5 FLNAGE NB450 CL150 SA105 | NO | 8 | 16 | 1312 | 2624
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | ASME B16.11 SW STUBNB15 CL6000 SA105 | NO | 10 | 20 | 1.8 | 3.6
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | ASME B16.11 SW STUBNB25 CL6000 SA105 | NO | 76 | 152 | 43.32 | 86.64
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | ASME B16.11 SW STUBNB40 CL6000 SA105 | NO | 5 | 10 | 3.75 | 7.5
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | ASME B16.11 SW STUBNB50 CL6000 SA105 | NO | 5 | 10 | 6.65 | 13.3
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | TEMPERATURE STUB M33X2, L=64 (CS) SA105 | NO | 26 | 52 | 18.2 | 36.4
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PACKING RING M33x2 SA105 | NO | 26 | 52 | 0.26 | 0.52
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | COPPER PACKING RING M33X2 IS1972 | NO | 26 | 52 | 20.8 | 41.6
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | FLAT END CLOSURE OD114.3x6.02 SA515GR.70 | NO | 1 | 2 | 2.19 | 4.38
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BRANCH PIPE OD88.9x15.24 SA106GRB | M | 1.6 | 3.2 | 44.288 | 88.576
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BRANCH PIPE OD114.3x15.24 SA106GRB | M | 2 | 4 | 74.44 | 148.88
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | CARRIER PLATE16X50X100 SA515 GR.70 | NO | 24 | 48 | 15.072 | 30.144
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | CARRIER PLATE12X50X80 SA515 GR.70 | NO | 12 | 24 | 4.521 | 9.042
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SUPPORT PIPE OD323.9x9.53 SA106GRB | M | 12 | 24 | 1097.6457 | 2195.2914
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PLATE 10 THK 2000X2000 SA515GR70 | NO | 1 | 2 | 314 | 628
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PLATE 12 THK 2000x2000 SA515 GR70 | NO | 2 | 4 | 30.144 | 60.288
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SUPPORT PIPE OD219.1X12.7 SA106GRB | M | 2.5 | 5 | 161.6 | 323.2
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SUPPORT PIPE OD168.3X7.11 SA106GRB | M | 4 | 8 | 113.048 | 226.096
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | LUG PLATE 16 THK 559X325 -SA515GR.70 | NO | 2 | 4 | 29.6 | 59.2
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | LUG PLATE 16 THK 600X360 -SA515GR.70 | NO | 1 | 2 | 17.6 | 35.2
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 323.9 X 9.53 SA106GRB | M | 2 | 4 | 147.76 | 295.52
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 406.4 X 12.7 SA106GRB | M | 6 | 12 | 739.8 | 1479.6
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 406.4 X 12.7 SA106GRC | M | 2 | 4 | 246.6 | 493.2
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 457.0 X 12.7 SA106GRC | M | 3 | 6 | 417.441 | 834.882
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 323.9 X 12.7 SA106GRB | M | 1 | 2 | 97.46 | 194.92
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 273 X 9.27 SA106GRB | M | 5.1 | 10.2 | 307.4688 | 614.9376
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | TEMPERATURE STUB Rc1.5" SA105 OD98 L=H=45 | NO | 50 | 100 | 88.5 | 177
3 | Lara 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SCREW PLUG Rc1.5" SA105 | NO | 50 | 100 | 25 | 50
3 Total | [10 empty] | 208336.5022
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | PIPE OD 813 x 10 - SA672 B70 | M | 18 | 36 | 3564 | 7128
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | PIPE OD 610 x 10 - SA672 B70 | M | 11 | 22 | 1628 | 3256
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | PIPE OD 323.9 x 9.53 - SA106GRC | M | 13 | 26 | 960.44 | 1920.88
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SUPPORT PIPE OD559x9.53 L=700SA106GRB | M | 0.7 | 1.4 | 90.391 | 180.782
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SUPPORT PIPE OD273x12.7 L=700SA106GRC | M | 0.7 | 1.4 | 57.064 | 114.128
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | BW LR 90DEG ELL OD323.9X9.53 SA234WPC | NO | 5 | 10 | 281.3 | 562.6
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | BW LR 90DEG ELL OD610X10 SA234WPB | NO | 4 | 8 | 850.2 | 1700.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | BW LR 30DEG ELL OD610X10 SA234WPB | NO | 1 | 2 | 70.85 | 141.7
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | BW MITRE BEND R0.75D 90DEG OD813x10 SA672 B70 | NO | 4 | 8 | 758.24 | 1516.48
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 4 | 8 | 1.72 | 3.44
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | LUG PLATE 16 THK 520x632 -SA515 GR70 | NO | 3 | 6 | 123.84 | 247.68
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SUPPORT PLATE 12x600x600-SA515GR70 | NO | 1 | 2 | 33.91 | 67.82
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SUPPORT PLATE 10X300X300-SA515GR70 | NO | 1 | 2 | 7.07 | 14.14
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SPARE PIPE OD 813 x 10 - SA672 B70 | M | 1 | 2 | 198 | 396
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SPARE PIPE OD 610 x 10 - SA672 B70 | M | 1 | 2 | 148 | 296
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SPARE PIPE OD 323.9 x 9.53 - SA106GRC | M | 1 | 2 | 73.88 | 147.76
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | PIPE DIA 323.9 X 9.53 SA335P22 | M | 6 | 12 | 443.28 | 886.56
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | PIPE DIA 219.1 X 12.7 SA335P22 | M | 4 | 8 | 258.56 | 517.12
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | PIPE OD-219.1X12.7X6000-SA106GRC | M | 8 | 16 | 517.12 | 1034.24
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | PIPE DIA 168.3 X 7.11 SA106GRB | M | 2.5 | 5 | 70.65 | 141.3
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | BW LR 30DEG ELL 219.1X12.7 SA234WP22CL1 | NO | 1 | 2 | 11.13 | 22.26
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | BW LR 60DEG ELL OD219.1X12.7 SA234WPC | NO | 2 | 4 | 44.52 | 89.04
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | BW EQT OD323.9X9.53 SA335WP22CL1 | NO | 2 | 4 | 120.84 | 241.68
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB25 SA105 CL:3000 | NO | 10 | 20 | 4.3 | 8.6
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB50 SA105 CL:3000 | NO | 14 | 28 | 18.62 | 37.24
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB50 SA182F22 CL:3000 | NO | 14 | 28 | 18.62 | 37.24
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB50 SA182F22 CL:9000 | NO | 8 | 16 | 10.64 | 21.28
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB25 SA182F22 CL:3000 | NO | 1 | 2 | 0.43 | 0.86
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB40 SA182F22 CL:3000 | NO | 1 | 2 | 1.07 | 2.14
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD219.1X12.7-(PLATE OD219.1X48THK) SA515GR70 | NO | 3 | 6 | 43.2 | 86.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD168.3X7.11 (PLATE OD168.3X33THK) SA515GR70 | NO | 1 | 2 | 6.64 | 13.28
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD219.1X12.7 (PLATE OD219.1X48THK) SA387GR22CL2 | NO | 1 | 2 | 14.4 | 28.8
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD323.9X9.53-(PLATE OD324X48THK) SA387GR22CL2 | NO | 3 | 6 | 117 | 234
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD33.4X4.55 (PLATE OD33.4X20THK) SA387GR22CL2 | NO | 1 | 2 | 0.138 | 0.276
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD60.3X5.54 (PLATE OD60.3X20THK) SA515GR70 | NO | 2 | 4 | 22 | 44
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD60.3X5.54 - (PLATE OD60.3X20THK) SA387GR22CL2 | NO | 1 | 2 | 11 | 22
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD33.4X4.55 (PLATE OD33.4X20THK) SA515GR70 | NO | 2 | 4 | 0.276 | 0.552
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | SUPPORT PIPE OD168.3X10.97 L= 350 SA335P11 | NO | 1 | 2 | 14.9 | 29.8
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | SUPPORT PIPE OD168.3X10.97 L= 1050- SA106GRB | NO | 1 | 2 | 44.69 | 89.38
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | SUPPORT PIPE OD114.3X6.02 L= 400 SA106GRB | NO | 1 | 2 | 6.43 | 12.86
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | SUPPORT PIPE OD273X6.35 L= 1050 SA335P11 | NO | 1 | 2 | 43.84 | 87.68
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | BOTTOM PLATE 12 THK,1500X1500 - SA515GR70 | NO | 1 | 2 | 211.95 | 423.9
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | BOTTOM PLATE 12 THK, 1000X1000 - SA387GR11CL2 | NO | 1 | 2 | 94.2 | 188.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | PIPE OD 219.1 x 6.35 - SA106GRB | M | 4 | 8 | 133.24 | 266.48
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | SPARE PIPE OD 219.1 x 6.35 - SA106GRB | M | 1 | 2 | 33.31 | 66.62
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | PIPE OD 406.4x9.53 - SA106GRB | M | 24 | 48 | 2238.48 | 4476.96
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | SUPPORT PIPE OD168.3x7.11 L=2000 SA106GRB | M | 2 | 4 | 56.524 | 113.048
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | BW LR 90DEG ELL OD219.1X6.35 SA234WPB | NO | 4 | 8 | 66.8 | 133.6
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | BW LR 60DEG ELL OD219.1X6.35 SA234WPB | NO | 1 | 2 | 16.7 | 33.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | BW LR 45DEG ELL OD406.4x9.53 SA234WPB | NO | 3 | 6 | 133.98 | 267.96
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 4 | 8 | 1.72 | 3.44
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | CARRIER PLATE 16X120X50-SA515GR70 | NO | 4 | 8 | 3.52 | 7.04
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | SUPPORT PLATE 10X200X200-SA515GR70 | NO | 4 | 8 | 12.56 | 25.12
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | SUPPORT PIPE OD323.9X9.53 L=1500 SA106GRB | M | 1.5 | 3 | 110.82 | 221.64
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | PIPE DIA 273.0 X 6.35 SA106GRB | M | 12 | 24 | 501.24 | 1002.48
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | ASMEB16.9 BWLR 45DEG ELBOW OD355.6X9.53 SA234GRB | NO | 5 | 10 | 170.15 | 340.3
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 SA234GRB | NO | 5 | 10 | 131 | 262
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | MACHINED REDUCER NB25/15 SA234WPB | NO | 5 | 10 | 20 | 40
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | SOW FLANGE NB 250 CL150 BMC16 SA515GR70 | NO | 5 | 10 | 72.5 | 145
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | STUD M 24 X 3 X 230 SA193B7 | NO | 70 | 140 | 49 | 98
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | NUT -M24 -GR7 | NO | 140 | 280 | 15.4 | 30.8
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | NON-ASBESTOS JOINTING SH 3.0MM 1000X1000 | NO | 1 | 2 | 6 | 12
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | GALVANISED WIRE MESH 1.2THKX1200X2000 IS280 | NO | 5 | 10 | 31.2 | 62.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | SUPPORT PIPE OD219.8X8.18 L=9000 SA106GRB | M | 9 | 18 | 382.86 | 765.72
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | SUPPORT PLATE 12THKX1200X800 SA515GR70 | NO | 1 | 2 | 90.432 | 180.864
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | DRIP PAN ASSY NB 250 (CS)-3.15THK,600DIA SA515GR70 | NO | 5 | 10 | 69.9 | 139.8
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | DRIP PAN ASSY NB 250 (CS)-3.15THK,100X1700 SA515GR70 | NO | 5 | 10 | 21 | 42
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | COVER PLATE FOR DRIP PAN - 10THK,600DIA SA515GR70 | NO | 5 | 10 | 110.5 | 221
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | PIPE DIA 168.3 X 7.11 SA106GRB | M | 2 | 4 | 56.524 | 113.048
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 4 | 8 | 41.6 | 83.2
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | 45DEG BW LR ELBOW 168.3X7.11 SA234WPB | NO | 1 | 2 | 5.08 | 10.16
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 1 | 2 | 0.43 | 0.86
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 20 | 32.371 | 64.742
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | 90DEG BW LR ELBOW 33.4X4.55 SA234WPB | NO | 3 | 6 | 0.6 | 1.2
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | ORIFICE PLATE ASSY PIPE OD 168.3X7.11 SA106GRB L=300 | M | 0.3 | 0.6 | 8.4786 | 16.9572
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | ORIFICE PLATE ASSY For Pipe NB150- SA515GR70 | NO | 1 | 2 | 2.22 | 4.44
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | LUG PLATE THICK12x340x170 SA515 GR70 | NO | 1 | 2 | 3.7 | 7.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | SPARE PIPE DIA 168.3 X 7.11 SA106GRB | M | 0.5 | 1 | 14.131 | 28.262
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | PIPE DIA 168.3 X 7.11 SA106GRB | M | 2 | 4 | 56.5238 | 113.0476
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 4 | 8 | 41.6 | 83.2
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | 45 DEG BW LR ELBOW 168.3X7.11 SA234WPB | NO | 1 | 2 | 5.08 | 10.16
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 1 | 2 | 0.43 | 0.86
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 20 | 32.371 | 64.742
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | 90DEG BW LR ELBOW 33.4X4.55 SA234WPB | NO | 3 | 6 | 0.6 | 1.2
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | ORIFICE PLATE ASSY PIPE OD 168.3X7.11 SA106GRB L=300 | M | 0.3 | 0.6 | 8.4786 | 16.9572
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | ORIFICE PLATE ASSY For Pipe NB150- SA515GR70 | NO | 1 | 2 | 2.22 | 4.44
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | LUG PLATE THICK12x340x170 SA515 GR70 | NO | 1 | 2 | 3.7 | 7.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | SPARE PIPE DIA 168.3 X 7.11 SA106GRB | M | 0.5 | 1 | 14.131 | 28.262
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | PIPE DIA 114.3 X 6.02 SA106GRB | M | 42 | 84 | 675.1292 | 1350.2584
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 9 | 18 | 34.56 | 69.12
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | BW LR 45DEG ELL OD114.3X6.02 SA234WPB | NO | 2 | 4 | 3.84 | 7.68
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 3 | 6 | 1.29 | 2.58
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 20 | 32.371 | 64.742
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | 90DEG BW LR ELBOW 33.4X4.55 SA234WPB | NO | 3 | 6 | 0.6 | 1.2
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | ORIFICE PLATE ASSY PIPE OD 114.3X6.02 SA106GRB L=300 | NO | 1 | 2 | 4.83 | 9.66
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | 0ORIFICE PLATE ASSY for Pipe NB100- SA515GR70 | NO | 1 | 2 | 1.026 | 2.052
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | SUPPORT PIPE OD88.9X7.62 L=254MM SA106GRB | NO | 2 | 4 | 7.76 | 15.52
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | SPARE PIPE DIA 114.3 X 6.02 SA106GRB | M | 2 | 4 | 32.149 | 64.298
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | PIPE DIA 114.3 X 6.02 SA106GRB | M | 47 | 94 | 755.5025 | 1511.005
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 9 | 18 | 34.56 | 69.12
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | BW LR 45DEG ELL OD114.3X6.02 SA234WPB | NO | 2 | 4 | 3.84 | 7.68
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 2 | 4 | 0.86 | 1.72
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 20 | 32.371 | 64.742
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | 90DEG BW LR ELBOW 33.4X4.55 SA234WPB | NO | 3 | 6 | 0.6 | 1.2
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | ORIFICE PLATE ASSY PIPE OD 114.3X6.02 SA106GRB L=300 | NO | 1 | 2 | 4.83 | 9.66
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | 0ORIFICE PLATE ASSY for Pipe NB100- SA515GR70 | NO | 1 | 2 | 0.026 | 0.052
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | SUPPORT PIPE OD88.9X7.62 L=254MM SA106GRB | NO | 2 | 4 | 7.76 | 15.52
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | SPARE PIPE DIA 114.3 X 6.02 SA106GRB | M | 2 | 4 | 32.149 | 64.298
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | PIPE DIA 114.3 X 6.02 SA106GRB | M | 35.589 | 71.178 | 572.076 | 1144.152
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 9 | 18 | 34.56 | 69.12
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | BW LR 45DEG ELL OD114.3X6.02 SA234WPB | NO | 1 | 2 | 1.92 | 3.84
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 2 | 4 | 0.86 | 1.72
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 20 | 32.371 | 64.742
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | 90DEG BW LR ELBOW 33.4X4.55 SA234WPB | NO | 3 | 6 | 0.6 | 1.2
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | ORIFICE PLATE ASSY PIPE OD 114.3X6.02 SA106GRB L=300 | NO | 1 | 2 | 4.83 | 9.66
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | 0ORIFICE PLATE ASSY for Pipe NB100- SA515GR70 | NO | 1 | 2 | 1.026 | 2.052
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | SUPPORT PIPE OD88.9X7.62 L=254MM SA106GRB | NO | 1 | 2 | 3.879 | 7.758
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | SUPPORT PLATE THICK10X100X100MM SA515 GR70 | NO | 1 | 2 | 0.785 | 1.57
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | SPARE PIPE DIA 114.3 X 6.02 SA106GRB | M | 2 | 4 | 32.149 | 64.298
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | PIPE DIA 355.6 X 9.53 SA106GRB | M | 40 | 80 | 3253.1937 | 6506.3874
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | PIPE OD 60.3x5.54 SA106GRB | M | 4 | 8 | 29.924 | 59.848
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | BW LR 90DEG ELL OD355.6X9.53 SA234WPB | NO | 4 | 8 | 272.4 | 544.8
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | BW LR 45DEG ELL OD355.6X9.53 SA234WPB | NO | 1 | 2 | 34.03 | 68.06
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | BW ELL 90 DEG OD 60.3x5.54 SA106GRB | NO | 5 | 10 | 4.5 | 9
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | BW UEQT 355.6X9.53/219.1x8.18 SA234WPB | NO | 1 | 2 | 65.93 | 131.86
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | BW REDUCER - OD355.6x9.53/OD323.9x9.53 SA234WPB | NO | 1 | 2 | 25.6184 | 51.2367
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | ASME B16.11 SW STUB NB25,CL:3000-SA105 | NO | 1 | 2 | 35.8206 | 71.6413
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | ASME B16.11 SW STUB NB50,CL:3000-SA105 | NO | 1 | 2 | 0.12807 | 0.25613
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | SUPPORT PIPE OD273X6.35 L=0.8 SA106GRB | M | 0.8 | 1.6 | 28.6565 | 57.313
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | SUPPORT PLATE THICK 10X300X300MM SA515GR70 | NO | 4 | 8 | 0.51227 | 1.0245
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | GAL WIRE MWSH 1.2x1200x2000 IS2062 FE410 | NO | 1 | 2 | 6.7519 | 13.5037
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | SPARE PIPE DIA 355.6 X 9.53 SA106GRB | M | 2 | 4 | 25.794 | 51.5879
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | PIPE DIA 355.6 X 9.53 SA106GRB | M | 32 | 64 | 40.7077 | 81.4155
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | PIPE DIA 273.0 X 6.35 SA106GRB | M | 3.5 | 7 | 11.7316 | 23.4632
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | BW LR 45DEG ELL OD355.6X9.53 SA234WPB | NO | 5 | 10 | 6.3606 | 12.7212
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | BW SR 90DEG ELL OD273X6.35 SA234WPB | NO | 5 | 10 | 124.88 | 249.76
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | BW RED 457.2X9.53/355.6X9.53 SA234WPB | NO | 5 | 10 | 179.1032 | 358.2064
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | DRIP PAN ASSY NB 250 (CS)-3.15THK,600DIA SA515GR70 | NO | 5 | 10 | 0.64033 | 1.2807
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | DRIP PAN ASSY NB 250 (CS)-3.15THK,100X1700 SA515GR70 | NO | 5 | 10 | 179.1032 | 358.2064
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | COVER PLATE FOR DRIP PAN - 10THK,600DIA SA515GR70 | NO | 5 | 10 | 0.64033 | 1.2807
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | SW RED NB25/15 CL3000 SA105 | NO | 5 | 10 | 0.65 | 1.3
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | NON-ASBESTOS JOINTING SHEET 3MM 1500X1500 | NO | 1 | 2 | 12.897 | 25.794
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | SOW FLANGE NB250 CL.150 SA105 | NO | 5 | 10 | 6.3606 | 12.7212
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | HEX.BOLT M24X120 IS1364 | NO | 75 | 150 | 251.391 | 502.782
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | HEX.NUT M24 IS1364 | NO | 75 | 150 | 95.4088 | 190.8175
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | GAL WIRE MESH 1.2X1200X2000 IS280 | NO | 5 | 10 | 31.2 | 62.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | SUPPORT PIPE OD219.1X6.35 SA106GRB | M | 5 | 10 | 166.575 | 333.15
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | BOTTOM PLATE 10X250X250 SA515GR70 | NO | 20 | 40 | 98.2 | 196.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | SPARE PIPE DIA 355.6 X 9.53 SA106GRB | M | 2 | 4 | 162.66 | 325.32
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | PIPE OD 355.6x9.53 - SA106GRB | M | 50 | 100 | 4065 | 8130
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | PIPE OD 273x6.35 - SA106GRB | M | 3 | 6 | 125.28 | 250.56
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | PIPE OD 168.3x7.11 - SA106GRB | M | 2 | 4 | 56.524 | 113.048
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | BW 90 DEG SR ELBOW 273X6.35 SA234WPB | NO | 2 | 4 | 49.952 | 99.904
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | BW 45 DEG LR ELBOW 355.6X9.53 SA234WPB | NO | 6 | 12 | 204.18 | 408.36
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | BW RED 457.2x9.53/355.6X9.53 SA234WPB | NO | 2 | 4 | 71.64 | 143.28
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | SW RED NB25/NB15 CL3000 SA234WPB | NO | 2 | 4 | 0.26 | 0.52
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | SUPPORT PIPE OD219.1x6.35 SA106GRB | M | 6 | 12 | 199.89 | 399.78
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | BOTTOM PLATE 10 THK 250X250-SA515GR70 | NO | 18 | 36 | 88.38 | 176.76
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | FLANGE 250NB CL150 SA515GR70 | NO | 2 | 4 | 30 | 60
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | DRIP PAN ASSY NB 250 (CS)-3.15THK,600DIA SA515GR70 | NO | 2 | 4 | 27.96 | 55.92
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | DRIP PAN ASSY NB 250 (CS)-3.15THK,100X1700 SA515GR70 | NO | 2 | 4 | 8.4 | 16.8
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | COVER PLATE FOR DRIP PAN - 10THK,600DIA SA515GR70 | NO | 2 | 4 | 0.44 | 0.88
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | HEX.BOLT M24x120 IS1364 | NO | 25 | 50 | 13.5 | 27
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | HEX.NUT M24 IS1364 | NO | 25 | 50 | 2.5 | 5
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | GALVANISED WIRE MESH 1.2 THKx1200x1200 IS280 | NO | 2 | 4 | 12 | 24
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | NON ASBESTOS JOINTING SHEET 3mm x1000x1000 | NO | 1 | 2 | 5.1 | 10.2
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | SPARE PIPE DIA 355.6 X 9.53 SA106GRB | M | 2 | 4 | 162.66 | 325.32
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | SOW FLANGE NB150 CL600 SA515GR70 | NO | 2 | 4 | 14.3 | 28.6
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | FT STUD M27X180 | NO | 2 | 4 | 1.54 | 3.08
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | NUT -M27 -2H | NO | 2 | 4 | 0.34 | 0.68
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | PIPE DIA 219.1x6.35 SA106GRB | M | 45 | 90 | 1499.175 | 2998.35
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | PIPE DIA 273x6.35 SA106GRB | M | 43 | 86 | 1796.1047 | 3592.2094
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | PIPE DIA 323.9x9.53 SA106GRB | M | 34 | 68 | 2511.92 | 5023.84
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW LR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 33 | 66 | 526.086 | 1052.172
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW LR 90DEG ELL OD273x6.35 SA234WPB | NO | 9 | 18 | 224.784 | 449.568
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW LR 90DEG ELL OD323.9x9.53 SA234WPB | NO | 5 | 10 | 265.2 | 530.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW EQT OD219.1x6.35 SA234WPB | NO | 4 | 8 | 77.08 | 154.16
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW UEQT OD323.9x9.53/OD219.1x6.35 SA234WPB | NO | 4 | 8 | 216.8 | 433.6
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW C.RED OD273x6.35/OD219.1x6.35 SA234WPB | NO | 8 | 16 | 54 | 108
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW C.RED OD323.9x9.53/OD219.1x6.35 SA234WPB | NO | 4 | 8 | 51.6 | 103.2
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | TEMPERATURE STUB M33X2, L=64 SA105 | NO | 6 | 12 | 2.1 | 4.2
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | PACKING RING M33x2 IS1972 SA105 | NO | 6 | 12 | 0.3 | 0.6
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SCREW PLUG M33 x 2 SA105 SA105 | NO | 6 | 12 | 2.4 | 4.8
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | PRESSURE STUB NB25 CLASS 3000 SA105 | NO | 6 | 12 | 1.2 | 2.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | FLAT END CLOSURE OD273x6.35 SA515 GR70 | NO | 4 | 8 | 69.84 | 139.68
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | CARRIER PLATE 16THK 80x50 SA515GR70 | NO | 20 | 40 | 10.04 | 20.08
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SUPPORT PIPE DIA 168.3 X 7.11 SA106GRB | M | 4 | 8 | 113.0471 | 226.0942
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SUPPORT PLATE TH10X200X200 SA515GR70 | NO | 10 | 20 | 6.28 | 12.56
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SPARE PIPE DIA 219.1x6.35 SA106GRB | M | 3 | 6 | 99.945 | 199.89
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SPARE PIPE DIA 273x6.35 SA106GRB | M | 2 | 4 | 83.539 | 167.078
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SPARE PIPE DIA 323.9x9.53 SA106GRB | M | 2 | 4 | 147.76 | 295.52
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | PIPE DIA 114.3 X 6.02 SA106GRB | M | 12 | 24 | 192.8304 | 385.6608
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | PIPE OD 60.3X 5.54 SA106GRB | M | 15 | 30 | 112.1999 | 224.3998
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 2 | 4 | 7.68 | 15.36
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | BW LR 45DEG ELL OD114.3X6.02 SA234WPB | NO | 1 | 2 | 1.92 | 3.84
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 SA234WPB | NO | 10 | 20 | 9 | 18
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | ASMEB16.9 BWLR 45DEG ELBOW OD60.3X5.54 SA234WPB | NO | 1 | 2 | 0.45 | 0.9
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | BW RED 114.3X6.02/60.3X5.54 SA234WPB | NO | 2 | 4 | 2.54 | 5.08
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | BW UEQT 114.3X6.02/60.3X5.54 SA234WPB | NO | 5 | 10 | 29.58 | 59.16
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | BW EQL TEE 60.3X5.54 SA234WPB | NO | 2 | 4 | 4.4 | 8.8
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | ORIFICE PLATE ASSY 200X200X10 SA515GR70 | NO | 5 | 10 | 15.7 | 31.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | SUPPORT PIPE OD48.3X5.08 SA106GRB | M | 2 | 4 | 11.492 | 22.984
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | SUPPORT PIPE OD88.9X7.62 SA106GRB | M | 3 | 6 | 45.8192 | 91.6385
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | PLATE 10THK 2000X1000 - SA515GR70 | NO | 1 | 2 | 157 | 314
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | CARRIER PLATE TH16X80X50 SA515GR70 | NO | 8 | 16 | 4 | 8
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | GAL WIRE MESH 1.2 X1200X1200 IS280 | NO | 1 | 2 | 6.24 | 12.48
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | SPARE PIPE DIA 114.3 X 6.02 SA106GRB | M | 1 | 2 | 16.069 | 32.138
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | SPARE PIPE OD 60.3X 5.54 SA106GRB | M | 1 | 2 | 7.479 | 14.958
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | PIPE DIA 168.3 X 7.11 SA106GRB | M | 38 | 76 | 1073.8802 | 2147.7604
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | PIPE OD 60.3X 5.54 SA106GRB | M | 48 | 96 | 359.0404 | 718.0808
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 5 | 10 | 52 | 104
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | BW 45 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 2 | 4 | 10.16 | 20.32
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 SA234WPB | NO | 19 | 38 | 17.1 | 34.2
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | ASMEB16.9 BWLR 45DEG ELBOW OD60.3X5.54 SA234WPB | NO | 2 | 4 | 0.9 | 1.8
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | BW RED 168.3X7.11/114.3X6.02 SA234WPB | NO | 2 | 4 | 6.7 | 13.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | BW RED 114.3X6.02/60.3X5.54 SA234WPB | NO | 2 | 4 | 2.54 | 5.08
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | SUPPORT PIPE OD114. 3X6.02 SA106GRB | M | 5 | 10 | 80.35 | 160.7
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | SUPPORT PIPE OD48.3X5.08 SA106GRB | M | 4 | 8 | 21.656 | 43.312
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | PLATE 10THK 750X750 - SA515GR70 | NO | 1 | 2 | 44.156 | 88.312
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | CARRIER PLATE 16X80X50 SA515GR70 | NO | 16 | 32 | 8.032 | 16.064
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | GAL WIRE MESH 1.2 X1200X2000 IS280 | NO | 1 | 2 | 6.2 | 12.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | SPARE PIPE DIA 168.3 X 7.11 SA106GRB | M | 2.5 | 5 | 70.65 | 141.3
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | SPARE PIPE OD 60.3X 5.54 SA106GRB | M | 3 | 6 | 22.44 | 44.88
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 508.00 X 9.53 - SA106GRB | M | 45 | 90 | 5271.525 | 10543.05
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 168.3 X 7.11 SA106GRB | M | 80 | 160 | 2260.8 | 4521.6
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 114.3 X 6.02 SA106GRB | M | 105 | 210 | 1687.875 | 3375.75
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 323.9 X 9.53 SA106GRB | M | 32 | 64 | 2364.16 | 4728.32
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BW LR 45DEG ELL OD508X9.53 SA234WPB | NO | 3 | 6 | 210.21 | 420.42
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | 90° BW LR ELBOW 323.9X9.53 SA234WPB | NO | 9 | 18 | 486 | 972
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BW LR 45DEG ELL 323.9X9.53SA234WPB | NO | 2 | 4 | 53 | 106
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 34 | 68 | 353.6 | 707.2
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BW 45 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 4 | 8 | 20.8 | 41.6
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 SA234WPB | NO | 30 | 60 | 115.2 | 230.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | ASMEB16.9 BWLR 45DEG ELBOW OD114.3X6.02 SA234WPB | NO | 2 | 4 | 3.84 | 7.68
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BWCONRED508X15.09/323.9X10.31 SA234WPB | NO | 2 | 4 | 153.88 | 307.76
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 12 | 24 | 5.16 | 10.32
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | TEMPERATURE STUB M33X2 L=45 SA105 | NO | 4 | 8 | 2 | 4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SCREW PLUG M33 X 2 SA105 | NO | 4 | 8 | 3.2 | 6.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PACKING RING IS1972 | NO | 4 | 8 | 0.4 | 0.8
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SUPPORT PIPE OD219.1x6.35 SA106GRB | M | 3 | 6 | 99.945 | 199.89
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SUPPORT PLATE 10 THK 250X250-SA515GR70 | NO | 8 | 16 | 39.2 | 78.4
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE OD 355.6x9.53 - SA106GRB | M | 4 | 8 | 325.32 | 650.64
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SUPPORT PLATE 10 THK 400X400-SA515GR70 | NO | 8 | 16 | 100.48 | 200.96
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | CARRIER PLATE 25X50X100 CS SA515GR70 | NO | 12 | 24 | 9.42 | 18.84
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | CARRIER PLATE 16X50X80 CS SA515GR70 | NO | 12 | 24 | 6.03 | 12.06
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | GI SHEET FOR RAIN HOOD 2.5X1200X2500 IS1079D | NO | 4 | 8 | 235.5 | 471
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | GAL WIRE MESH 1.2 X1200X2000 IS280 | NO | 2 | 4 | 12.48 | 24.96
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | ASBESTOS JOINTING SHEET 1.5MM | NO | 2 | 4 | 4.94 | 9.88
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SOW FLANGE NB 100 CL150 SA515GR70 | NO | 5 | 10 | 27.3 | 54.6
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SOW FLANGE NB150 CL150 SA515GR70 | NO | 6 | 12 | 42.9 | 85.8
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | FLAT END CLOSURE FOR OD114.3X6.02 SA234WPB | NO | 2 | 4 | 4.38 | 8.76
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BOLT-M16X90 -8.8-IS1364P1 | NO | 48 | 96 | 5.1 | 10.2
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | NUT -M16 -CL8-IS1364P3 | NO | 48 | 96 | 0.9 | 1.8
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | HEX HD BOLT M20X100,P.CL6.8 IS:1364(P-1) | NO | 48 | 96 | 20.262 | 40.524
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | NUT -M20 -CL6-IS1364P3 | NO | 48 | 96 | 4.29 | 8.58
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SPARE PIPE DIA 508.00 X 9.53 - SA106GRB | M | 2 | 4 | 234.29 | 468.58
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SPARE PIPE DIA 168.3 X 7.11 SA106GRB | M | 3 | 6 | 84.78 | 169.56
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SPARE PIPE DIA 114.3 X 6.02 SA106GRB | M | 3 | 6 | 48.21 | 96.42
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SPARE PIPE DIA 323.9 X 9.53 SA106GRB | M | 2 | 4 | 147.76 | 295.52
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 168.3 X 10.97 SA106GRB | M | 2 | 4 | 67.072 | 134.144
4 | Lara 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 114.3 X 13.49 SA106GRB | M | 2 | 4 | 67.072 | 134.144
4 Total | [10 empty] | 106377.1687
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | OD PIPE DIA 508.00 X 9.53 - SA106GRB | M | 85 | 170 | 9957.75 | 19915.5
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 8 | 16 | 1121.84 | 2243.68
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | BW LR 45DEG ELL OD508X9.53 SA234WPB | NO | 1 | 2 | 70.07 | 140.14
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | BW RED 610X10/508X9.53 SA234WPB | NO | 1 | 2 | 67.81 | 135.62
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | BRANCH PIPE OD 219.1 x 12.70 - SA106GRC L=1000 | M | 1 | 2 | 64.64 | 129.28
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SW STUB NB25 CL3000 CS SA105 | NO | 4 | 8 | 1.72 | 3.44
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SW STUB NB15 CL3000 CS SA105 | NO | 10 | 20 | 4.3 | 8.6
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | THERMOWELL STUB D65 H157 CS SA105 | NO | 2 | 4 | 7.2 | 14.4
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SW STUB 50NB SA105 OD80 L=80 | NO | 4 | 8 | 5.32 | 10.64
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | CARRIAR PLATE 20X55X120 SA515GR70 | NO | 4 | 8 | 4.12 | 8.24
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SUPPORT PIPE OD219.1X8.18 L=5M SA515GR70 | M | 5 | 10 | 212.7 | 425.4
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SUPPORT PLATE 12X2000X1000 SA515GR70 | NO | 1 | 2 | 188.4 | 376.8
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | LUG PLATE 16X628X390 SA515GR70 | NO | 1 | 2 | 19.5 | 39
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SPARE PIPE OD508.00 X 9.53 - SA106GRB | M | 2 | 4 | 234.3 | 468.6
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | TEMP STUB RC 1" L=45-SA105 | NO | 4 | 8 | 2.45 | 4.9
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SCREW PLUG RC 1" SA105 | NO | 4 | 8 | 0.7 | 1.4
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | PIPE DIA 660.0 X 10.0 SA672GRB70CL22 | M | 34 | 68 | 5450.2 | 10900.4
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | OD PIPE DIA 508.00 X 9.53 - SA106GRB | M | 27 | 54 | 3163.046 | 6326.0921
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW LR 90DEG ELL OD660.4X9.53 SA234WPB(W) | NO | 2 | 4 | 476.24 | 952.48
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW LR 30DEG ELL OD660.4X9.53 SA234WPB(W) | NO | 2 | 4 | 158.56 | 317.12
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW LR 53.8 DEG ELL OD660.4X9.53 SA234WPB(W) | NO | 1 | 2 | 142.205 | 284.41
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 3 | 6 | 420.69 | 841.38
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW LR 45DEG ELL OD508X9.53 SA234WPB | NO | 2 | 4 | 140.14 | 280.28
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW RED 610X10/508X9.53 SA234WPB(W) | NO | 2 | 4 | 135.62 | 271.24
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW RED 660X10/508X9.53 SA234WPB(W) | NO | 1 | 2 | 83.59 | 167.18
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW RED 660X10/610X10 SA234WPB(W) | NO | 2 | 4 | 188 | 376
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW UEQT 660X10/508X9.53 SA234WPB(W) | NO | 1 | 2 | 229 | 458
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BRANCH PIPE OD 219.1 X12.7 L=2.5 SA106GRB | M | 2.5 | 5 | 161.6 | 323.2
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SUPPORT PIPE OD 219.1 X12.7 L=1.5 SA106GRB | M | 1.5 | 3 | 96.96 | 193.92
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | FLAT END CLOSURE OD219.1X6.35 SA515GR70 | NO | 3 | 6 | 19.8 | 39.6
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | TEMP.STUB M33X2 (CS)L=64 SA105 | NO | 1 | 2 | 0.7 | 1.4
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SCREW PLUG CS (M33X2) SA105 | NO | 1 | 2 | 0.4 | 0.8
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | COPPER PACKING RING M33X2 IS1972 | NO | 1 | 2 | 0.1 | 0.2
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | TEMP STUB HWR SA105 OD80 L=45 | NO | 1 | 2 | 0.65 | 1.3
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SW STUB NB25 CL3000 CS SA105 OD50 H=54 | NO | 4 | 8 | 1.72 | 3.44
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SW STUB 50NB SA105 OD80 L=75 | NO | 4 | 8 | 5.32 | 10.64
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SW STUB 15NB SA105 OD36 L=44 | NO | 8 | 16 | 1.44 | 2.88
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | TEMP STUB RC 1" L=45-SA105 | NO | 4 | 8 | 2.45 | 4.9
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SCREW PLUG RC 1" SA105 | NO | 4 | 8 | 0.7 | 1.4
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | PIPE DIA 813.0 X 10.0 SA672GRB70CL22 | M | 24 | 48 | 4752 | 9504
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | PIPE DIA 660.0 X 10.0 SA672GRB70CL22 | M | 15 | 30 | 2404.5 | 4809
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 90DEG ELL OD813X10 SA234WPB(W) | NO | 1 | 2 | 379.19 | 758.38
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 30DEG ELL OD813X10 SA234WPB(W) | NO | 3 | 6 | 378 | 756
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 53.9 DEG ELL OD813X10 SA234WPB(W) | NO | 1 | 2 | 226 | 452
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 60DEG ELL OD813X10 SA234WPB(W) | NO | 2 | 4 | 504 | 1008
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW SR 90DEG ELL OD813X10 SA234WPB(W) | NO | 1 | 2 | 252 | 504
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 90DEG ELL OD660X10 SA234WPB | NO | 2 | 4 | 498.78 | 997.56
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 45DEG ELL OD660X10 SA234WPC(W) | NO | 5 | 10 | 623.45 | 1246.9
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW C RED 813X9.53/660.4X9.53 SA234WPB(W) | NO | 1 | 2 | 105 | 210
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW RED 660X9.53/610X9.53 SA234WPB(W) | NO | 2 | 4 | 179.5 | 359
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW RED 914X10/813X10 SA234WPB(W) | NO | 1 | 2 | 129.16 | 258.32
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW UEQT 813X9.53 /660.4X9.53 SA234WPB (W) | NO | 1 | 2 | 357 | 714
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BRANCH PIPE OD 323.9X 9.53 L=2.4 SA106GRB | M | 2.4 | 4.8 | 170.6667 | 341.3333
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | TEMP.STUB M33X2 (CS)L=64 SA105 | NO | 2 | 4 | 1.4 | 2.8
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SCREW PLUG CS (M33X2) SA105 | NO | 2 | 4 | 0.8 | 1.6
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | COPPER PACKING RING M33X2 IS1972 | NO | 2 | 4 | 0.2 | 0.4
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | TEMP STUB HWR SA105 OD80 L=45 | NO | 2 | 4 | 1.3 | 2.6
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SW STUB NB25 CL3000 CS SA105 OD50 H=54 | NO | 4 | 8 | 1.72 | 3.44
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SW STUB 50NB SA105 OD80 L=75 | NO | 4 | 8 | 5.32 | 10.64
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SW STUB 15NB SA105 OD36 L=44 | NO | 8 | 16 | 1.44 | 2.88
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SUPPORT PIPE OD508X9.53 L=800 SA106GRB | M | 0.8 | 1.6 | 93.716 | 187.432
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | TEMP STUB RC 1" L=45-SA105 | NO | 5 | 10 | 3.0625 | 6.125
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SCREW PLUG RC 1" SA105 | NO | 5 | 10 | 0.875 | 1.75
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BRANCH PIPE OD 219.1 X12.7 L=2.5 SA106GRB | M | 2.5 | 5 | 161.6 | 323.2
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | FLAT END CLOSURE for Pipe OD323.9X9.53 SA515GR70 | NO | 3 | 6 | 44.628 | 89.256
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | PIPE DIA 610.0 X 10.0 SA672GRB70CL22 | M | 45 | 90 | 6660 | 13320
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | PIPE DIA 406.4 X 9.53 SA106GRB | M | 85 | 170 | 7927.95 | 15855.9
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | PIPE OD-323.9X9.53-SA106GRC | M | 16 | 32 | 1182.08 | 2364.16
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | OD PIPE DIA 273.00 X 12.70-SA106GRC | M | 73 | 146 | 5950.96 | 11901.92
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | OD PIPE DIA 273.00 X 9.27 - SA106GRB | M | 25 | 50 | 1507 | 3014
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | PIPE 273.00 X 6.35 - SA106GRB | M | 69 | 138 | 2881.095 | 5762.19
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW LR 90DEG ELL 406.4X9.53SA234WPB | NO | 20 | 40 | 1787.4 | 3574.8
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW LR 45DEG ELL OD406.4X9.53 SA234WPB | NO | 5 | 10 | 223.3 | 446.6
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW LR 90DEG ELL OD323.9X9.53 SA234WPC | NO | 4 | 8 | 212.16 | 424.32
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW 90DEG SR ELBOW OD323.9X9.53 SA234WPC | NO | 2 | 4 | 74 | 148
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW LR 90DEG ELL OD273X12.7 SA234WPC | NO | 15 | 30 | 731.85 | 1463.7
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW LR 45DEG ELL OD273X12.7 SA234WPC | NO | 3 | 6 | 73.14 | 146.28
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW 90DEG LR EL OD273.1 X 9.27 SA234WPB | NO | 7 | 14 | 267.54 | 535.08
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW LR 90DEG ELL OD273X6.35 SA234WPB | NO | 6 | 12 | 157.2 | 314.4
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW LR 45DEG ELL OD273X6.35 SA234WPB | NO | 4 | 8 | 52.4 | 104.8
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW RED 610X9.53/559X9.53 SA234WPB | NO | 2 | 4 | 137.52 | 275.04
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | 16.9BW REDUCER OD610X9.53/406.4X9.53 SA234WPB | NO | 2 | 4 | 86 | 172
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW RED 323.9X9.53/273X6.35 SA234WPB | NO | 2 | 4 | 23.44 | 46.88
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW RED 406.4X9.53/323.9X9.53 SA234WPB | NO | 2 | 4 | 60.24 | 120.48
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW RED 406.4X9.53/273X6.35 SA234WPB | NO | 3 | 6 | 71.73 | 143.46
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW UNEQT 610 X 10/ 406.4 X 9.53 SA106GRB | NO | 1 | 2 | 263 | 526
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW UEQT 406.4X9.53/273X9.27 SA234WPB | NO | 4 | 8 | 376.16 | 752.32
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW UEQT 273X12.7/219.1X6.35 SA234WPC | NO | 4 | 8 | 204.08 | 408.16
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW EQT OD406.4X9.53 SA234WPB | NO | 2 | 4 | 180.98 | 361.96
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW EQT OD273X12.7 SA234WPC | NO | 2 | 4 | 113.66 | 227.32
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW UEQT 323.9X9.53/168.3X10.97 SA234WPC | no | 2 | 4 | 108.92 | 217.84
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | TEMP STUB RC 1";L=45 OD55 SA105 | NO | 6 | 12 | 6.618 | 13.236
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SCREW PLUG R 1" SA105 | NO | 6 | 12 | 2.07 | 4.14
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | TEMP STUB M33X2 L=45 CS SA105 | NO | 4 | 8 | 7.108 | 14.216
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SCREW PLUG M33X2 CS SA105 | NO | 4 | 8 | 2.772 | 5.544
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | COPPER PACKING RING M33X2 IS1972 | NO | 4 | 8 | 0.04 | 0.08
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SW STUB NB25 CL3000 SA105 | NO | 20 | 40 | 13.96 | 27.92
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | THERMOWELL STUB OD70H80 CS SA105 | NO | 2 | 4 | 3.4 | 6.8
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | CARRIER PLATE 20X50X120 CS SA515GR70 | NO | 36 | 72 | 36 | 72
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BRANCH PIPE OD 219.1 X12.7 L=400 SA106GRC | M | 2 | 4 | 129.28 | 258.56
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BRANCH PIPE DIA 114.30 X 11.13 - SA106GRB | M | 2 | 4 | 56.58 | 113.16
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD114.3X6.02 L=10500 SA106GRB | M | 10.5 | 21 | 168.782 | 337.564
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD168.3X7.11 L=1M SA106GRB | M | 1 | 2 | 28.2633 | 56.5267
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD219.1X8.18 L=5300 SA106GRB | M | 5.3 | 10.6 | 225.497 | 450.994
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | LUG PLATE 16X443X260 SA515GR70 | NO | 1 | 2 | 9.4 | 18.8
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | PLATE 20THKX4000X4000 SA515GR70 | NO | 1 | 2 | 2512 | 5024
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SW STUB 15NB SA105 OD36 L=44 | NO | 15 | 30 | 2.7 | 5.4
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | TEMP STUB RC 1";L=45 OD55 SA105 | NO | 6 | 12 | 6.618 | 13.236
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SCREW PLUG R 1" SA105 | NO | 6 | 12 | 2.07 | 4.14
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | TEMP STUB M33X2 L=45 CS SA105 | NO | 4 | 8 | 7.108 | 14.216
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SCREW PLUG M33X2 CS SA105 | NO | 4 | 8 | 2.772 | 5.544
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | COPPER PACKING RING M33X2 IS1972 | NO | 4 | 8 | 0.04 | 0.08
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SW STUB NB25 CL3000 SA105 | NO | 20 | 40 | 13.96 | 27.92
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | THERMOWELL STUB OD70H80 CS SA105 | NO | 2 | 4 | 3.4 | 6.8
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | CARRIER PLATE 20X50X120 CS SA515GR70 | NO | 36 | 72 | 36 | 72
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD114.3X6.02 L=10500 SA106GRB | M | 10.5 | 21 | 168.782 | 337.564
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD168.3X7.11 L=1M SA106GRB | M | 1 | 2 | 28.2633 | 56.5267
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD219.1X8.18 L=5300 SA106GRB | M | 5.3 | 10.6 | 225.497 | 450.994
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | LUG PLATE 16X443X260 SA515GR70 | NO | 1 | 2 | 9.4 | 18.8
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | PLATE 20THKX4000X4000 SA515GR70 | NO | 1 | 2 | 2512 | 5024
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SW STUB 15NB SA105 OD36 L=44 | NO | 15 | 30 | 2.7 | 5.4
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | PIPE OD965x38 SA672GRB70CL22 | M | 2.5 | 5 | 2171.675 | 4343.35
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | PIPE OD965x10 SA672GRB70CL22 | M | 10 | 20 | 2355 | 4710
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SPARE PIPE OD406.4x21.44 SA106 GR.C | M | 1 | 2 | 203.545 | 407.09
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | PIPE OD406.4X21.44, SA106GRC | M | 31 | 62 | 6309.895 | 12619.79
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | PIPE OD323.9X9.53, SA106GRB | M | 1.5 | 3 | 110.82 | 221.64
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BRANCH PIPE OD323.9X12.7, SA106GRB | M | 1 | 2 | 97.46 | 194.92
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BRANCH PIPE OD114.3X13.49, SA106GRC | M | 1 | 2 | 33.54 | 67.08
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BW LR 90DEG ELL OD965X10 SA234WPB(W) | NO | 3 | 6 | 1607.07 | 3214.14
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BW 90DEG LR ELBOW OD406.4x21.44 SA234WPC | NO | 7 | 14 | 1364.44 | 2728.88
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BW RED 965x38/711x10 SA234WPB | NO | 1 | 2 | 466.722 | 933.444
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BW UNEQT OD965X10/508X9.53 SA234WPB | NO | 1 | 2 | 476.81 | 953.62
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BW EQT OD965X10 SA234WPB | NO | 1 | 2 | 529.79 | 1059.58
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | FLAT END CLOSURE for Pipe OD323.9X9.53 SA515GR70 | NO | 1 | 2 | 31.617 | 63.234
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | FLAT END CLOSURE for Pipe OD219.1X8.18 SA515GR70 | NO | 1 | 2 | 8.63 | 17.26
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | FLAT END CLOSURE for Pipe OD114.3X6.02 SA515GR70 | NO | 1 | 2 | 2.77 | 5.54
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD273X9.53 L=1500 SA106GRB | M | 1.5 | 3 | 92.883 | 185.766
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD323X9.53 L=2500 SA106GRB | M | 2.5 | 5 | 184.7 | 369.4
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SW STUB NB25 CL6000 CS SA105 | NO | 8 | 16 | 4.56 | 9.12
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SW STUB NB25 CL3000 CS SA105 OD50 H=54 | NO | 5 | 10 | 2.15 | 4.3
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SW STUB NB15 CL3000 CS SA105 OD36 H=44 | NO | 14 | 28 | 2.52 | 5.04
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | TEMPERATURE STUB M33X2 (CS) SA105 ( D-78 , H-45) (ROD-80) | NO | 3 | 6 | 3.36 | 6.72
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SCREW PLUG M33X2 CS SA105 | NO | 3 | 6 | 1.2 | 2.4
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | PACKING RING IS1972 | NO | 3 | 6 | 0.03 | 0.06
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | TEMP.STUB L=45 SA105 ( HWR ) ROD-80 DIA | NO | 2 | 4 | 1.3 | 2.6
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | TEMP.STUB RC 1 "(CS) D55 , L=45 SA105 (ROD-D63) | NO | 8 | 16 | 5.6 | 11.2
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SCREW PLUG R 1 " (CS) SA105 (ROD-D40) | NO | 8 | 16 | 1.6 | 3.2
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | CARRIER PLATE 20X50X120 SA515GR70 | NO | 24 | 48 | 21.12 | 42.24
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | LUG PLATE 16X559X325 SA515GR70 | NO | 2 | 4 | 29.6 | 59.2
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SUPPORT PLATE 20X1500X2000 SA515GR70 | NO | 1 | 2 | 471 | 942
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SUPPORT PLATE 10X2000X1000 SA515GR70 | NO | 2 | 4 | 157 | 314
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | THERMOWELL STUB SA105 OD-70, H-80 (ROD-80) | NO | 5 | 10 | 8.5 | 17
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | PIPE OD323.9X21.44 SA335P22 | M | 28 | 56 | 4477.844 | 8955.688
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | PIPE OD273.00 X 18.26 - SA335P22 | M | 44 | 88 | 5047.416 | 10094.832
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SPARE PIPE OD273.00 X 18.26 - SA335P22 | M | 1.5 | 3 | 172.071 | 344.142
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | PIPE OD219.1X15.09 - SA335P22 | M | 19 | 38 | 1442.499 | 2884.998
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | PIPE OD114.30 X 8.56 - SA335P22 | M | 1.5 | 3 | 33.483 | 66.966
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW 90DEG LR ELBOW OD323.9X21.44 SA234WP22 | NO | 4 | 8 | 458.96 | 917.92
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW 90DEG LR ELBOW OD273X18.26 SA234WP22 | NO | 12 | 24 | 823.32 | 1646.64
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW LR 45DEG ELL 273 X 18.26 SA234WP22 | NO | 2 | 4 | 68.62 | 137.24
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW 90DEG LR ELBOW OD219.1X15.09 SA234WP22CL1 | NO | 3 | 6 | 109.05 | 218.1
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW LR 45DEG ELL 168.3X18.26 SA234WP22CL1 | NO | 2 | 4 | 25 | 50
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW C RED OD323.9x21.44 / 273x18.26 SA234WP22CL1 | NO | 3 | 6 | 89.82 | 179.64
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW C RED OD323.9x21.44 / 219.1X15.09 SA234WP22CL1 | NO | 1 | 2 | 27.69 | 55.38
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW C RED OD219.1X15.09 / 168.3X18.26 SA234WP22CL1 | NO | 2 | 4 | 23.88 | 47.76
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW C RED OD273.1X16/219.1X15.09,SA234WP22CL1 | NO | 2 | 4 | 36.9 | 73.8
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW UNEQT OD323.9X21.44/219.1X15.09 SA234WP22CL1 | NO | 1 | 2 | 117.66 | 235.32
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW UNEQT OD323.9X21.44/273X18.26 SA234WP22CL1 | NO | 1 | 2 | 123 | 246
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | STUB OD114.3X13.49 SA182 F22 CL3 L=250 | NO | 2 | 4 | 25.74 | 51.48
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | FLAT END CLOSURE OD114.3X8.56 SA387 GR22 (OD 115X30THK) | NO | 2 | 4 | 4.84 | 9.68
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SW STUB NB40 CL6000 SA182F22CL3 OD70 H=60 | NO | 2 | 4 | 3.4 | 6.8
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SW STUB NB50 CL6000 SA182F22CL3 OD84 H=60 | NO | 4 | 8 | 7.84 | 15.68
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SW STUB NB25 CL6000 SA182F22CL3 OD060 H=60 | NO | 16 | 32 | 9.12 | 18.24
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | THERMOWELL STUB D120 H-80 SA182F22CL3 | NO | 5 | 10 | 26 | 52
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | TEMPERATURE STUB RC-1.5'' OD124 L-45 SA182F22CL3 | NO | 14 | 28 | 39.62 | 79.24
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SCREW PLUG RC 1.5 '' SA182 F22 | NO | 14 | 28 | 7 | 14
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | CARRIER PLATE 20X55X120 SA387GR22CL2 | NO | 12 | 24 | 12.432 | 24.864
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SUPPORT PIPE OD114.3X13.49 L=1000 SA335P22 (2 - NO ) | M | 1 | 2 | 33.54 | 67.08
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SUPPORT PIPE OD168.3X18.26 L=1000 SA335P22 ( 2 - NO ) | M | 1 | 2 | 42.56 | 85.12
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | TEMPERATURE STUB M33X2 (AS) SA182F22 ( D-78 , H-45) (ROD-80) | NO | 2 | 4 | 2.24 | 4.48
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SCREW PLUG M33X2 SA182F22 | NO | 2 | 4 | 0.8 | 1.6
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | PACKING RING IS1972 | NO | 2 | 4 | 0.02 | 0.04
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | PIPE OD406.4X21.44 SA106GRC | M | 42 | 84 | 8548.89 | 17097.78
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SPARE PIPE OD406.4X21.44 SA106GRC | M | 1 | 2 | 203.545 | 407.09
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | PIPE 323.90 X 14.27 - SA106GRC | M | 18 | 36 | 1961.1 | 3922.2
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | BW 90DEG LR ELBOW OD406.4X21.44 SA234 WPC | NO | 13 | 26 | 2533.96 | 5067.92
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | BW 90DEG LR EL OD323.9X14.27 SA234WPC | NO | 11 | 22 | 859.98 | 1719.96
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | BW RED 323.9X14.27/273X12.7 SA234WPC | NO | 2 | 4 | 40.88 | 81.76
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | BW UEQT OD406.4X21.44/OD323.9X14.27 SA234WPC | NO | 2 | 4 | 370.62 | 741.24
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SUPPORT PIPE OD323.9X9.53 L=1000 SA106GRC | M | 1 | 2 | 73.88 | 147.76
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SUPPORT PIPE OD168.3X10.97 L=1000 SA106GRC | M | 1 | 2 | 42.56 | 85.12
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | TEMP.STUB RC 1-1/2"(CS) D98 L=45 SA105 (ROD-100) | NO | 10 | 20 | 17 | 34
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SCREW PLUG R 1-1/2"(CS) SA105 ( ROD-50) | NO | 10 | 20 | 5 | 10
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | TEMP.STUB- CS D78 L-45 M33X2 SA105 (ROD-80) | NO | 2 | 4 | 2.24 | 4.48
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SCREW PLUG CS (M33X2) SA105 (ROD-50) | NO | 2 | 4 | 0.8 | 1.6
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | COPPER PACKING RING M33X2 IS1972 | NO | 2 | 4 | 0.02 | 0.04
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SW STUB CS NB25 CL:6000 SA105 | NO | 10 | 20 | 5.7 | 11.4
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | THERMOWELL STUB WELDED D114 H95 CS SA105 (ROD-125mm) | NO | 4 | 8 | 19 | 38
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | CARRIER PLATE 20THKX50X120 SA515GR70 | NO | 4 | 8 | 3.52 | 7.04
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SUPPORT PLATE 10THKX1000X1000 SA515GR70 | NO | 1 | 2 | 78.5 | 157
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | PIPE OD 406.4X12.7 -SA335P22 | M | 47 | 94 | 5781 | 11562
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | SPARE PIPE OD 406.4X12.7 -SA335P22 | M | 1 | 2 | 123 | 246
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | PIPE DIA 273.0 X 9.27 SA335P22 | M | 9 | 18 | 542.79 | 1085.58
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | PIPE OD 355.6X12.7 -SA335P22 | M | 1 | 2 | 53.698 | 107.396
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | BW 90DEG LR ELBOW OD 406.4X12.7 -SA234 WP22 | NO | 9 | 18 | 1080 | 2160
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | BW LR 90DEG ELL OD273X9.27 SA234WP22CL1 | NO | 5 | 10 | 180.4 | 360.8
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | RED OD457X12.7/406.4X12.7 SA234 WP22 | NO | 1 | 2 | 50.065 | 100.13
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | RED OD406.4X12.7/355.6X12.7 SA234 WP22 | NO | 2 | 4 | 82.266 | 164.532
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | C RED OD406.4X12.7/OD273X12.7 SA234WP22CL1 | NO | 1 | 2 | 37.06 | 74.12
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | BW UEQT 406.4X12.7/273X9.27 SA234WP22CL1 | NO | 1 | 2 | 109 | 218
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | BW UEQT 406.4X12.7/168.3x7.11 SA234WP22CL1 | NO | 2 | 4 | 209.72 | 419.44
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | BRANCH PIPE OD168.3X10.97 L=1500 SA335P22 | M | 1.5 | 3 | 63.75 | 127.5
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | SUPPORT PIPE OD168.3X10.97 L=300 SA335P22 | M | 0.3 | 0.6 | 12.75 | 25.5
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | TEMPERATURE STUB RC 1-1/2'' OD125 L45 SA182F22CL3 | NO | 12 | 24 | 33.96 | 67.92
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | SCREW PLUG RC1-1/2'' SA182F22CL3 | NO | 12 | 24 | 6 | 12
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | TEMPERATURE STUB HWR OD50 : L=45 SA182F22CL3 | NO | 2 | 4 | 0.74 | 1.48
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | SW STUB NB25 CL6000 F22 SA182F22CL3 | NO | 14 | 28 | 7.98 | 15.96
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | THERMOWELL STUB(TW) OD78 H=64 SA182F22CL3 | NO | 5 | 10 | 9 | 18
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | SW STUB NB50 CL3000 F22 SA182F22CL3 | NO | 2 | 4 | 2.66 | 5.32
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | CARRIER PLATE 20X55X120 SA387GR22CL2 | NO | 4 | 8 | 4.144 | 8.288
5 | Lara 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | FLAT END CAP OD168.3X7.11 SA387 Gr22 OD169X32 | NO | 2 | 4 | 11.26 | 22.52
5 Total | [10 empty] | 249743.7098
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | PIPE DIA 323.9 X 9.53 SA106GRB | M | 4 | 8 | 295.52 | 591.04
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | PIPE DIA 219.1 X 6.35 X 6500 - SA106GRB | M | 50 | 100 | 1665.5 | 3331
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | PIPE DIA 168.3 X 7.11 SA106GRB | M | 77 | 154 | 2176.02 | 4352.04
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | PIPE DIA 114.3 X 6.02 SA106GRB | M | 27 | 54 | 433.89 | 867.78
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW LR 90DEG ELL OD219.1X6.35 SA234WPB | NO | 12 | 24 | 206.52 | 413.04
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW LR 60DEG ELL OD219.1X6.35 SA234WPB | NO | 1 | 2 | 12.09 | 24.18
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 16 | 32 | 179.68 | 359.36
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW 45°LR ELBOW 168.3X7.11 SA234WPB | NO | 2 | 4 | 11.22 | 22.44
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 7 | 14 | 26.88 | 53.76
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW LR 30DEG ELL OD114.3X6.02 SA234WPB | NO | 2 | 4 | 2.56 | 5.12
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW RED 323.9X9.53/168.3X7.11 SA234WPB | NO | 1 | 2 | 11.26 | 22.52
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW RED 219.1X6.35/168.3X7.11 SA234WPB | NO | 1 | 2 | 4.84 | 9.68
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW RED 168.3X7.11/114.3X6.02 SA234WPB | NO | 1 | 2 | 3.16 | 6.32
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW EQT OD168.3X7.11 SA234WPB | NO | 1 | 2 | 13.28 | 26.56
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW UEQT 323.9X6.35/114.3X6.02 SA234WPB | NO | 1 | 2 | 35.68 | 71.36
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | SUPPORT PIPE DIA 168.3 X 7.11 SA106GRB | M | 1.7 | 3.4 | 48.042 | 96.084
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | SUPPORT PIPE DIA 114.3 X 6.02 SA106GRB | M | 2 | 4 | 32.14 | 64.28
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | SUPPORT PIPE DIA 88.9X6.02 SA106GRB | M | 0.6 | 1.2 | 7.38 | 14.76
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BOTTOM PLATE 10MM THK 1000X1000 SA515GR70 | NO | 1 | 2 | 78.5 | 157
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | LUG PLATE 12MM THK 340X170 SA515GR70 | NO | 1 | 2 | 3.7 | 7.4
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | SW STUB NB25 CL3000 CS OD36,H=44 SA105 | NO | 4 | 8 | 1.72 | 3.44
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | CARRIER PLATE 16X50X120 SA515GR70 | NO | 4 | 8 | 3 | 6
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | PIPE OD114.3X6.02 SA106GRB | M | 36 | 72 | 578.88 | 1157.76
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | PIPE OD168.3X7.11 SA106GRB | M | 45 | 90 | 1271.7 | 2543.4
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 12 | 24 | 52.08 | 104.16
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 14 | 28 | 157.22 | 314.44
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | BW RED 168.3X7.11/114.3X6.02 SA234WPB | NO | 3 | 6 | 9.87 | 19.74
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | BW UEQT OD168.3X7.11/114.3X6.02 SA234WPB | NO | 3 | 6 | 42 | 84
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | SW STUB NB25 OD46 H=44 SA105 | NO | 4 | 8 | 1.72 | 3.44
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | SUPPORT PLATE 10MM THK 500x500 SA515GR70 | NO | 1 | 2 | 19.63 | 39.26
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | SUPPORT PIPE DIA 88.9X6.02 SA106GRB | M | 2 | 4 | 24.6 | 49.2
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | EQT 33.4X4.55 SA234WPB | NO | 2 | 4 | 0.86 | 1.72
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | ELBOW 90DEG OD33.4X4.55 SA234WPB | NO | 4 | 8 | 1 | 2
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | PIPE OD 33.4X4.55 SA106GRB | M | 6 | 12 | 19.44 | 38.88
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | PIPE OD 21.3X3.73 SA106GRB | M | 5 | 10 | 8.1 | 16.2
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | PIPE OD273x12.7x6000 - SA106 Gr.C | M | 200 | 400 | 16176 | 32352
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | PIPE OD323.9x12.7x6000 - SA106 Gr.C | M | 5 | 10 | 487.3 | 974.6
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SUPPORT PIPE OD273x12.7x6000 - SA106 Gr.C | M | 1 | 2 | 81.52 | 163.04
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SUPPORT PIPE OD219.1x12.7x6000 - SA106 Gr.C | M | 7.5 | 15 | 484.8 | 969.6
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SUPPORT PIPE OD114.3x6.02x6000 - SA106 Gr.C | M | 2 | 4 | 32.12 | 64.24
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW LR 90DEG ELL OD273x12.7 SA234WPC | NO | 50 | 100 | 2617.5 | 5235
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW LR 45DEG ELL OD273x12.7 SA234WPC | NO | 12 | 24 | 314.04 | 628.08
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW RED 273.1X12.7 / 168.3X8.56 SA234WPC | NO | 4 | 8 | 48.28 | 96.56
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW RED 273X12.7 / 219.1x12.7 SA234WPC | NO | 2 | 4 | 26.28 | 52.56
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW RED 323.9X12.7 / 219.1x12.7 SA234WPC | NO | 2 | 4 | 33.96 | 67.92
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW RED 323.9X12.7 / 273x12.7 SA234WPC | NO | 6 | 12 | 109.74 | 219.48
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | ASME B16.11 SW STUB NB25,CL:6000 SA105 | NO | 16 | 32 | 9.12 | 18.24
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | TEMP STUB RC 1.5" L=45-SA105 | NO | 18 | 36 | 31.86 | 63.72
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SCREW PLUG RC 1.5" SA105 | NO | 18 | 36 | 9 | 18
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | THERMOWEL STUB OD-63.5 H=154-SA105 C.S | NO | 4 | 8 | 12.408 | 24.816
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | CARRIER PLATE 12X80X40-SA515GR70 | NO | 16 | 32 | 4.816 | 9.632
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | LUG PLATE 16x443x260 SA515 GR70 | NO | 5 | 10 | 72.35 | 144.7
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BOTTOM PLATE 10THKX150X150 SA515 GR70 | NO | 4 | 8 | 7.04 | 14.08
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BOTTOM PLATE 10THKX250X250 SA515 GR70 | NO | 12 | 24 | 58.875 | 117.75
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BOTTOM PLATE 10THKX300X300 SA515 GR70 | NO | 1 | 2 | 7.065 | 14.13
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | TEMPERATURE STUB M33X2, L=64 SA105 | NO | 4 | 8 | 2.8 | 5.6
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | PACKING RING M33x2 IS1972 | NO | 4 | 8 | 0.04 | 0.08
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SCREW PLUG M33 x 2 SA105 SA105 | NO | 4 | 8 | 0.64 | 1.28
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SPARE PIPE OD273x12.7x6000 - SA106 Gr.C | M | 4 | 8 | 323.2 | 646.4
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | PIPE OD273X6.35x6000 - SA106 Gr.B | M | 175 | 350 | 7308 | 14616
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | PIPE OD273X12.7x6000 - SA106 Gr.B | M | 7 | 14 | 570.71 | 1141.42
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | PIPE OD323.9X12.7x6000 - SA106 Gr.B | M | 2.5 | 5 | 243.65 | 487.3
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SUPPORT PIPE OD114.3x6.02 SA106GR.B | M | 6 | 12 | 96.48 | 192.96
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SUPPORT PIPE OD168.3x7.11 SA106GR.B | M | 3 | 6 | 84.78 | 169.56
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SUPPORT PIPE OD219.1x12.7 SA106GR.B | M | 3 | 6 | 193.92 | 387.84
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SPARE PIPE OD273x6.35 SA106GR.B | M | 3 | 6 | 125.28 | 250.56
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW LR 90DEG ELL OD273x6.35 SA234WPB | NO | 29 | 58 | 777.49 | 1554.98
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW LR 60DEG ELL OD273x6.35 SA234WPB | NO | 3 | 6 | 54 | 108
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW LR 45DEG ELL OD273x6.35 SA234WPB | NO | 3 | 6 | 40.23 | 80.46
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW LR 30DEG ELL OD273x6.35 SA234WPB | NO | 4 | 8 | 36 | 72
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW LR 90DEG ELL OD 355.6x9.53 SA234WPB | NO | 2 | 4 | 136.2 | 272.4
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW RED 355.6x9.53 / 273X6.35 SA234WPB | NO | 4 | 8 | 95.204 | 190.408
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW RED 323.9X12.7 / 219.1x12.7 SA234WPC | NO | 2 | 4 | 43.968 | 87.936
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW RED 273.1X12.7 / 168.3X8.56 SA234WPC | NO | 4 | 8 | 48.32 | 96.64
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW RED 273X12.7 / 219.1x12.7 SA234WPC | NO | 2 | 4 | 26.28 | 52.56
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | ASME B16.11 SW STUB NB15,CL:3000 SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 6 | 12 | 2.58 | 5.16
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | TEMP STUB RC 1" L=45-SA105 | NO | 18 | 36 | 9.284 | 18.568
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SCREW PLUG RC 1" SA105 | NO | 18 | 36 | 3.6 | 7.2
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | THERMOWEL STUB OD-70 H=157-SA105 | NO | 4 | 8 | 14.4 | 28.8
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | LUG PLATE 16x443x260 SA515 GR70 | NO | 2 | 4 | 28.932 | 57.864
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BOTTOM PLATE 10THKX250X250 SA515 GR70 | NO | 4 | 8 | 19.624 | 39.248
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BOTTOM PLATE 10THKX200X200 SA515 GR70 | NO | 20 | 40 | 62.8 | 125.6
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BOTTOM PLATE 10THKX350X350 SA515 GR70 | NO | 2 | 4 | 19.232 | 38.464
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | PIPE OD219.1X6.35x6000 - SA106 Gr.B | M | 60 | 120 | 1999.2 | 3998.4
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | PIPE OD219.1X12.7x6000 - SA106 Gr.B | M | 4 | 8 | 258.56 | 517.12
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | SUPPORT PIPE OD168.3x7.11 SA106GR.B | M | 3.5 | 7 | 98.91 | 197.82
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW LR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 13 | 26 | 223.73 | 447.46
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW LR 45DEG ELL OD219.1x6.35 SA234WPB | NO | 2 | 4 | 17.2 | 34.4
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW LR 30DEG ELL OD219.1x12.7 SA234WPB | NO | 1 | 2 | 11.13 | 22.26
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW LR 90EG ELL OD273x12.7 SA234WPB | NO | 1 | 2 | 52.47 | 104.94
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW RED 273X6.35 / 219.1X6.35 SA234WPB | NO | 2 | 4 | 13.5 | 27
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW RED 273X12.7 / 219.1X12.7 SA234WPB | NO | 1 | 2 | 13.14 | 26.28
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW RED OD219.1x6.35/168.3x10.97 SA234WPB | NO | 2 | 4 | 8 | 16
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW RED OD219.1x12.7/168.3x10.97 SA234WPB | NO | 2 | 4 | 17.46 | 34.92
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW EQT 219.1x12.7 SA234WPB | NO | 1 | 2 | 37.4 | 74.8
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 3 | 6 | 1.29 | 2.58
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | TEMPERATURE STUB M33x2 L=64 -SA105 | NO | 1 | 2 | 0.7 | 1.4
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | SCREW PLUG M33 X 2-SA105 | NO | 1 | 2 | 0.16 | 0.32
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | PACKING RING M33x2 - IS1972 | NO | 1 | 2 | 0.01 | 0.02
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | TEMP STUB RC 1" L=64-SA105 | NO | 7 | 14 | 4.9 | 9.8
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | SCREW PLUG RC 1" SA105 | NO | 7 | 14 | 1.4 | 2.8
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BOTTOM PLATE 10THKX1000X1500 SA515 GR70 | NO | 1 | 2 | 117.75 | 235.5
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | PIPE OD273X12.7x6000 - SA106 Gr.B | M | 39 | 78 | 3179.28 | 6358.56
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | SUPPORT PIPE OD219.1x12.7 L=1.5 SA106GR.B | M | 1.5 | 3 | 96.96 | 193.92
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | BW LR 90DEG ELL OD273x12.7 SA234WPB | NO | 23 | 46 | 1206.81 | 2413.62
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | BW LR 60DEG ELL OD273x12.7 SA234WPB | NO | 3 | 6 | 104.94 | 209.88
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | BW EQT 273x12.7 SA234WPB | NO | 1 | 2 | 56.83 | 113.66
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | BW RED 406.4x17 / 273x12.7 SA234WPB | NO | 1 | 2 | 48.96 | 97.92
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 3 | 6 | 1.29 | 2.58
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | TEMP STUB RC 1" L=64-SA105 | NO | 6 | 12 | 4.2 | 8.4
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | SCREW PLUG RC 1" SA105 | NO | 6 | 12 | 1.2 | 2.4
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | TEMPERATURE STUB M33x2 L=64 -SA105 | NO | 2 | 4 | 1.4 | 2.8
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | SCREW PLUG M33 X 2-SA105 | NO | 2 | 4 | 0.32 | 0.64
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | PACKING RING M33x2 - IS1972 | NO | 2 | 4 | 0.02 | 0.04
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | LUG PLATE 16x443x260 SA515 GR70 | NO | 1 | 2 | 14.46 | 28.92
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | BOTTOM PLATE 10THKX250X250 SA515 GR70 | NO | 4 | 8 | 19.64 | 39.28
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | SPARE PIPE OD273X12.7 - SA106 Gr.B | M | 1 | 2 | 81.52 | 163.04
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | PIPE OD273X12.7x6000 - SA106 Gr.B | M | 34 | 68 | 2771.68 | 5543.36
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | PIPE OD2191.X6.35x6000 - SA106 Gr.B | M | 45 | 90 | 1498.95 | 2997.9
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SPARE PIPE OD219.1x12.7 SA106GR.B | M | 1 | 2 | 64.64 | 129.28
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SUPPORT PIPE OD168.3x7.11 SA106GR.B | M | 2 | 4 | 56.52 | 113.04
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW SR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 1 | 2 | 11.46 | 22.92
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW LR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 7 | 14 | 120.47 | 240.94
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW LR 45DEG ELL OD219.1x6.35 SA234WPB | NO | 5 | 10 | 43 | 86
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW LR 30DEG ELL OD219.1x6.35 SA234WPB | NO | 4 | 8 | 23 | 46
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW LR 90DEG ELL OD273x12.7 SA234WPB | NO | 11 | 22 | 577.17 | 1154.34
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW LR 45DEG ELL OD273x12.7 SA234WPB | NO | 1 | 2 | 26.24 | 52.48
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW RED 323.9x9.53 / 273x12.7 SA234WPB | NO | 1 | 2 | 13.88 | 27.76
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW RED 323.9x9.53/ 219.1X6.35 SA234WPB | NO | 1 | 2 | 12.9 | 25.8
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW RED 273x6.35/219.1X6.35 SA234WPB | NO | 1 | 2 | 6.75 | 13.5
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 2 | 4 | 0.86 | 1.72
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | TEMPERATURE STUB M33x2 L=64 -SA105 | NO | 2 | 4 | 1.4 | 2.8
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SCREW PLUG M33 X 2-SA105 | NO | 2 | 4 | 0.32 | 0.64
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | PACKING RING M33x2 - IS1972 | NO | 2 | 4 | 0.02 | 0.04
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | TEMP STUB RC 1" L=64-SA105 | NO | 4 | 8 | 2.8 | 5.6
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SCREW PLUG RC 1" SA105 | NO | 4 | 8 | 0.8 | 1.6
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | LUG PLATE 16x443x260 SA515 GR70 | NO | 1 | 2 | 14.47 | 28.94
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BOTTOM PLATE 10THKX250X250 SA515 GR70 | NO | 4 | 8 | 19.6 | 39.2
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SPARE PIPE OD273X12.7x6000 - SA106 Gr.B | M | 1 | 2 | 81.52 | 163.04
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | PIPE DIA 273.0 X 6.35 X 6500 SA106GRB | M | 68 | 136 | 2839.68 | 5679.36
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | PIPE OD-219.1X12.7X6000-SA106GRC | M | 39 | 78 | 2520.96 | 5041.92
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | PIPE DIA 88.9 X 5.49 SA106GRB | M | 38 | 76 | 429.02 | 858.04
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW LR 90DEG ELL OD273X6.35 SA234WPB | NO | 20 | 40 | 537.6 | 1075.2
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW LR 45DEG ELL OD273X6.35 SA234WPB | NO | 4 | 8 | 53.76 | 107.52
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW LR 90DEG ELL OD219.1X8.18 SA234WPC | NO | 15 | 30 | 329.7 | 659.4
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW LR 45DEG ELL OD219.1X8.18 SA234WPC | NO | 2 | 4 | 21.98 | 43.96
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 5 | 10 | 10.05 | 20.1
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW RED 323.9X6.35/273X6.35 SA234WPB | NO | 4 | 8 | 37.4 | 74.8
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW RED 323.9X12.7/219.1X12.7 SA234WPC | NO | 1 | 2 | 17 | 34
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW RED 219.1X8.18/168.3X7.11 SA234WPC | NO | 1 | 2 | 5.76 | 11.52
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW RED 168.3X7.11/88.9X5.49 SA234WPB | NO | 1 | 2 | 3.1 | 6.2
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW EQT OD273X6.35 SA234WPB | NO | 1 | 2 | 29.11 | 58.22
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW EQT OD219.1X8.18 SA234WPC | NO | 1 | 2 | 24.61 | 49.22
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW EQT OD88.9X5.49 SA234WPB | NO | 1 | 2 | 3.29 | 6.58
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | ASME B16.11 SW STUB NB25 CL 3000 SA105 | NO | 5 | 10 | 2.15 | 4.3
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | TEMP STUB-CS- RC1" L=64 - CS SA105 | NO | 9 | 18 | 6.3 | 12.6
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | CARBON STEEL PLUG 1" CS SA105 | NO | 9 | 18 | 1.8 | 3.6
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | TEMP STUB MX33X2 L=64CS SA105 | NO | 1 | 2 | 0.7 | 1.4
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SOW FLANGE NB 25 CL150 SA515GR 70 | NO | 2 | 4 | 1.8 | 3.6
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SOW FLANGE NB50 CL 150 SA515GR 70 | NO | 2 | 4 | 4 | 8
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | LUG PLATE 12THK 260X125 SA515GR 70 | NO | 3 | 6 | 9.18 | 18.36
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SUPPORT PIPE OD60.3X5.54 SA234WPB | M | 3 | 6 | 22.44 | 44.88
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SUPPORT PIPE OD219.1X6.35 SA234WPB | M | 4 | 8 | 133.24 | 266.48
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SUPPORT PIPE OD168.3X7.11 SA234WPB | NO | 4 | 8 | 113.04 | 226.08
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | CARRIER PLATE 16X50X120 CS SA515GR70 | NO | 12 | 24 | 9.12 | 18.24
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | STUD M12 X 1.75 X140 SA193B7 | NO | 8 | 16 | 0.896 | 1.792
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | NUT M12 SA194GR7 | NO | 16 | 32 | 0.32 | 0.64
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | STUD M16 X 2 X 110 SA193B7 | NO | 8 | 16 | 1.16 | 2.32
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | NUT M16 SA194GR7 | NO | 16 | 32 | 0.48 | 0.96
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | NON-ASBESTOS JOINTING SHT 1.5MMX500X500 | NO | 1 | 2 | 0.618 | 1.236
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | PIPE OD-323.9X12.7X6000-SA106GRC | M | 2 | 4 | 194.92 | 389.84
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | PIPE 88.9X5.49 - SA106GRB | M | 35 | 70 | 395.15 | 790.3
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | PIPE OD60.3X5.54 L=6000 SA106GRB | M | 12 | 24 | 89.76 | 179.52
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 10 | 20 | 20.2 | 40.4
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | BW LR 90DEG ELL 60.3 X 5.54 SA234WPB | NO | 6 | 12 | 6.36 | 12.72
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | BW UEQT 88.9X5.49/60.3X5.54 SA234WPB | NO | 2 | 4 | 5.94 | 11.88
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | SW STUB NB25 CL3000 SA105 | NO | 2 | 4 | 0.86 | 1.72
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | SW STUB NB15 CL3000 SA105 | NO | 2 | 4 | 0.36 | 0.72
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | SPARE PIPE 88.9X5.49 - SA106GRB | M | 1 | 2 | 11.29 | 22.58
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | SPARE PIPE OD60.3X5.54 L=6000 SA106GRB | M | 1 | 2 | 7.48 | 14.96
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | PIPE DIA 114.3 X 6.02 SA106GRB | M | 52 | 104 | 835.64 | 1671.28
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 SA234GRB | NO | 6 | 12 | 25.98 | 51.96
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | ASMEB16.9 BW EQUAL TEE OD114.3X6.02 SA234GRB | NO | 6 | 12 | 33.9 | 67.8
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | SOW FLANGE NB100 CL150-OD230X30 SA515GR70 | NO | 2 | 4 | 10.6 | 21.2
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | BOLT-M16x90 -8.8-IS1364P1 | NO | 8 | 16 | 1.36 | 2.72
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | NUT -M16 -CL4-IS1363P3 | NO | 8 | 16 | 0.24 | 0.48
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | NON-ASBESTOS JOINTING SHEET 1.5MM | NO | 1 | 2 | 2.47 | 4.94
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | BLIND FLANGE NB100 CL150 SA515GR70 | NO | 2 | 4 | 15.44 | 30.88
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | SPARE PIPE OD 114.3X6.02 L=2000 SA234GRB | M | 2 | 4 | 32.14 | 64.28
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | SUPPORT PIPE DIA 88.9 X 5.49, L=4000 SA234GRB | M | 4 | 8 | 45.16 | 90.32
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | PLATE 10.0 MM, 1000X500 SA515GR70 | NO | 1 | 2 | 39.25 | 78.5
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | PIPE DIA 323.9 X 6.35 SA106GRB L=195MM | NO | 1 | 2 | 9.697 | 19.394
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | BW RED 323.9X6.35/114.3X6.02 SA234WPB | NO | 1 | 2 | 8.16 | 16.32
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | PIPE OD 114.3X6.02 L=350MM SA106GRB | NO | 2 | 4 | 3.15 | 6.3
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | PIPE OD168.3x7.11x6000 - SA106 Gr.B | M | 60 | 120 | 1695.6 | 3391.2
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | PIPE OD219.1x12.7x6000 - SA106 Gr.B | M | 7 | 14 | 452.48 | 904.96
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | SUPPORT PIPE OD114.3x6.02 L=2M SA106GR.B | M | 2 | 4 | 32.16 | 64.32
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | SUPPORT PIPE OD168.3x7.11 L=1M-SA106GRB | M | 1 | 2 | 28.26 | 56.52
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW LR 90DEG ELL OD219.1X12.7 SA234WPB | NO | 5 | 10 | 166.95 | 333.9
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 12 | 24 | 134.4 | 268.8
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW LR 45DEG ELL OD168.3X7.11 SA234WPB | NO | 2 | 4 | 11.2 | 22.4
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW LR 30DEG ELL OD168.3X7.11 SA234WPB | NO | 1 | 2 | 3.73 | 7.46
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW RED 219.1x12.7/168.3x7.11 SA234WPB | NO | 3 | 6 | 26.19 | 52.38
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW RED 219.1x12.7/88.9X7.62 SA234WPB | NO | 1 | 2 | 7.31 | 14.62
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW RED 168.3x7.11/88.9x 7.62SA234WPB | NO | 1 | 2 | 3.09 | 6.18
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 5 | 10 | 2.15 | 4.3
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | TEMP STUB RC 1" L=64-SA105 | NO | 8 | 16 | 5.6 | 11.2
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | SCREW PLUG RC 1" SA105 | NO | 8 | 16 | 1.6 | 3.2
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | TEMPERATURE STUB M33x2 L=64 -SA105 | NO | 5 | 10 | 3.5 | 7
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | SCREW PLUG M33 X 2-SA105 | NO | 5 | 10 | 0.05 | 0.1
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | PACKING RING M33x2 - IS1972 | NO | 5 | 10 | 0.8 | 1.6
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | CARRIER PLATE 12X50X80-SA515GR70 | NO | 4 | 8 | 1.507 | 3.014
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BOTTOM PLATE 10THKX1000X500 SA515 GR70 | NO | 1 | 2 | 39.25 | 78.5
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | PIPE OD168.3X10.97x6000 - SA106 Gr.C | M | 29 | 58 | 1234.24 | 2468.48
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | PIPE OD219.1X12.7x6000 - SA106 Gr.C | M | 117 | 234 | 7562.9965 | 15125.993
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | SUPPORT PIPE OD114.3x6.02 L=1000 SA106GR.C | M | 2 | 4 | 32.14 | 64.28
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | SUPPORT PIPE OD168.3x7.11 L=3000 SA106GR.C | M | 3 | 6 | 84.78 | 169.56
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW LR 90DEG ELL OD168.3x10.97 SA234WPC | NO | 13 | 26 | 199.03 | 398.06
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW LR 45DEG ELL OD168.3x10.97 SA234WPC | NO | 2 | 4 | 15.31 | 30.62
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW LR 90DEG ELL OD219.1x12.7 SA234WPC | NO | 26 | 52 | 805.22 | 1610.44
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW LR 45DEG ELL OD219.1x12.7 SA234WPC | NO | 6 | 12 | 92.88 | 185.76
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW LR 30DEG ELL OD219.1x12.7 SA234WPC | NO | 1 | 2 | 15.48 | 30.96
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW RED 219.1x12.7 / 168.3x10.97 SA234WPC | NO | 4 | 8 | 37.2 | 74.4
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | ASME B16.11 SW STUB NB25,CL:6000 SA105 | NO | 14 | 28 | 7.98 | 15.96
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | TEMP STUB RC 1 1/2 " L=64-SA105 | NO | 16 | 32 | 37.504 | 75.008
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | SCREW PLUG RC 1 1/2 " SA105 | NO | 16 | 32 | 8 | 16
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | THERMOWEL STUB OD-70 H=157-SA105 | NO | 4 | 8 | 14.4 | 28.8
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | LUG PLATE 16x428x240 SA515 GR70 | NO | 1 | 2 | 12.901 | 25.802
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | LUG PLATE 12x340x170 SA515 GR70 | NO | 3 | 6 | 16.334 | 32.668
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BOTTOM PLATE 10THKX150X150 SA515 GR70 | NO | 2 | 4 | 3.532 | 7.064
6 | Lara 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BOTTOM PLATE 10THKX200X200 SA515 GR70 | NO | 6 | 12 | 18.84 | 37.68
6 Total | [10 empty] | 146522.871
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | PIPE OD 219.1 x 36 - SA106GRC | M | 48 | 96 | 7802.82 | 15605.64
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | SPARE PIPE OD 219.1 x 36 - SA106GRC | M | 2 | 4 | 325.118 | 650.236
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | PIPE DIA 168.3 X 27.5 SA106GRC | M | 7 | 14 | 668.425 | 1336.85
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | PIPE DIA 168.3 X 31 SA335 P22 | M | 2 | 4 | 209.934 | 419.868
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | PIPE DIA 114.3 X 6.02 SA106GRC | M | 1 | 2 | 16.075 | 32.15
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW LR 90DEG ELL OD219.1X36 SA234WPC | NO | 9 | 18 | 700.92 | 1401.84
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW LR 90DEG ELL OD168.3x27.5 SA234WPC | NO | 3 | 6 | 103.05 | 206.1
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW SR 90DEG ELL OD168.3x31 SA234WP22 | NO | 1 | 2 | 25.05 | 50.1
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW LR 90DEG ELL OD168.3x31 SA234WP22 | NO | 4 | 8 | 150.96 | 301.92
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW UEQT 219.1X36/168.3X27.5 SA234WPC | NO | 1 | 2 | 86.48 | 172.96
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW C.RED 219.1 X 36/168.3X27.5 SA234WPC | NO | 1 | 2 | 19.79 | 39.58
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | CARRIER PLATE 16X50X120-SA515 GR70 | NO | 4 | 8 | 3.04 | 6.08
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | ASME B16.11 SW STUB NB25,CL:9000-SA105 | NO | 4 | 8 | 3.24 | 6.48
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | TEMP STUB RC 1.5" OD98 L=64 - CS SA105 | NO | 1 | 2 | 2.344 | 4.688
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | SCREW PLUG RC 1.5" CS SA105 | NO | 1 | 2 | 0.5 | 1
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | ASME B16.11 SW STUB NB25,CL:9000-SA182F22 | NO | 2 | 4 | 1.62 | 3.24
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | LUGPLATE 16X340X170 SA387 GR22 | NO | 2 | 4 | 7.4 | 14.8
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | PIPE DIA 219.1x12.7 SA106GRC | M | 70 | 140 | 4524.87 | 9049.74
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | PIPE DIA 168.3x7.11 SA106GRB | M | 70 | 140 | 1978.2 | 3956.4
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | SPARE PIPE DIA 168.3x7.11 SA106GRB | M | 2 | 4 | 56.52 | 113.04
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | SPARE PIPE DIA 219.1x12.7 SA106GRC | M | 2 | 4 | 129.282 | 258.564
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | SUPP.PIPE DIA 114.3 X 8.56 SA106GRC | M | 3 | 6 | 66.963 | 133.926
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW LR 90DEG ELBOW OD219.1x12.7 SA234WPC | NO | 12 | 24 | 371.16 | 742.32
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW LR 30DEG ELBOW OD219.1x12.7 SA234WPC | NO | 1 | 2 | 10.31 | 20.62
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW LR 90DEG ELBOW OD168.3x7.11SA234WPB | NO | 8 | 16 | 81.12 | 162.24
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW LR 45DEG ELBOW OD168.3x7.11 SA234WPB | NO | 3 | 6 | 15.21 | 30.42
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW RED 219.1x12.7/168.3X7.11 SA234WPB | NO | 1 | 2 | 7.01 | 14.02
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW RED 323.9x12.7/219.1X12.7 SA234WPC | NO | 2 | 4 | 35 | 70
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | CARRIER PLATE 20X50X120-SA515 GR70 | NO | 28 | 56 | 91.448 | 182.896
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | PLATE 20X300X300 SA515 GR70 | NO | 4 | 8 | 56.52 | 113.04
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | PLATE 20X150X150 SA515 GR70 | NO | 9 | 18 | 31.788 | 63.576
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | PLATE 20X200X200 SA515 GR70 | NO | 1 | 2 | 6.28 | 12.56
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | ASME B16.11 SW STUB NB25,CL:9000-SA105 | NO | 1 | 2 | 0.81 | 1.62
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | ASME B16.11 SW STUB NB50,CL:9000 SA105 | NO | 6 | 12 | 14.64 | 29.28
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | PIPE DIA 168.3 X 21.95 - SA106GRC | M | 170 | 340 | 13467.4 | 26934.8
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | PIPE DIA 114.3x13.49 SA106GRC | M | 33 | 66 | 1107.15 | 2214.3
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | PIPE DIA 88.9x11.13 SA106GRC | M | 66 | 132 | 1409.1 | 2818.2
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SPARE PIPE DIA 168.3 X 21.95 - SA106GRC | M | 3 | 6 | 237.66 | 475.32
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SPARE PIPE DIA 114.3x13.49 SA106GRC | M | 1 | 2 | 33.55 | 67.1
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SPARE PIPE DIA 88.9x11.13 SA106GRC | M | 2 | 4 | 42.7 | 85.4
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW LR 90DEG ELBOW OD168.3x21.95 SA234WPC | NO | 25 | 50 | 712.5 | 1425
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW LR 90DEG ELBOW OD114.3x13.49 SA234WPC | NO | 11 | 22 | 88.11 | 176.22
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW LR 90DEG ELBOW OD88.9x11.13 SA234WPC | NO | 16 | 32 | 61.12 | 122.24
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW EQT OD168.3x21.95 SA234WPC | NO | 1 | 2 | 37.04 | 74.08
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW UEQT OD168.3x21.95/OD114.3X13.49 SA234WPC | NO | 1 | 2 | 32.04 | 64.08
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW RED OD168.3x21.95/OD114.3X13.49 SA234WPC | NO | 2 | 4 | 15.78 | 31.56
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW RED OD168.3x21.95/OD88.9X11.13 SA234WPC | NO | 1 | 2 | 6.89 | 13.78
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | ASME B16.11 SW STUB NB25,CL:6000-SA105 | NO | 1 | 2 | 0.57 | 1.14
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | ASME B16.11 SW STUB NB50,CL:6000 SA105 | NO | 5 | 10 | 9.8 | 19.6
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | THERMOWEL STUB OD70 H-146 CS SA105 | NO | 1 | 2 | 3.6 | 7.2
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | LUG PLATE 12x260x125 SA515 GR70 | NO | 1 | 2 | 2.2 | 4.4
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SUPPORT PIPE OD 114.3x13.49 SA106 GRC | M | 4.5 | 9 | 150.975 | 301.95
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SUPPORT PIPE OD 88.9x11.13 SA106 GRC | M | 3 | 6 | 64.05 | 128.1
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SUPPORT PIPE OD 60.3x11.07 SA106 GRC | M | 2 | 4 | 26.88 | 53.76
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BOTTOM PLATE 16THK 1500x2000 SA515 GR70 | NO | 1 | 2 | 376.8 | 753.6
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | TEMP STUB RC 1.5" OD98 L=64 - CS SA105 | NO | 4 | 8 | 9.376 | 18.752
7 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SCREW PLUG RC 1.5" CS SA105 | NO | 4 | 8 | 2 | 4
7 Total | [10 empty] | 71002.376
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | PIPE OD 323.9X 9.53 X 6000 - SA106GRB | M | 12 | 24 | 886.56 | 1773.12
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | PIPE OD 273x9.27 SA106GRB | M | 43 | 86 | 2592.384 | 5184.768
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | PIPE DIA 33.4X4.55 SA106GRB | M | 5 | 10 | 16.15 | 32.3
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | BW LR 90DEG ELL OD323.9x9.53 SA234WPB | NO | 1 | 2 | 54 | 108
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | BW LR 90DEG ELL OD273x9.27 SA234WPB | NO | 6 | 12 | 222 | 444
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | BW EQT OD323.9x9.53 SA234WPB | NO | 1 | 2 | 60.42 | 120.84
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | BW RED OD323.9x9.53/273x9.27 SA234WPB | NO | 1 | 2 | 13.8801 | 27.7603
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | ASME B16.11 SW STUB NB25 CL:6000-SA105 | NO | 2 | 4 | 2.9146 | 5.8291
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | BOTTEM PLATE 10 THK500x500 SA515 GR70 | NO | 1 | 2 | 2.4271 | 4.8542
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | SUPPORT PIPE OD219.1x12.7 SA106 GRB | M | 1 | 2 | 64.644 | 129.288
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | SPARE PIPE OD 323.9X 9.53 X 6000 - SA106GRB | M | 2 | 4 | 147.76 | 295.52
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | SPARE PIPE OD 273x9.27 X 6000 - SA106GRB | M | 2 | 4 | 120.58 | 241.16
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | PIPE OD 114.3X6.02 SA106GRB | M | 36 | 72 | 578.68 | 1157.36
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | PIPE OD 88.9X5.49 SA106GRB | M | 88 | 176 | 993.72 | 1987.44
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 20 | 32.37 | 64.74
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | 90DEG BW LR ELBOW 114.3X6.02 SA234WPB | NO | 4 | 8 | 20 | 40
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | 90DEG BW LR ELBOW 88.9X5.49 SA234WPB | NO | 21 | 42 | 48.3 | 96.6
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | BW RED 114.3X6.02/88.9X5.49 SA234WPB | NO | 1 | 2 | 1.46 | 2.92
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | BW EQUAL TEE OD 88.9 X 5.49 SA234WPB | NO | 2 | 4 | 7.6 | 15.2
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SW STUB-CS-NB 25 CLASS 6000 CS SA105 | NO | 5 | 10 | 2.15 | 4.3
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SW STUB-CS-NB 50 CLASS 6000 CS SA105 | NO | 2 | 4 | 1.8 | 3.6
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | TEMPERATURE STUB M33X2 L=45 SA105 | NO | 2 | 4 | 1 | 2
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SCREW PLUG M33 X 2 SA105 | NO | 2 | 4 | 1.6 | 3.2
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | PACKING RING IS1972 | NO | 2 | 4 | 0.2 | 0.4
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SUPPORT PIPE OD 60.3X 5.54 SA106GRB | M | 5.5 | 11 | 41.1461 | 82.2922
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SUPPORT PLATE TH 12X1500X1000MM SA515GR70 | NO | 1 | 2 | 141.3 | 282.6
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | CARRIER PLATE 10X50X80 SA515GR70 | NO | 4 | 8 | 1.256 | 2.512
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SPARE PIPE OD 114.3X6.02 SA106GRB | M | 2 | 4 | 32.149 | 64.298
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SPARE PIPE OD 88.9X5.49 SA106GRB | M | 2 | 4 | 22.5847 | 45.1693
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SUPPORT PIPE OD 88.9X5.49 SA106GRB | M | 1 | 2 | 11.2923 | 22.5847
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | BWUN EQUAL TEEOD 114.3X6.02/60.3X5.54 SA234WPB | NO | 2 | 4 | 9.86 | 19.72
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | TEMP STUB RC1 INCH SA105 | NO | 4 | 8 | 3.376 | 6.752
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | CARBON STEEL PLUG 1" SA105 | NO | 4 | 8 | 0.8 | 1.6
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PIPE OD 457 X 9.53X 6000 - SA106GRC | M | 72 | 144 | 7571.52 | 15143.04
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PIPE OD 457 X 12.7X 6000 - SA106GRC | M | 42 | 84 | 5844.3 | 11688.6
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SPARE PIPE OD457X9.53 SA106 GR.C | M | 2 | 4 | 210.32 | 420.64
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SPARE PIPE OD457X12.7 SA106 GR.C | M | 1 | 2 | 139.15 | 278.3
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SUPPORT PIPE OD406.4x9.53 L=5000 SA106GRC | M | 5 | 10 | 466.3 | 932.6
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SUPPORT PIPE OD219.1x12.7 L=2000 SA106GRC | M | 2 | 4 | 129.28 | 258.56
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SUPPORT PIPE OD168.3X7.11 L=4500 SA106GRC | M | 4.5 | 9 | 127.17 | 254.34
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 90DEG ELL OD457x12.7 SA234WPC | NO | 8 | 16 | 1200.16 | 2400.32
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW SR 90DEG ELL OD457x9.53 SA234WPC | NO | 2 | 4 | 150.9 | 301.8
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 45DEG ELL OD457x9.53 SA234WPC | NO | 1 | 2 | 56.63 | 113.26
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 30DEG ELL OD457x9.53 SA234WPC | NO | 1 | 2 | 37.75 | 75.5
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 90DEG ELL OD457x9.53 SA234WPC | NO | 12 | 24 | 1359.6 | 2719.2
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 90DEG ELL OD355.6x9.53 SA234WPC | NO | 2 | 4 | 136.2 | 272.4
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW SR 90DEG ELL OD457x12.7 SA234WPC | NO | 2 | 4 | 199.88 | 399.76
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 30DEG ELL OD457x12.7 SA234WPC | NO | 2 | 4 | 99.9 | 199.8
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW RED 457x9.53 /355.6x9.53 SA234WPC | NO | 2 | 4 | 72.24 | 144.48
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW RED 457x9.53 /406.4x9.53 SA234WPC | NO | 2 | 4 | 75.88 | 151.76
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW RED 559x12.7 / 457x12.7 SA234WPC | NO | 2 | 4 | 159.08 | 318.16
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW RED 610x10 / 457x9.53 SA234WPC | NO | 4 | 8 | 261.84 | 523.68
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BOTTOM PLATE 10 THK 450 X 450-SA515GR70 | NO | 7 | 14 | 111.272 | 222.544
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BOTTOM PLATE 10 THK 2000 X 2000-SA515GR70 | NO | 1 | 2 | 314 | 628
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | CARRIER PLATE 20X120X50-SA515GR70 | NO | 8 | 16 | 7.04 | 14.08
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | ASME B16.11 SW STUB NB15 CL:3000-SA105 | NO | 22 | 44 | 3.96 | 7.92
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SW STUB NB25 CL:3000-SA105 | NO | 8 | 16 | 3.44 | 6.88
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | ASME B16.11 SW STUB NB40 CL:3000-SA105 | NO | 2 | 4 | 1.5 | 3
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SW STUB NB50 CL:3000-SA105 | NO | 6 | 12 | 7.98 | 15.96
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | TEMP STUB RC 1" L=45-SA105 | NO | 3 | 6 | 2.532 | 5.064
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SCREW PLUG RC 1" (CS) SA105 | NO | 3 | 6 | 0.6 | 1.2
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | TEMP STUB RC 1.5" L=45 - CS SA105 | NO | 7 | 14 | 7 | 14
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SCREW PLUG RC 1.5"-CS SA105 | NO | 7 | 14 | 3.5 | 7
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | TEMPERATURE STUB M33x2 L=64 (CS)-SA105 | NO | 1 | 2 | 0.7 | 1.4
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SCREW PLUG M33 X 2-SA105 | NO | 1 | 2 | 0.8 | 1.6
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PACKING RING-COPPER | NO | 1 | 2 | 0.01 | 0.02
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | LUG PLATE 16 THK 400X650-SA515 GR70 | NO | 2 | 4 | 65.312 | 130.624
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PIPE OD 355.6 X 9.53 L=2000 -SA106GRC | M | 2 | 4 | 162.64 | 325.28
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PIPE OD 60.3 X 5.54 L=10M -SA106GRB | M | 10 | 20 | 74.8 | 149.6
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PIPE OD 33.9 X 4.55 L=10M -SA106GRB | M | 10 | 20 | 32.3 | 64.6
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 90DEG 60.3 X 5.54 SA234WPB | NO | 2 | 4 | 1.78 | 3.56
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 90DEG 33.4 X 4.55 -SA234WPB | NO | 2 | 4 | 0.38 | 0.76
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | PIPE OD 355.6 X 9.53 X 6000 - SA106GRC | M | 96 | 192 | 7808.064 | 15616.128
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SUPPORT PIPE OD 323.9 x 9.53 - SA106GRC | M | 1.5 | 3 | 110.82 | 221.64
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SUPPORT PIPE DIA 168.3 X 7.11 SA106GRC | M | 1 | 2 | 28.264 | 56.528
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SPARE PIPE OD355.6x9.53 SA106 GRC | M | 2 | 4 | 162.66 | 325.32
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | BW LR 90DEG ELL OD355.6X9.53 SA234WPC | NO | 15 | 30 | 1050 | 2100
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | BW RED 355.6X9.53/323.9X9.53 SA234WPC | NO | 4 | 8 | 102.4 | 204.8
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | BW RED 406.4X12.7/355.6X9.53 SA234WPC | NO | 1 | 2 | 45 | 90
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | BW RED 457X9.53/ 355.6X9.53 SA234WPC | NO | 2 | 4 | 72.24 | 144.48
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | ASME B16.11 SW STUB NB15 CL:3000-SA105 | NO | 9 | 18 | 1.62 | 3.24
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 5 | 10 | 2.15 | 4.3
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | ASME B16.11 SW STUB NB50 CL:3000-SA105 | NO | 4 | 8 | 5.32 | 10.64
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | TEMP STUB RC 1.5" L=45 - CS SA105 | NO | 7 | 14 | 7 | 14
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SCREW PLUG RC 1.5" CS SA105 | NO | 7 | 14 | 3.5 | 7
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | TEMP STUB RC 1" L=45-SA105 | NO | 3 | 6 | 2.532 | 5.064
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SCREW PLUG RC 1" (CS) SA105 | NO | 3 | 6 | 0.6 | 1.2
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | CARRIER PLATE T=20X50X120-SA515GR70 | NO | 12 | 24 | 10.56 | 21.12
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SUPPORT PLATE 10X350X350-SA515GR70 | NO | 4 | 8 | 38.464 | 76.928
8 | Lara 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | LUG PLATE 16 THK 546X315-SA515 GR70 | NO | 1 | 2 | 14 | 28
8 Total | [10 empty] | 69402.4078
Grand Total | [10 empty] | 1034295.6711
Notes- 1. For Schedule No 1, the quantity & weight for both boilers of a project are not the same (Boiler 1- 59.33 MT kg; Boiler 2- 41.83 MT). In view of the same, for Schedule No 1 alone, the quantity & weight has been seperately indicated for 2 boilers of the project. For rest of the Schedules, quantity & weight indicated is for 1 boiler of the project. 2. Suitable cushion +/-15% in quantity / weight shall be considered by the supplier in tender. 3. Pipe Size / Thickness / Specification mentioned in table may vary for very few cases during detail drawing stage. 4. IBR approval for applicable drawings / PGMA' are in vendor scope. 5. Fabrication drawings shall be prepared by vendor and shall be submitted to BHEL for review and approval prior to commencement of manufacturing. Please refer Technical Specification for better clarity. 6. All attachments like Stubs, Carrier Plates etc shall be welded on to the main pipe. These attachments have been indicated separately in the detailed BOM for better understanding the quantum involved. For better clarity regarding welding details / scope for these items, please refer Sl No 4.6 of the Technical Specification. 7. Items for which weight has been revised have been highlighed in Red.

## BOM- Singrauli 2x800 MW
Enquiry No 4202600002 dt 14.01.2026 Procurement of TG Cycle Piping of IBR & Non IBR Systems for NTPC projects Annexure C- Detailed Piping System BOM (R01)
Schedule No | Project | Piping System | IBR / Non IBR | PGMA | Drawing No | Item Description | UOM | Quantity per Boiler of the project (refer Note 1) | Total Quantity for 2 Boilers | *Weight per Boiler of the project (kg) (refer Note 1) | Total Weight for 2 Boilers (kg)
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD355.6X9.53 SA106GRB | M | 4 | 4 | 325.32 | 325.32
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD219.1X6.35 SA106GRB | M | 5 | 5 | 166.55 | 166.55
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD168.3X7.11 SA106GRB | M | 5.5 | 5.5 | 155.43 | 155.43
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD88.9X5.49 SA106GRB | M | 5.5 | 5.5 | 62.095 | 62.095
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD355.6X9.53 SA234WPB | NO | 1 | 1 | 70 | 70
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 45DEG ELL OD355.6x9.53 SA234WPB | NO | 1 | 1 | 34.03 | 34.03
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 1 | 1 | 16.7 | 16.7
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 45DEG ELL OD219.1x6.35 SA234WPB | NO | 1 | 1 | 7.97 | 7.97
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 1 | 1 | 10.14 | 10.14
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 1 | 1 | 2.02 | 2.02
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 45DEG ELL OD88.9X5.49 SA234WPB | NO | 1 | 1 | 1.01 | 1.01
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PIPE OD 219.1 x 6.35 - SA106GRB | M | 60 | 60 | 1998.6 | 1998.6
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PIPE OD 219.1 x 12.7 - SA106GRC | M | 15 | 15 | 969.6 | 969.6
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PIPE DIA 114.3 X 6.02 SA106GRB | M | 1 | 1 | 16.07 | 16.07
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SUPPORT PIPE OD168.3x7.11 SA106GRB | M | 2.5 | 2.5 | 70.655 | 70.655
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 90DEG ELL OD219.1X6.35 SA234WPB | NO | 11 | 11 | 183.7 | 183.7
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 45DEG ELL OD219.1X6.35 SA234WPB | NO | 2 | 2 | 15.96 | 15.96
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 90DEG ELL OD219.1X12.7 SA234WPC | NO | 1 | 1 | 30.97 | 30.97
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 45DEG ELL OD219.1X12.7 SA234WPC | NO | 2 | 2 | 30.96 | 30.96
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW REDUCER - OD273x12.7/OD219.1x12.7 SA234WPC | NO | 1 | 1 | 13.29 | 13.29
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | FLAT END CLOSURE OD114.3X6.02 SA515GR70 | NO | 1 | 1 | 2.2 | 2.2
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW UEQT 219.1X6.35/114.3X6.02 SA234WPB | NO | 1 | 1 | 17.18 | 17.18
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW EQT 219.1X6.35 SA234WPB | NO | 1 | 1 | 19.27 | 19.27
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | ASME B16.11 SW STUB NB40 CL:6000-SA105 | NO | 2 | 2 | 2.14 | 2.14
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | ASME B16.11 SW STUB NB25 CL:6000-SA105 | NO | 2 | 2 | 1.14 | 1.14
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | TEMPERATURE STUB M33x2 L=45 OD-78 -SA105 | NO | 1 | 1 | 1.12 | 1.12
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SCREW PLUG M33 X 2-SA105 | NO | 1 | 1 | 0.8 | 0.8
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PACKING RING M33x2 | NO | 1 | 1 | 0.01 | 0.01
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | CARRIER PLATE T=8X50X80-SA515GR70 | NO | 8 | 8 | 2.009 | 2.009
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SUPPORT PIPE 168.3X7.11 SA106GRB | M | 3 | 3 | 84.78 | 84.78
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SUPPORT PLATE 10X200X200-SA515GR70 | NO | 8 | 8 | 25.12 | 25.12
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 508x9.53 - SA106 GRB | M | 15 | 15 | 1757.25 | 1757.25
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 355.6x9.53 - SA106 GRB | M | 4 | 4 | 325.2 | 325.2
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 273x9.27 - SA106 GRB | M | 40 | 40 | 2411.52 | 2411.52
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 168.3x7.11 - SA106 GRB | M | 8 | 8 | 226.096 | 226.096
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 219.1x6.35 - SA106 GRB | M | 1 | 1 | 33.31 | 33.31
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 114.3x6.02 - SA106 GRB | M | 1 | 1 | 16.0733 | 16.0733
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 3 | 3 | 420.69 | 420.69
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 45DEG ELL OD508X9.53 SA234WPB | NO | 1 | 1 | 70.07 | 70.07
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD355.6X9.53 SA234WPB | NO | 2 | 2 | 136.2 | 136.2
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD273X9.27 SA234WPB | NO | 10 | 10 | 370 | 370
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 3 | 3 | 30.42 | 30.42
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW UEQT 273X9.27/114.3x6.02 SA234WPB | NO | 1 | 1 | 34.4 | 34.4
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW UEQT 273X9.27/168.3x7.11 SA234WPB | NO | 1 | 1 | 35.46 | 35.46
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW UEQT 508X9.53/219.1x6.35 SA234WPB | NO | 1 | 1 | 120.7 | 120.7
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW EQT 273X9.27 SA234WPB | NO | 1 | 1 | 38.83 | 38.83
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW EQT 508X9.53 SA234WPB | NO | 1 | 1 | 141.95 | 141.95
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 508X9.53/273x9.27 SA234WPB | NO | 2 | 2 | 93.28 | 93.28
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 355.6X9.53/168.3x7.11 SA234WPB | NO | 1 | 1 | 18.49 | 18.49
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 406.4x9.53/355.6X9.53 SA234WPB | NO | 1 | 1 | 31.21 | 31.21
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 965X9.53/508X9.53 SA234WPB | NO | 1 | 1 | 117.84 | 117.84
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 8 | 8 | 3.44 | 3.44
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | FLAT END CLOSURE OD219.1X6.35 SA515GR70 | NO | 1 | 1 | 8.5 | 8.5
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | FLAT END CLOSURE OD114.3X6.02 SA515GR70 | NO | 1 | 1 | 2.2 | 2.2
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | CARRIER PLATE 16X120X50-SA515GR70 | NO | 8 | 8 | 7.04 | 7.04
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | CARRIER PLATE 16X80X50-SA515GR70 | NO | 8 | 8 | 3.84 | 3.84
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | LUG PLATE 16 THK 443x260 -SA515 GR70 | NO | 1 | 1 | 9.4 | 9.4
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | SUPPORT PLATE 12x500x500-SA515GR70 | NO | 4 | 4 | 94.2 | 94.2
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | SUPPORT PIPE OD 457 X 9.53 L=1000-SA106GRB | M | 1 | 1 | 105.3 | 105.3
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | ORIFICE PLATE ASSY-NB350 -SA515GR70 | NO | 1 | 1 | 30.788 | 30.788
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | SOW FLANGE NB350CL150 SA515GR70 | NO | 2 | 2 | 179.75 | 179.75
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | STUD M27 X 3 X 160 SA193B7 | NO | 12 | 12 | 8.1 | 8.1
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | NUT -M27 -2H | NO | 24 | 24 | 4.08 | 4.08
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | NON-ASBESTOS JOINTING SHEET 3.0MM | NO | 1 | 1 | 5.69 | 5.69
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | PIPE DIA 88.9 X 5.49 SA106GRB | M | 68 | 68 | 767.72 | 767.72
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 14 | 14 | 28.28 | 28.28
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | ASMEB16.9 BWLR 45DEG ELBOW OD88.9X5.49 SA234WPB | NO | 2 | 2 | 2.02 | 2.02
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | TEMP STUB M33X2; L=64 SA105 | NO | 1 | 1 | 0.72 | 0.72
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | COPPER PACKING RING M33X2 IS1972 | NO | 1 | 1 | 0.01 | 0.01
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SCREW PLUG CS (M33X2) SA105 | NO | 1 | 1 | 0.4 | 0.4
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 4 | 4 | 4.3 | 4.3
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SW STUB NB15 CL 3000 SA105 | NO | 2 | 2 | 0.546 | 0.546
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SW STUB NB40 CL3000 CS SA105 | NO | 1 | 1 | 0.75 | 0.75
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | CARRIER PLATE 16X50X80 SA515GR70 | NO | 4 | 4 | 2.01 | 2.01
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SUPPORT PIPE OD60.3X5.54 L=4000 SA106GRB | M | 4 | 4 | 29.92 | 29.92
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | PLATE 10.0 MM 1000X1000 SA515GR70 | NO | 1 | 1 | 78.5 | 78.5
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | TEMP STUB RC 1" L=64-SA105 | NO | 3 | 3 | 1.8375 | 1.8375
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SCREW PLUG RC 1" SA105 | NO | 3 | 3 | 0.525 | 0.525
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | PIPE DIA 273.0 X 9.27 SA106GRB | M | 240 | 240 | 14469.12 | 14469.12
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BRANCH PIPE OD 168.30 x 7.11 X 6500 - SA106GRB | M | 3 | 3 | 84.78 | 84.78
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BRANCH PIPE DIA 114.3 X 6.02 SA106GRB | M | 3 | 3 | 48.21 | 48.21
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW LR 90DEG ELL OD273X9.27 SA234WPB | NO | 44 | 44 | 1587.52 | 1587.52
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW RED 355.6X9.53/273X9.27 SA234WPB | NO | 1 | 1 | 23.67 | 23.67
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW UEQT 355.6X9.53/273X9.27 SA234WPB | NO | 1 | 1 | 68.37 | 68.37
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW EQT OD273X9.27 SA234WPB | NO | 4 | 4 | 168.12 | 168.12
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW UEQT 273X9.27/114.3X6.02 SA234WPB | NO | 6 | 6 | 219.24 | 219.24
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | FLAT END CLOSURE FOR OD114.3X6.02 SA515GR70 | NO | 6 | 6 | 16.2 | 16.2
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | TEMP STUB M33X2; L=64 SA105 | NO | 4 | 4 | 2.88 | 2.88
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | COPPER PACKING RING M33X2 IS1972 | NO | 4 | 4 | 0.04 | 0.04
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | SCREW PLUG CS (M33X2) SA105 | NO | 4 | 4 | 1.6 | 1.6
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | SW STUB NB25 CL3000 SA105 | NO | 2 | 2 | 1.66 | 1.66
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | FLAT END CLOSURE OD273x9.27 SA515 GR70 | NO | 2 | 2 | 34.92 | 34.92
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | CARRIER PLATE 16X50X80 SA515GR70 | NO | 8 | 8 | 4.02 | 4.02
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | SUPPORT PIPE OD219.1X8.18 L=5M SA106GRB | M | 5 | 5 | 212.7 | 212.7
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | PLATE TH 10.0X2000X2500 SA515 GR70 | NO | 1 | 1 | 392.5 | 392.5
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | TEMPERATURE STUB RC 1" L=45 CS-SA105 | NO | 3 | 3 | 1.5 | 1.5
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | PLUG R 1" CS SA105 | NO | 3 | 3 | 0.6 | 0.6
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW UEQT 273X9.27/168.3X7.11 SA234WPB | NO | 2 | 2 | 75.42 | 75.42
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | SUPPORT PIPE OD114.3X6.02 L=5M SA106GRB | NO | 5 | 5 | 80.35 | 80.35
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | FLAT END CLOSURE OD168.3x7.11 SA515 GR70 | NO | 2 | 2 | 9.3 | 9.3
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | PIPE DIA 457 X 9.53 - SA335P22 | M | 7 | 7 | 736.12 | 736.12
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | PIPE DIA 457 X 9.53 - SA335P11 | M | 1.5 | 1.5 | 157.74 | 157.74
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | PIPE DIA 457 X 9.53 - SA106 GR.B | M | 30 | 30 | 3154.8 | 3154.8
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SPARE PIPE DIA 457 X 9.53 - SA106 GR.B | M | 1 | 1 | 105.16 | 105.16
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SUPPORT PIPE OD323.9x9.53 SA335 P11 | M | 1.5 | 1.5 | 110.82 | 110.82
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SUPPORT PIPE OD406.4x12.7 SA106 GR.B | M | 3.5 | 3.5 | 431.55 | 431.55
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD457x9.53 SA234WPB | NO | 4 | 4 | 453.48 | 453.48
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD457x9.53 SA234WP22 | NO | 1 | 1 | 116.5 | 116.5
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW UEQT OD457x9.53/OD219.1x6.35 SA234WPB | NO | 9 | 9 | 913.68 | 913.68
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW UEQT OD457x9.53/OD273x9.27 SA234WPB | NO | 2 | 2 | 209.8 | 209.8
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW UEQT OD457x9.53/OD355.6x9.53 SA234WPB | NO | 2 | 2 | 220 | 220
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW RED OD457x9.53/OD219.1x8.18 SA234WP22 | NO | 1 | 1 | 30.787 | 30.787
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BRANCH PIPE OD114.3x13.49 SA106 GR.B | M | 2 | 2 | 67.08 | 67.08
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BRANCH PIPE OD168.3x10.97 SA106 GR.B | M | 2 | 2 | 85.12 | 85.12
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BRANCH PIPE OD88.9x11.13 SA106 GR.B | M | 2 | 2 | 30.54 | 30.54
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SPARE CONNN.PIPE DIA 114.3x6.02 SA106GRB | M | 2 | 2 | 32.14 | 32.14
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB15 CL:3000-SA105 | NO | 8 | 8 | 1.44 | 1.44
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 3 | 3 | 1.29 | 1.29
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | TEMP STUB RC 1" L=45 - CS SA105 | NO | 7 | 7 | 3.5 | 3.5
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SCREW PLUG RC 1" CS SA105 | NO | 7 | 7 | 1.4 | 1.4
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW END CAP OD114.3x6.02 SA515GR70 | NO | 4 | 4 | 8.8 | 8.8
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | FLAT ENDCLOSURE OD219.1x6.35 SA515GR70 | NO | 2 | 2 | 17.86 | 17.86
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW END CAP OD457x9.53 SA234WPB | NO | 1 | 1 | 77.77 | 77.77
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | CARRIER PLATE 20x50x120 SA515 GR70 | NO | 16 | 16 | 14.08 | 14.08
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BOTTOM PLATE 16THK 2000x1500 SA515 GR70 | NO | 1 | 1 | 376.8 | 376.8
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 114.3x8.56 SA106GRC | M | 45 | 45 | 1004.445 | 1004.445
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SPARE PIPE DIA 114.3x8.56 SA106GRC | M | 1 | 1 | 22.321 | 22.321
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SPARE PIPE DIA 219.1x6.35 SA106GRB | M | 1 | 1 | 33.31 | 33.31
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 219.1x12.7 SA106GRC | M | 1 | 1 | 64.641 | 64.641
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 219.1x6.35 SA106GRB | M | 30 | 30 | 999.3 | 999.3
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 114.3x6.02 SA106GRB | M | 0.5 | 0.5 | 8.035 | 8.035
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SUPP. PIPE OD88.9x7.62 SA106 GR.B | M | 3 | 3 | 45.81 | 45.81
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD114.3x8.56 SA234WPC | NO | 9 | 9 | 49.5 | 49.5
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD219.1x6.35 SA234WPB | NO | 8 | 8 | 133.6 | 133.6
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW EQT OD114.3x8.56 SA234WPC | NO | 1 | 1 | 7.7 | 7.7
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW EQT OD219.1x6.35 SA234WPC | NO | 1 | 1 | 19.27 | 19.27
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW UEQT OD219.1x6.35/OD114.3x6.02 SA234WPB | NO | 2 | 2 | 34.36 | 34.36
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW REDUCER OD219.1x12.7/114.3x8.56 SA234 WPC | NO | 2 | 2 | 18 | 18
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW REDUCER OD114.3x8.56/OD88.9x7.62 SA234 WPC | NO | 2 | 2 | 3.86 | 3.86
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW END CAP OD114.3x6.02 SA234WPB | NO | 2 | 2 | 4.4 | 4.4
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | CARRIER PLATE 16x50x80 SA515 GR70 | NO | 4 | 4 | 1.92 | 1.92
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BOTTOM PLATE 16THK 1000x1000 SA515 GR 70 | NO | 1 | 1 | 125 | 125
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB25 CL:6000-SA105 | NO | 12 | 12 | 6.84 | 6.84
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB50 CL:6000-SA105 | NO | 5 | 5 | 9.8 | 9.8
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | TEMP STUB RC 1.5" OD78 L=64 - CS SA105 | NO | 5 | 5 | 7.5 | 7.5
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SCREW PLUG RC 1.5" SA105 | NO | 5 | 5 | 2.5 | 2.5
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | GI -SHEET FOR RAIN HOOD 0.63 THKx1000x2000 IS277 | NO | 1 | 1 | 9.892 | 9.892
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | PIPE OD711X10, SA672GRB70 | M | 27 | 27 | 4668.3 | 4668.3
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SPARE PIPE OD508x9.53 SA106 GRB | M | 2 | 2 | 234.3 | 234.3
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | PIPE OD508X9.53, SA106GRB | M | 84 | 84 | 9840.6 | 9840.6
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BRANCH PIPE OD219.1X16 , SA106GRB | M | 2 | 2 | 160.26 | 160.26
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW LR 90DEG ELL OD711X10 SA234WPB(W) | NO | 3 | 3 | 939 | 939
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW LR 45DEG ELL OD711X10 SA234WPB(W) | NO | 3 | 3 | 432.93 | 432.93
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 12 | 12 | 1682.76 | 1682.76
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW RED OD711X9.53/610X9.53 SA234WPB | NO | 1 | 1 | 93.9 | 93.9
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW RED OD711X10/508X9.53 SA234WPB | NO | 2 | 2 | 180.86 | 180.86
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW UNEQT OD711X10/610X9.53 SA234WPB | NO | 1 | 1 | 274.85 | 274.85
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | FLAT END CLOSURE OD219.1X8.18 SA515GR70 | NO | 2 | 2 | 17.26 | 17.26
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SW STUB NB25 CL6000 CS SA105 | NO | 8 | 8 | 4.56 | 4.56
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SW STUB NB25 CL3000 CS SA105 OD50 H=54 | NO | 5 | 5 | 2.15 | 2.15
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SW STUB NB15 CL3000 CS SA105 OD36 H=44 | NO | 14 | 14 | 2.52 | 2.52
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | TEMPERATURE STUB M33X2 (CS) SA105 ( D-78 , H-45) (ROD-80) | NO | 3 | 3 | 3.36 | 3.36
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SCREW PLUG M33X2 CS SA105 | NO | 3 | 3 | 1.2 | 1.2
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | PACKING RING IS1972 | NO | 3 | 3 | 0.03 | 0.03
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | TEMP.STUB L=45 SA105 ( HWR ) ROD-80 DIA | NO | 2 | 2 | 1.3 | 1.3
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | TEMP.STUB RC 1 "(CS) D55 , L=45 SA105 (ROD-D63) | NO | 8 | 8 | 5.6 | 5.6
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SCREW PLUG R 1 " (CS) SA105 (ROD-D40) | NO | 8 | 8 | 1.6 | 1.6
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | CARRIER PLATE 20X50X120 SA515GR70 | NO | 24 | 24 | 21.12 | 21.12
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD914X9.53 L=800 SA106GRB | M | 0.8 | 0.8 | 170 | 170
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD660X9.53 L=1000 SA106GRB | M | 1 | 1 | 152.876 | 152.876
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD457X9.53 L=1500 SA106GRB | M | 1.5 | 1.5 | 157.74 | 157.74
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | LUG PLATE 16X559X325 SA515GR70 | NO | 2 | 2 | 29.6 | 29.6
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PLATE 20X1500X2000 SA515GR70 | NO | 1 | 1 | 471 | 471
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PLATE 10X2000X1000 SA515GR70 | NO | 2 | 2 | 157 | 157
1 | Singrauli 2x800 MW Unit 1 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | THERMOWELL STUB SA105 OD-70, H-80 (ROD-80) | NO | 5 | 5 | 8.5 | 8.5
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD355.6X9.53 SA106GRB | M | 4 | 4 | 325.32 | 325.32
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD219.1X6.35 SA106GRB | M | 5 | 5 | 166.55 | 166.55
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD168.3X7.11 SA106GRB | M | 5.5 | 5.5 | 155.43 | 155.43
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD88.9X5.49 SA106GRB | M | 5.5 | 5.5 | 62.095 | 62.095
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD355.6X9.53 SA234WPB | NO | 1 | 1 | 70 | 70
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 45DEG ELL OD355.6x9.53 SA234WPB | NO | 1 | 1 | 34.03 | 34.03
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 1 | 1 | 16.7 | 16.7
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 45DEG ELL OD219.1x6.35 SA234WPB | NO | 1 | 1 | 7.97 | 7.97
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 1 | 1 | 10.14 | 10.14
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 1 | 1 | 2.02 | 2.02
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 45DEG ELL OD88.9X5.49 SA234WPB | NO | 1 | 1 | 1.01 | 1.01
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PIPE OD 219.1 x 6.35 - SA106GRB | M | 60 | 60 | 1998.6 | 1998.6
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PIPE OD 219.1 x 12.7 - SA106GRC | M | 15 | 15 | 969.6 | 969.6
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PIPE DIA 114.3 X 6.02 SA106GRB | M | 1 | 1 | 16.07 | 16.07
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SUPPORT PIPE OD168.3x7.11 SA106GRB | M | 2.5 | 2.5 | 70.655 | 70.655
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 90DEG ELL OD219.1X6.35 SA234WPB | NO | 11 | 11 | 183.7 | 183.7
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 45DEG ELL OD219.1X6.35 SA234WPB | NO | 2 | 2 | 15.96 | 15.96
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 90DEG ELL OD219.1X12.7 SA234WPC | NO | 1 | 1 | 30.97 | 30.97
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 45DEG ELL OD219.1X12.7 SA234WPC | NO | 2 | 2 | 30.96 | 30.96
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW REDUCER - OD273x12.7/OD219.1x12.7 SA234WPC | NO | 1 | 1 | 13.29 | 13.29
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | FLAT END CLOSURE OD114.3X6.02 SA515GR70 | NO | 1 | 1 | 2.2 | 2.2
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW UEQT 219.1X6.35/114.3X6.02 SA234WPB | NO | 1 | 1 | 17.18 | 17.18
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW EQT 219.1X6.35 SA234WPB | NO | 1 | 1 | 19.27 | 19.27
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | ASME B16.11 SW STUB NB40 CL:6000-SA105 | NO | 2 | 2 | 2.14 | 2.14
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | ASME B16.11 SW STUB NB25 CL:6000-SA105 | NO | 2 | 2 | 1.14 | 1.14
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | TEMPERATURE STUB M33x2 L=45 OD-78 -SA105 | NO | 1 | 1 | 1.12 | 1.12
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SCREW PLUG M33 X 2-SA105 | NO | 1 | 1 | 0.8 | 0.8
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PACKING RING M33x2 | NO | 1 | 1 | 0.01 | 0.01
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | CARRIER PLATE T=8X50X80-SA515GR70 | NO | 8 | 8 | 2.009 | 2.009
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SUPPORT PIPE 168.3X7.11 SA106GRB | M | 3 | 3 | 84.78 | 84.78
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SUPPORT PLATE 10X200X200-SA515GR70 | NO | 8 | 8 | 25.12 | 25.12
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 508x9.53 - SA106 GRB | M | 15 | 15 | 1757.25 | 1757.25
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 355.6x9.53 - SA106 GRB | M | 4 | 4 | 325.2 | 325.2
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 273x9.27 - SA106 GRB | M | 40 | 40 | 2411.52 | 2411.52
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 168.3x7.11 - SA106 GRB | M | 8 | 8 | 226.096 | 226.096
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 219.1x6.35 - SA106 GRB | M | 1 | 1 | 33.31 | 33.31
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 114.3x6.02 - SA106 GRB | M | 1 | 1 | 16.0733 | 16.0733
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 3 | 3 | 420.69 | 420.69
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 45DEG ELL OD508X9.53 SA234WPB | NO | 1 | 1 | 70.07 | 70.07
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD355.6X9.53 SA234WPB | NO | 2 | 2 | 136.2 | 136.2
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD273X9.27 SA234WPB | NO | 10 | 10 | 370 | 370
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 3 | 3 | 30.42 | 30.42
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW UEQT 273X9.27/114.3x6.02 SA234WPB | NO | 1 | 1 | 34.4 | 34.4
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW UEQT 273X9.27/168.3x7.11 SA234WPB | NO | 1 | 1 | 35.46 | 35.46
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW UEQT 508X9.53/219.1x6.35 SA234WPB | NO | 1 | 1 | 120.7 | 120.7
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW EQT 273X9.27 SA234WPB | NO | 1 | 1 | 38.83 | 38.83
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW EQT 508X9.53 SA234WPB | NO | 1 | 1 | 141.95 | 141.95
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 508X9.53/273x9.27 SA234WPB | NO | 2 | 2 | 93.28 | 93.28
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 355.6X9.53/168.3x7.11 SA234WPB | NO | 1 | 1 | 18.49 | 18.49
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 406.4x9.53/355.6X9.53 SA234WPB | NO | 1 | 1 | 31.21 | 31.21
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 965X9.53/508X9.53 SA234WPB | NO | 1 | 1 | 117.84 | 117.84
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 8 | 8 | 3.44 | 3.44
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | FLAT END CLOSURE OD219.1X6.35 SA515GR70 | NO | 1 | 1 | 8.5 | 8.5
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | FLAT END CLOSURE OD114.3X6.02 SA515GR70 | NO | 1 | 1 | 2.2 | 2.2
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | CARRIER PLATE 16X120X50-SA515GR70 | NO | 8 | 8 | 7.04 | 7.04
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | CARRIER PLATE 16X80X50-SA515GR70 | NO | 8 | 8 | 3.84 | 3.84
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | LUG PLATE 16 THK 443x260 -SA515 GR70 | NO | 1 | 1 | 9.4 | 9.4
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | SUPPORT PLATE 12x500x500-SA515GR70 | NO | 4 | 4 | 94.2 | 94.2
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | SUPPORT PIPE OD 457 X 9.53 L=1000-SA106GRB | M | 1 | 1 | 105.3 | 105.3
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | ORIFICE PLATE ASSY-NB350 SA515GR70 | NO | 1 | 1 | 30.788 | 30.788
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | SOW FLANGE NB350CL150 OD535X40 SA515GR70 | NO | 2 | 2 | 179.75 | 179.75
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | STUD M27 X 3 X 160 SA193B7 | NO | 12 | 12 | 8.1 | 8.1
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | NUT -M27 -2H | NO | 24 | 24 | 4.08 | 4.08
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | NON-ASBESTOS JOINTING SHEET 3.0MM | NO | 1 | 1 | 5.69 | 5.69
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | PIPE DIA 88.9 X 5.49 SA106GRB | M | 68 | 68 | 767.72 | 767.72
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 14 | 14 | 28.28 | 28.28
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | ASMEB16.9 BWLR 45DEG ELBOW OD88.9X5.49 SA234WPB | NO | 2 | 2 | 2.02 | 2.02
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | TEMP STUB M33X2; L=64 SA105 | NO | 1 | 1 | 0.72 | 0.72
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | COPPER PACKING RING M33X2 IS1972 | NO | 1 | 1 | 0.01 | 0.01
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SCREW PLUG CS (M33X2) SA105 | NO | 1 | 1 | 0.4 | 0.4
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 4 | 4 | 4.3 | 4.3
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SW STUB NB15 CL 3000 SA105 | NO | 2 | 2 | 0.546 | 0.546
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SW STUB NB40 CL3000 CS SA105 | NO | 1 | 1 | 0.75 | 0.75
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | CARRIER PLATE 16X50X80 SA105 | NO | 4 | 4 | 2.01 | 2.01
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SUPPORT PIPE OD60.3X5.54 L=4000 SA106GRB | M | 4 | 4 | 29.92 | 29.92
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | PLATE 10.0 MM 1000X1000 SA515GR70 | NO | 1 | 1 | 78.5 | 78.5
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | TEMP STUB RC 1" L=64-SA105 | NO | 3 | 3 | 1.8375 | 1.8375
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SCREW PLUG RC 1" SA105 | NO | 3 | 3 | 0.525 | 0.525
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | PIPE DIA 457 X 9.53 - SA335P22 | M | 7 | 7 | 736.12 | 736.12
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | PIPE DIA 457 X 9.53 - SA335P11 | M | 1.5 | 1.5 | 157.74 | 157.74
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | PIPE DIA 457 X 9.53 - SA106 GR.B | M | 30 | 30 | 3154.8 | 3154.8
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SPARE PIPE DIA 457 X 9.53 - SA106 GR.B | M | 1 | 1 | 105.16 | 105.16
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SUPPORT PIPE OD323.9x9.53 SA335 P11 | M | 1.5 | 1.5 | 110.82 | 110.82
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SUPPORT PIPE OD406.4x12.7 SA106 GR.B | M | 3.5 | 3.5 | 431.55 | 431.55
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD457x9.53 SA234WPB | NO | 4 | 4 | 453.48 | 453.48
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD457x9.53 SA234WP22 | NO | 1 | 1 | 116.5 | 116.5
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW UEQT OD457x9.53/OD219.1x6.35 SA234WPB | NO | 9 | 9 | 913.68 | 913.68
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW UEQT OD457x9.53/OD273x9.27 SA234WPB | NO | 2 | 2 | 209.8 | 209.8
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW UEQT OD457x9.53/OD355.6x9.53 SA234WPB | NO | 2 | 2 | 220 | 220
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW RED OD457x9.53/OD219.1x8.18 SA234WP22 | NO | 1 | 1 | 30.787 | 30.787
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BRANCH PIPE OD114.3x13.49 SA106 GR.B | M | 2 | 2 | 67.08 | 67.08
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BRANCH PIPE OD168.3x10.97 SA106 GR.B | M | 2 | 2 | 85.12 | 85.12
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BRANCH PIPE OD88.9x11.13 SA106 GR.B | M | 2 | 2 | 30.54 | 30.54
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SPARE CONNN.PIPE DIA 114.3x6.02 SA106GRB | M | 2 | 2 | 32.14 | 32.14
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB15 CL:3000-SA105 | NO | 8 | 8 | 1.44 | 1.44
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 3 | 3 | 1.29 | 1.29
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | TEMP STUB RC 1" L=45 - CS SA105 | NO | 7 | 7 | 3.5 | 3.5
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SCREW PLUG RC 1" CS SA105 | NO | 7 | 7 | 1.4 | 1.4
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW END CAP OD114.3x6.02 SA234WPB | NO | 4 | 4 | 8.8 | 8.8
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | FLAT ENDCLOSURE OD219.1x6.35 SA515GR70 | NO | 2 | 2 | 17.86 | 17.86
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW END CAP OD457x9.53 SA234WPB | NO | 1 | 1 | 77.77 | 77.77
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | CARRIER PLATE 20x50x120 SA515 GR70 | NO | 16 | 16 | 14.08 | 14.08
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BOTTOM PLATE 16THK 2000x1500 SA515 GR70 | NO | 1 | 1 | 376.8 | 376.8
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 114.3x8.56 SA106GRC | M | 45 | 45 | 1004.445 | 1004.445
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SPARE PIPE DIA 114.3x8.56 SA106GRC | M | 1 | 1 | 22.321 | 22.321
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SPARE PIPE DIA 219.1x6.35 SA106GRB | M | 1 | 1 | 33.31 | 33.31
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 219.1x12.7 SA106GRC | M | 1 | 1 | 64.641 | 64.641
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 219.1x6.35 SA106GRB | M | 30 | 30 | 999.3 | 999.3
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 114.3x6.02 SA106GRB | M | 0.5 | 0.5 | 8.035 | 8.035
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SUPP. PIPE OD88.9x7.62 SA106 GR.B | M | 3 | 3 | 45.81 | 45.81
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD114.3x8.56 SA234WPC | NO | 9 | 9 | 49.5 | 49.5
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD219.1x6.35 SA234WPB | NO | 8 | 8 | 133.6 | 133.6
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW EQT OD114.3x8.56 SA234WPC | NO | 1 | 1 | 7.7 | 7.7
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW EQT OD219.1x6.35 SA234WPC | NO | 1 | 1 | 19.27 | 19.27
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW UEQT OD219.1x6.35/OD114.3x6.02 SA234WPB | NO | 2 | 2 | 34.36 | 34.36
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW REDUCER OD219.1x12.7/114.3x8.56 SA234 WPC | NO | 2 | 2 | 18 | 18
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW REDUCER OD114.3x8.56/OD88.9x7.62 SA234 WPC | NO | 2 | 2 | 3.86 | 3.86
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW END CAP OD114.3x6.02 SA234WPB | NO | 2 | 2 | 4.4 | 4.4
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | CARRIER PLATE 16x50x80 SA515 GR70 | NO | 4 | 4 | 1.92 | 1.92
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BOTTOM PLATE 16THK 1000x1000 SA515 GR 70 | NO | 1 | 1 | 125 | 125
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB25 CL:6000-SA105 | NO | 12 | 12 | 6.84 | 6.84
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB50 CL:6000-SA105 | NO | 5 | 5 | 9.8 | 9.8
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | TEMP STUB RC 1.5" OD78 L=64 - CS SA105 | NO | 5 | 5 | 7.5 | 7.5
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SCREW PLUG RC 1.5" SA105 | NO | 5 | 5 | 2.5 | 2.5
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | GI -SHEET FOR RAIN HOOD 0.63 THKx1000x2000 IS277 | NO | 1 | 1 | 9.892 | 9.892
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | PIPE OD711X10, SA672GRB70 | M | 27 | 27 | 4668.3 | 4668.3
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SPARE PIPE OD508x9.53 SA106 GRB | M | 2 | 2 | 234.3 | 234.3
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | PIPE OD508X9.53, SA106GRB | M | 84 | 84 | 9840.6 | 9840.6
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BRANCH PIPE OD219.1X16 , SA106GRB | M | 2 | 2 | 160.26 | 160.26
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW LR 90DEG ELL OD711X10 SA234WPB(W) | NO | 3 | 3 | 939 | 939
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW LR 45DEG ELL OD711X10 SA234WPB(W) | NO | 3 | 3 | 432.93 | 432.93
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 12 | 12 | 1682.76 | 1682.76
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW RED OD711X9.53/610X9.53 SA234WPB | NO | 1 | 1 | 93.9 | 93.9
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW RED OD711X10/508X9.53 SA234WPB | NO | 2 | 2 | 180.86 | 180.86
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW UNEQT OD711X10/610X9.53 SA234WPB | NO | 1 | 1 | 274.85 | 274.85
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | FLAT END CLOSURE OD219.1X8.18 SA515GR70 | NO | 2 | 2 | 17.26 | 17.26
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SW STUB NB25 CL6000 CS SA105 | NO | 8 | 8 | 4.56 | 4.56
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SW STUB NB25 CL3000 CS SA105 OD50 H=54 | NO | 5 | 5 | 2.15 | 2.15
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SW STUB NB15 CL3000 CS SA105 OD36 H=44 | NO | 14 | 14 | 2.52 | 2.52
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | TEMPERATURE STUB M33X2 (CS) SA105 ( D-78 , H-45) (ROD-80) | NO | 3 | 3 | 3.36 | 3.36
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SCREW PLUG M33X2 CS SA105 | NO | 3 | 3 | 1.2 | 1.2
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | PACKING RING IS1972 | NO | 3 | 3 | 0.03 | 0.03
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | TEMP.STUB L=45 SA105 ( HWR ) ROD-80 DIA | NO | 2 | 2 | 1.3 | 1.3
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | TEMP.STUB RC 1 "(CS) D55 , L=45 SA105 (ROD-D63) | NO | 8 | 8 | 5.6 | 5.6
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SCREW PLUG R 1 " (CS) SA105 (ROD-D40) | NO | 8 | 8 | 1.6 | 1.6
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | CARRIER PLATE 20X50X120 SA515GR70 | NO | 24 | 24 | 21.12 | 21.12
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD914X9.53 L=800 SA106GRB | M | 0.8 | 0.8 | 170 | 170
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD660X9.53 L=1000 SA106GRB | M | 1 | 1 | 152.876 | 152.876
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD457X9.53 L=1500 SA106GRB | M | 1.5 | 1.5 | 157.74 | 157.74
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | LUG PLATE 16X559X325 SA515GR70 | NO | 2 | 2 | 29.6 | 29.6
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PLATE 20X1500X2000 SA515GR70 | NO | 1 | 1 | 471 | 471
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PLATE 10X2000X1000 SA515GR70 | NO | 2 | 2 | 157 | 157
1 | Singrauli 2x800 MW Unit 2 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | THERMOWELL STUB SA105 OD-70, H-80 (ROD-80) | NO | 5 | 5 | 8.5 | 8.5
1 Total | [10 empty] | 101164.9837
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | PIPE OD2032x16 L=14980 SA672 GRB70 | M | 21 | 42 | 16704.03 | 33408.06
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | 90DEG MITRE BEND OD2032x16 R=1500 SA387GR12CL2(CERT) | NO | 6 | 12 | 12905.652 | 25811.304
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | 13.6DEG MITRE BEND OD2032x16 R=1500 SA387GR12CL2(CERT) | NO | 2 | 4 | 1863.592 | 3727.184
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | ASME B16.11 SW STUB NB15,CL:3000-SA105 OD36 H=44 | NO | 10 | 20 | 1.8 | 3.6
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | ASME B16.11 SW STUB NB50,CL:3000-SA105 OD80 H=60 | NO | 4 | 8 | 5.32 | 10.64
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | TEMP STUB RC 1" L=45-SA105 | NO | 8 | 16 | 4.9 | 9.8
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | SCREW PLUG RC 1" SA105 | NO | 8 | 16 | 1.4 | 2.8
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | BLIND FLANGE ASSY NB500 CL150 SA515GR70 | NO | 2 | 4 | 126 | 252
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | BRANCH PIPE OD508x12.7 L=500 SA106GRB | M | 1 | 2 | 155.1 | 310.2
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | SOW FLANGE NB500 CL150 SA515GR70 | NO | 2 | 4 | 108 | 216
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | BRANCH PIPE OD323.9x9.53 L=500 SA106GRB | M | 1 | 2 | 73.88 | 147.76
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | FLAT FACED FLANGE NB2000 SA515GR70 | NO | 4 | 8 | 546.656 | 1093.312
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | NON ASBESTOS GASKET NB2000 PN10 NON-ASBESTOS | NO | 2 | 4 | 13.656 | 27.312
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | BOTTOM PLATE 20 THK 450X350-SA515GR70 | NO | 16 | 32 | 395.632 | 791.264
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | PAD PLATE 840x400x12 SA515GR70 | NO | 16 | 32 | 506.416 | 1012.832
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | STIFFNER PLATE 607x427x16 SA515GR70 | NO | 32 | 64 | 1041.728 | 2083.456
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | STIFFNER PLATE 740x275x16 SA515GR70 | NO | 16 | 32 | 408.96 | 817.92
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | BOTTOM PLATE 25 THK 750X474-SA515GR70 | NO | 4 | 8 | 279.068 | 558.136
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | PAD PLATE 717x375x12 SA515GR70 | NO | 4 | 8 | 101.312 | 202.624
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | STUD M 30 X200 SA193B16 | NO | 44 | 88 | 37.4 | 74.8
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | HEX . NUT M30 SA194GR2H | NO | 88 | 176 | 20.328 | 40.656
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | STUD M 52 X5X340 SA193B7 | NO | 100 | 200 | 560 | 1120
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | HEX . NUT M52x5 SA194GR2H | NO | 200 | 400 | 310 | 620
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | PIPE OD-323.9X9.53 SA106GRC | M | 54 | 108 | 3989.52 | 7979.04
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | BW LR 90DEG ELL OD323.9X9.53 SA234WPC | NO | 4 | 8 | 212.16 | 424.32
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | 45° BW LR ELBOW 323.9X9.53 SA234WPB | NO | 2 | 4 | 54 | 108
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | SUPPORT PIPE OD219.1X6.35 L=1000 SA106GRB | NO | 3 | 6 | 99.93 | 199.86
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | BOTTOM PLATE 10X1000X1000MM SA515GR70 | NO | 1 | 2 | 78.5 | 157
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | GAL WIRE MESH 1.2 X1200X2000 IS280 | NO | 1 | 2 | 6.24 | 12.48
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | SOW FLANGE NB 300 CL150 SA515GR70 | NO | 4 | 8 | 94.88 | 189.76
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | BOLT-M24X120 -4.6-IS1363P1 | NO | 26 | 52 | 13.676 | 27.352
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | NUT -M24 -CL4-IS1363 | NO | 26 | 52 | 2.86 | 5.72
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | NON-ASBESTOS JOINTING SHEET 3.0MMX500X500 | NO | 1 | 2 | 2.47 | 4.94
2 | Singrauli 2x800 MW Unit 1 & 2 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | SPARE PIPE OD-323.9X9.53X6000-SA106GRC | M | 2 | 4 | 147.76 | 295.52
2 Total | [10 empty] | 81745.652
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PIPE DIA 114.3 X 6.02 SA106GRB | M | 4 | 8 | 64.3 | 128.6
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PIPE DIA 323.9x9.53 SA106GRB | M | 17 | 34 | 1255.96 | 2511.92
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PIPE DIA 508 X 9.53 SA106GRB | M | 14 | 28 | 1640.0944 | 3280.1888
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PIPE DIA 660 X 10 SA672 B70 | M | 18 | 36 | 2865.15 | 5730.3
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PIPE DIA60.3x5.54 L=20000MM SA106 GRB | M | 20 | 40 | 149.62 | 299.24
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BW LR 49.2 DEG ELL OD660x9.53 SA234WPB | NO | 2 | 4 | 272.66 | 545.32
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BW LR 90DEG ELL OD323.9X9.53 SA234WPB | NO | 5 | 10 | 265.05 | 530.1
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BW UEQT OD660.4x9.53/323.9x9.53 SA234WPB | NO | 4 | 8 | 1052 | 2104
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BW UEQT OD660x9.53/508x9.53 SA234WPB | NO | 3 | 6 | 679.95 | 1359.9
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BW C.RED 610x9.53/508x9.53 SA234WPB | NO | 3 | 6 | 198.6 | 397.2
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 9 | 18 | 3.87 | 7.74
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | ASME B16.11 SW STUB NB50,CL:3000 SA105 | NO | 5 | 10 | 6.65 | 13.3
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | ASME B16.11 SW STUB NB15,CL:3000 SA105 | NO | 9 | 18 | 1.62 | 3.24
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | TEMPERATURE STUB M33X2, L=64 SA105 | NO | 10 | 20 | 7 | 14
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PACKING RING M33x2 IS1972 | NO | 10 | 20 | 10.1 | 20.2
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | SCREW PLUG M33 x 2 SA105 | NO | 10 | 20 | 8 | 16
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | FLAT END CLOSURE OD114.3x6.02 SA515 GR70( PLATE 120x120X8THK) | NO | 1 | 2 | 2.19 | 4.38
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | FLAT END CLOSURE OD660x10 SA515 GR70 (PLATE 660X660X10THK) | NO | 2 | 4 | 320 | 640
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | SOW FLANGE NB25 CL150 IS2062 | NO | 3 | 6 | 2.7 | 5.4
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | STUD M12X70 SA193GRB7 | NO | 20 | 40 | 1.2 | 2.4
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | HEX,NUT M12 SA194GR2H | NO | 40 | 80 | 0.8 | 1.6
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | SOW FLANGE NB50 CL150 IS2062 | NO | 3 | 6 | 6 | 12
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | STUD M16X100 SA193GRB7 | NO | 20 | 40 | 2.8 | 5.6
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | HEX,NUT M16 SA194GR2H | NO | 40 | 80 | 1.32 | 2.64
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | GASKET T=1.5MM 1000X1000 NON ASBESTOS | NO | 1 | 2 | 2.47 | 4.94
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BOTTOM SUPPORT PIPE OD406.4x9.53 L=5000 SA106 GRB | M | 5 | 10 | 466.35 | 932.7
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BOTTOM SUPPORT PIPE OD508x9.53 L=5000 SA106 GRB | M | 5 | 10 | 585.75 | 1171.5
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | SUPPORT PIPE OD88.9x5.49 SA106 GRB | M | 1 | 2 | 11.29 | 22.58
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BOTTEM PLATE 10 THK 120x120 SA515 GR70 | NO | 2 | 4 | 2.26 | 4.52
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BOTTOM SUPPORT PIPE OD273X9.27 L=4000MM SA106 GRB | M | 4 | 8 | 241.5 | 483
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BOTTOM SUPPORT PLATE 10x1500x3500 SA515 GR70 | NO | 1 | 2 | 412.125 | 824.25
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | TEMP STUB RC1 INCH SA105 | NO | 6 | 12 | 5.064 | 10.128
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | CARBON STEEL PLUG 1" SA105 | NO | 6 | 12 | 1.2 | 2.4
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | PIPE DIA 323.9 X 9.53 SA106GRC | M | 3 | 6 | 221.64 | 443.28
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | PIPE OD-323.9X9.53-SA106GRB | M | 40 | 80 | 2955.2 | 5910.4
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | PIPE DIA 273.0 X 9.27 SA106GRB | M | 7 | 14 | 422.17 | 844.34
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | BW LR 90DEG ELL OD323.9X9.53 SA234WPB | NO | 9 | 18 | 506.34 | 1012.68
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | BW LR 90DEG ELL OD273X9.27 SA234WPB | NO | 3 | 6 | 116.43 | 232.86
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | BW UEQT 323.9X9.53/273X9.27 SA234WPB | NO | 2 | 4 | 108.92 | 217.84
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | BW RED 323.9X9.53/168.3X10.97 SA234WPC | NO | 2 | 4 | 24.14 | 48.28
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | SW STUB NB25 CL3000 CS OD34XH44 SA105 | NO | 6 | 12 | 2.58 | 5.16
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | SUPPORT PIPE OD273.0X9.27 L=2500 SA106GRB | M | 2.5 | 5 | 180.85 | 361.7
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | BOTTOM SUPPORT PLATE 10x500x1000 SA515 GR70 | NO | 1 | 2 | 39.25 | 78.5
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 48.3X5.08 SA106GRB | M | 26 | 52 | 140.66 | 281.32
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 73.0X5.16 SA106GRB | M | 6 | 12 | 51.78 | 103.56
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | BW LR 90DEG ELL OD48.3X5.08 SA234WPB | NO | 9 | 18 | 5.58 | 11.16
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | BW LR 90DEG ELL OD73.0X5.16 SA234WPB | NO | 6 | 12 | 8.88 | 17.76
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | UNIONS 1/2"S.W.-1/2"NPT SA106GRB (OD21.3X3.73 L=200MM) | NO | 60 | 120 | 19.2 | 38.4
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | HEXAGONAL NIPPLES 1/2"NPT (M) -1/2"NPT (M) (OD21.3X3.73 L=200MM)SA106GRB | NO | 60 | 120 | 70.2 | 140.4
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 60.3X3.91 SA312TP304 | M | 120 | 240 | 651.6 | 1303.2
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 60.3X5.54 SA106GRB | M | 230 | 460 | 1720.63 | 3441.26
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 33.4X4.55 SA106GRB | M | 175 | 350 | 567 | 1134
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 21.3X3.73 SA106GRB | M | 500 | 1000 | 810 | 1620
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ELBOW 90DEG OD60.3X3.91 SA312WP304 | NO | 20 | 40 | 15.4 | 30.8
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ELBOW 90DEG OD60.3X5.54 SA234WPB | NO | 42 | 84 | 44.52 | 89.04
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ELBOW 90DEG OD33.4X4.55 SA234WPB | NO | 23 | 46 | 5.75 | 11.5
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ELBOW 90DEG OD21.3X3.73 SA234WPB | NO | 60 | 120 | 4.8 | 9.6
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | REDUCER 60.3X5.54/33.4X4.55 SA234WPB | NO | 2 | 4 | 1.14 | 2.28
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | REDUCER 33.4X4.55/21.3X3.73 SA234WPB | NO | 30 | 60 | 5.1 | 10.2
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | UEQT 60.3X5.54/33.4X4.55 SA234WPB | NO | 10 | 20 | 14.2 | 28.4
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | EQT 60.3X5.54 SA234WPB | NO | 4 | 8 | 6.32 | 12.64
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | EQT 33.4X4.55 SA234WPB | NO | 26 | 52 | 11.18 | 22.36
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | UEQT 33.4X4.55/21.3x3.73 SA234WPB | NO | 40 | 80 | 15.2 | 30.4
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | EQT 33.4X3.73 SA234WPB | NO | 20 | 40 | 7.2 | 14.4
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | EQT 60.3X3.91 SA312WP304 | NO | 6 | 12 | 7.2 | 14.4
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ROUND DIA 63 L=70 SA105 (ORIFICE PLATE NB50) | NO | 1 | 2 | 0.665 | 1.33
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ROUND DIA 40 L=60 SA105 (ORIFICE PLATE NB25) | NO | 1 | 2 | 0.25 | 0.5
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | EQT 21.3X3.73 SA234WPB | NO | 15 | 30 | 3.45 | 6.9
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | PIPE OD 219.1 x 12.7 - SA106GRB | M | 52 | 104 | 3361.2797 | 6722.5595
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | PIPE DIA 33.4X4.55 SA106GRB | M | 7 | 14 | 22.519 | 45.038
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | BW LR 90DEG ELL OD219.1X12.7 SA234WPB | NO | 15 | 30 | 464.55 | 929.1
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | BW EQT OD219.1x12.7 SA234WPB | NO | 2 | 4 | 74.8 | 149.6
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | BW RED OD219.1x12.7/168.3x7.11 SA234WPB | NO | 2 | 4 | 17.456 | 34.912
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 3 | 6 | 1.29 | 2.58
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | LUG PLATE 16 THK 428X240 -SA515GR.70 | NO | 2 | 4 | 16.8 | 33.6
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | SUPPORT PIPE OD168.3x7.11 SA106 GRB | M | 4 | 8 | 113.048 | 226.096
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | BOTTOM PLATE 10 THK 1000x1000 SA515 GR70 | NO | 1 | 2 | 78.5 | 157
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | SPARE PIPE OD 219.1 x 12.7 - SA106GRB | M | 2 | 4 | 129.28 | 258.56
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | PIPE DIA 168.3 X 7.11 SA106GRB | M | 62 | 124 | 1752.1205 | 3504.2409
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 30 | 60 | 304.2 | 608.4
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | BW LR 45DEG ELL OD168.3X7.11 SA234WPB | NO | 4 | 8 | 20.32 | 40.64
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | SUPPORT PIPE OD114.3X6.02 SA106 GRB | M | 3.5 | 7 | 56.261 | 112.522
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | BOTTOM PLATE 10 THK 1000x1000 SA515 GR70 | NO | 1 | 2 | 78.5 | 157
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | SPARE PIPE DIA 168.3 X 7.11 SA106GRB | M | 2 | 4 | 56.52 | 113.04
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 323.9 X 9.53 SA106GRB | M | 49 | 98 | 3620.12 | 7240.24
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 88.9 X 5.49 SA106GRB | M | 6 | 12 | 67.74 | 135.48
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 406.4 X 12.7 SA106GRB | M | 230 | 460 | 28359 | 56718
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 406.4 X 12.7 SA106GRC | M | 40 | 80 | 4932 | 9864
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 457.0 X 12.7 SA106GRC | M | 110 | 220 | 15306.17 | 30612.34
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 114.3 X 6.02 SA106GRB | M | 5 | 10 | 80.35 | 160.7
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 323.9 X 12.7 SA106GRB | M | 18 | 36 | 1754.28 | 3508.56
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 273 X 9.27 SA106GRB | M | 30 | 60 | 1808.64 | 3617.28
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD273x9.27 SA234WPB | NO | 7 | 14 | 259 | 518
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD88.9x5.49 SA234WPB | NO | 6 | 12 | 12.18 | 24.36
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD114.3x6.02 SA234WPB | NO | 1 | 2 | 3.84 | 7.68
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD323.9x9.53 SA234WPB | NO | 12 | 24 | 648 | 1296
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD323.9x9.53 SA234WPC | NO | 5 | 10 | 270 | 540
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 45DEG ELL OD323.9x9.53 SA234WPB | NO | 2 | 4 | 54 | 108
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD406.4x12.7 SA234WPB | NO | 53 | 106 | 5857.56 | 11715.12
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 60DEG ELL OD406.4x12.7 SA234WPB | NO | 1 | 2 | 73.68 | 147.36
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 45DEG ELL OD406.4x12.7 SA234WPB | NO | 9 | 18 | 497.34 | 994.68
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW SR 90DEG ELL OD406.4x12.7 SA234WPB | NO | 1 | 2 | 110.52 | 221.04
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD406.4x12.7 SA234WPC | NO | 6 | 12 | 663.12 | 1326.24
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD457.2x12.7 SA234WPC | NO | 24 | 48 | 3395.76 | 6791.52
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 45DEG ELL OD457.2x12.7 SA234WPC | NO | 3 | 6 | 212.22 | 424.44
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 60DEG ELL OD457.2x12.7 SA234WPC | NO | 1 | 2 | 94.33 | 188.66
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW SR 90DEG ELL OD457.2x12.7 SA234WPC | NO | 2 | 4 | 282.38 | 564.76
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW SR 90DEG ELL OD508x9.53 SA234WPB | NO | 1 | 2 | 93.48 | 186.96
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD406.4x12.7/OD273x9.27 SA234WPB | NO | 1 | 2 | 37.06 | 74.12
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD850 NB/OD406.4x12.7 SA234WPB | NO | 2 | 4 | 250.04 | 500.08
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD406.4X12.7/OD323.9x9.53 SA234WPB | NO | 1 | 2 | 39.53 | 79.06
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD508x12.7/OD406.4X12.7 SA234WPB | NO | 4 | 8 | 284.04 | 568.08
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD508x14.27/OD457x12.7 SA234WPC | NO | 4 | 8 | 334.96 | 669.92
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD457x12.7/OD406.4X12.7 SA234WPC | NO | 2 | 4 | 100.14 | 200.28
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD457x12.7/OD323.9x9.53 SA234WPC | NO | 6 | 12 | 274.32 | 548.64
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD323.9x9.53/OD273x9.27 SA234WPB | NO | 2 | 4 | 27.76 | 55.52
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW EQT OD406.4x12.7 SA234WPB | NO | 7 | 14 | 837.34 | 1674.68
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW EQT OD457x12.7 SA234WPC | NO | 4 | 8 | 607.48 | 1214.96
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT 323.9X9.53/168.3x7.11 SA234WPB | NO | 3 | 6 | 154.17 | 308.34
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT 406.4x12.7/323.9X9.53SA234WPB | NO | 5 | 10 | 538.15 | 1076.3
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT 406.4x12.7/219.1X12.7 SA234WPB | NO | 3 | 6 | 300.87 | 601.74
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT- OD457x12.7/OD406.4X12.7 SA234WPC | NO | 3 | 6 | 428.88 | 857.76
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT- OD457x12.7/OD323.9x9.53 SA234WPC | NO | 1 | 2 | 132.67 | 265.34
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT- OD457x12.7/OD219.1x12.7 SA234WPC | NO | 1 | 2 | 125.66 | 251.32
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | ASME16.5 FLNAGE NB450 CL150 SA105 | NO | 8 | 16 | 1312 | 2624
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | ASME B16.11 SW STUBNB15 CL6000 SA105 | NO | 10 | 20 | 1.8 | 3.6
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | ASME B16.11 SW STUBNB25 CL6000 SA105 | NO | 76 | 152 | 43.32 | 86.64
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | ASME B16.11 SW STUBNB40 CL6000 SA105 | NO | 5 | 10 | 3.75 | 7.5
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | ASME B16.11 SW STUBNB50 CL6000 SA105 | NO | 5 | 10 | 6.65 | 13.3
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | TEMPERATURE STUB M33X2, L=64 (CS) SA105 | NO | 26 | 52 | 18.2 | 36.4
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PACKING RING M33x2 SA105 | NO | 26 | 52 | 0.26 | 0.52
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | COPPER PACKING RING M33X2 IS1972 | NO | 26 | 52 | 20.8 | 41.6
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | FLAT END CLOSURE OD114.3x6.02 SA515GR.70 | NO | 1 | 2 | 2.19 | 4.38
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BRANCH PIPE OD88.9x15.24 SA106GRB | M | 1.6 | 3.2 | 44.288 | 88.576
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BRANCH PIPE OD114.3x15.24 SA106GRB | M | 2 | 4 | 74.44 | 148.88
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | CARRIER PLATE16X50X100 SA515 GR.70 | NO | 24 | 48 | 15.072 | 30.144
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | CARRIER PLATE12X50X80 SA515 GR.70 | NO | 12 | 24 | 4.521 | 9.042
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SUPPORT PIPE OD323.9x9.53 SA106GRB | M | 12 | 24 | 1097.6457 | 2195.2914
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PLATE 10 THK 2000X2000 SA515GR70 | NO | 1 | 2 | 314 | 628
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PLATE 12 THK 2000x2000 SA515 GR70 | NO | 2 | 4 | 30.144 | 60.288
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SUPPORT PIPE OD219.1X12.7 SA106GRB | M | 2.5 | 5 | 161.6 | 323.2
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SUPPORT PIPE OD168.3X7.11 SA106GRB | M | 4 | 8 | 113.048 | 226.096
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | LUG PLATE 16 THK 559X325 -SA515GR.70 | NO | 2 | 4 | 29.6 | 59.2
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | LUG PLATE 16 THK 600X360 -SA515GR.70 | NO | 1 | 2 | 17.6 | 35.2
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 323.9 X 9.53 SA106GRB | M | 2 | 4 | 147.76 | 295.52
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 406.4 X 12.7 SA106GRB | M | 6 | 12 | 739.8 | 1479.6
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 406.4 X 12.7 SA106GRC | M | 2 | 4 | 246.6 | 493.2
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 457.0 X 12.7 SA106GRC | M | 3 | 6 | 417.441 | 834.882
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 323.9 X 12.7 SA106GRB | M | 1 | 2 | 97.46 | 194.92
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 273 X 9.27 SA106GRB | M | 5.1 | 10.2 | 307.4688 | 614.9376
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | TEMPERATURE STUB Rc1.5" SA105 OD98 L=H=45 | NO | 50 | 100 | 88.5 | 177
3 | Singrauli 2x800 MW Unit 1 & 2 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SCREW PLUG Rc1.5" SA105 | NO | 50 | 100 | 25 | 50
3 Total | [10 empty] | 208336.5022
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | PIPE OD 813 x 10 - SA672 B70 | M | 18 | 36 | 3564 | 7128
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | PIPE OD 610 x 10 - SA672 B70 | M | 11 | 22 | 1628 | 3256
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | PIPE OD 323.9 x 9.53 - SA106GRC | M | 13 | 26 | 960.44 | 1920.88
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SUPPORT PIPE OD559x9.53 L=700SA106GRB | M | 0.7 | 1.4 | 90.391 | 180.782
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SUPPORT PIPE OD273x12.7 L=700SA106GRC | M | 0.7 | 1.4 | 57.064 | 114.128
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | BW LR 90DEG ELL OD323.9X9.53 SA234WPC | NO | 5 | 10 | 281.3 | 562.6
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | BW LR 90DEG ELL OD610X10 SA234WPB | NO | 4 | 8 | 850.2 | 1700.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | BW LR 30DEG ELL OD610X10 SA234WPB | NO | 1 | 2 | 70.85 | 141.7
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | BW MITRE BEND R0.75D 90DEG OD813x10 SA672 B70 | NO | 4 | 8 | 758.24 | 1516.48
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 4 | 8 | 1.72 | 3.44
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | LUG PLATE 16 THK 520x632 -SA515 GR70 | NO | 3 | 6 | 123.84 | 247.68
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SUPPORT PLATE 12x600x600-SA515GR70 | NO | 1 | 2 | 33.91 | 67.82
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SUPPORT PLATE 10X300X300-SA515GR70 | NO | 1 | 2 | 7.07 | 14.14
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SPARE PIPE OD 813 x 10 - SA672 B70 | M | 1 | 2 | 198 | 396
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SPARE PIPE OD 610 x 10 - SA672 B70 | M | 1 | 2 | 148 | 296
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SPARE PIPE OD 323.9 x 9.53 - SA106GRC | M | 1 | 2 | 73.88 | 147.76
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | PIPE DIA 323.9 X 9.53 SA335P22 | M | 6 | 12 | 443.28 | 886.56
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | PIPE DIA 219.1 X 12.7 SA335P22 | M | 4 | 8 | 258.56 | 517.12
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | PIPE OD-219.1X12.7X6000-SA106GRC | M | 8 | 16 | 517.12 | 1034.24
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | PIPE DIA 168.3 X 7.11 SA106GRB | M | 2.5 | 5 | 70.65 | 141.3
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | BW LR 30DEG ELL 219.1X12.7 SA234WP22CL1 | NO | 1 | 2 | 11.13 | 22.26
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | BW LR 60DEG ELL OD219.1X12.7 SA234WPC | NO | 2 | 4 | 44.52 | 89.04
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | BW EQT OD323.9X9.53 SA335WP22CL1 | NO | 2 | 4 | 120.84 | 241.68
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB25 SA105 CL:3000 | NO | 10 | 20 | 4.3 | 8.6
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB50 SA105 CL:3000 | NO | 14 | 28 | 18.62 | 37.24
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB50 SA182F22 CL:3000 | NO | 14 | 28 | 18.62 | 37.24
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB50 SA182F22 CL:9000 | NO | 8 | 16 | 10.64 | 21.28
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB25 SA182F22 CL:3000 | NO | 1 | 2 | 0.43 | 0.86
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB40 SA182F22 CL:3000 | NO | 1 | 2 | 1.07 | 2.14
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD219.1X12.7-(PLATE OD219.1X48THK) SA515GR70 | NO | 3 | 6 | 43.2 | 86.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD168.3X7.11 (PLATE OD168.3X33THK) SA515GR70 | NO | 1 | 2 | 6.64 | 13.28
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD219.1X12.7 (PLATE OD219.1X48THK) SA387GR22CL2 | NO | 1 | 2 | 14.4 | 28.8
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD323.9X9.53-(PLATE OD324X48THK) SA387GR22CL2 | NO | 3 | 6 | 117 | 234
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD33.4X4.55 (PLATE OD33.4X20THK) SA387GR22CL2 | NO | 1 | 2 | 0.138 | 0.276
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD60.3X5.54 (PLATE OD60.3X20THK) SA515GR70 | NO | 2 | 4 | 22 | 44
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD60.3X5.54 - (PLATE OD60.3X20THK) SA387GR22CL2 | NO | 1 | 2 | 11 | 22
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD33.4X4.55 (PLATE OD33.4X20THK) SA515GR70 | NO | 2 | 4 | 0.276 | 0.552
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | SUPPORT PIPE OD168.3X10.97 L= 350 SA335P11 | NO | 1 | 2 | 14.9 | 29.8
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | SUPPORT PIPE OD168.3X10.97 L= 1050- SA106GRB | NO | 1 | 2 | 44.69 | 89.38
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | SUPPORT PIPE OD114.3X6.02 L= 400 SA106GRB | NO | 1 | 2 | 6.43 | 12.86
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | SUPPORT PIPE OD273X6.35 L= 1050 SA335P11 | NO | 1 | 2 | 43.84 | 87.68
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | BOTTOM PLATE 12 THK,1500X1500 - SA515GR70 | NO | 1 | 2 | 211.95 | 423.9
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | BOTTOM PLATE 12 THK, 1000X1000 - SA387GR11CL2 | NO | 1 | 2 | 94.2 | 188.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | PIPE OD 219.1 x 6.35 - SA106GRB | M | 4 | 8 | 133.24 | 266.48
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | SPARE PIPE OD 219.1 x 6.35 - SA106GRB | M | 1 | 2 | 33.31 | 66.62
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | PIPE OD 406.4x9.53 - SA106GRB | M | 24 | 48 | 2238.48 | 4476.96
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | SUPPORT PIPE OD168.3x7.11 L=2000 SA106GRB | M | 2 | 4 | 56.524 | 113.048
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | BW LR 90DEG ELL OD219.1X6.35 SA234WPB | NO | 4 | 8 | 66.8 | 133.6
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | BW LR 60DEG ELL OD219.1X6.35 SA234WPB | NO | 1 | 2 | 16.7 | 33.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | BW LR 45DEG ELL OD406.4x9.53 SA234WPB | NO | 3 | 6 | 133.98 | 267.96
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 4 | 8 | 1.72 | 3.44
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | CARRIER PLATE 16X120X50-SA515GR70 | NO | 4 | 8 | 3.52 | 7.04
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | SUPPORT PLATE 10X200X200-SA515GR70 | NO | 4 | 8 | 12.56 | 25.12
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | SUPPORT PIPE OD323.9X9.53 L=1500 SA106GRB | M | 1.5 | 3 | 110.82 | 221.64
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | PIPE DIA 273.0 X 6.35 SA106GRB | M | 12 | 24 | 501.24 | 1002.48
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | ASMEB16.9 BWLR 45DEG ELBOW OD355.6X9.53 SA234GRB | NO | 5 | 10 | 170.15 | 340.3
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 SA234GRB | NO | 5 | 10 | 131 | 262
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | MACHINED REDUCER NB25/15 SA234WPB | NO | 5 | 10 | 20 | 40
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | SOW FLANGE NB 250 CL150 BMC16 SA515GR70 | NO | 5 | 10 | 72.5 | 145
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | STUD M 24 X 3 X 230 SA193B7 | NO | 70 | 140 | 49 | 98
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | NUT -M24 -GR7 | NO | 140 | 280 | 15.4 | 30.8
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | NON-ASBESTOS JOINTING SH 3.0MM 1000X1000 | NO | 1 | 2 | 6 | 12
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | GALVANISED WIRE MESH 1.2THKX1200X2000 IS280 | NO | 5 | 10 | 31.2 | 62.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | SUPPORT PIPE OD219.8X8.18 L=9000 SA106GRB | M | 9 | 18 | 382.86 | 765.72
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | SUPPORT PLATE 12THKX1200X800 SA515GR70 | NO | 1 | 2 | 90.432 | 180.864
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | DRIP PAN ASSY NB 250 (CS)-3.15THK,600DIA SA515GR70 | NO | 5 | 10 | 69.9 | 139.8
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | DRIP PAN ASSY NB 250 (CS)-3.15THK,100X1700 SA515GR70 | NO | 5 | 10 | 21 | 42
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | COVER PLATE FOR DRIP PAN - 10THK,600DIA SA515GR70 | NO | 5 | 10 | 110.5 | 221
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | PIPE DIA 168.3 X 7.11 SA106GRB | M | 2 | 4 | 56.524 | 113.048
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 4 | 8 | 41.6 | 83.2
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | 45DEG BW LR ELBOW 168.3X7.11 SA234WPB | NO | 1 | 2 | 5.08 | 10.16
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 1 | 2 | 0.43 | 0.86
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 20 | 32.371 | 64.742
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | 90DEG BW LR ELBOW 33.4X4.55 SA234WPB | NO | 3 | 6 | 0.6 | 1.2
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | ORIFICE PLATE ASSY PIPE OD 168.3X7.11 SA106GRB L=300 | M | 0.3 | 0.6 | 8.4786 | 16.9572
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | ORIFICE PLATE ASSY For Pipe NB150- SA515GR70 | NO | 1 | 2 | 2.22 | 4.44
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | LUG PLATE THICK12x340x170 SA515 GR70 | NO | 1 | 2 | 3.7 | 7.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | SPARE PIPE DIA 168.3 X 7.11 SA106GRB | M | 0.5 | 1 | 14.131 | 28.262
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | PIPE DIA 168.3 X 7.11 SA106GRB | M | 2 | 4 | 56.5238 | 113.0476
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 4 | 8 | 41.6 | 83.2
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | 45 DEG BW LR ELBOW 168.3X7.11 SA234WPB | NO | 1 | 2 | 5.08 | 10.16
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 1 | 2 | 0.43 | 0.86
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 20 | 32.371 | 64.742
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | 90DEG BW LR ELBOW 33.4X4.55 SA234WPB | NO | 3 | 6 | 0.6 | 1.2
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | ORIFICE PLATE ASSY PIPE OD 168.3X7.11 SA106GRB L=300 | M | 0.3 | 0.6 | 8.4786 | 16.9572
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | ORIFICE PLATE ASSY For Pipe NB150- SA515GR70 | NO | 1 | 2 | 2.22 | 4.44
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | LUG PLATE THICK12x340x170 SA515 GR70 | NO | 1 | 2 | 3.7 | 7.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | SPARE PIPE DIA 168.3 X 7.11 SA106GRB | M | 0.5 | 1 | 14.131 | 28.262
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | PIPE DIA 114.3 X 6.02 SA106GRB | M | 42 | 84 | 675.1292 | 1350.2584
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 9 | 18 | 34.56 | 69.12
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | BW LR 45DEG ELL OD114.3X6.02 SA234WPB | NO | 2 | 4 | 3.84 | 7.68
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 3 | 6 | 1.29 | 2.58
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 20 | 32.371 | 64.742
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | 90DEG BW LR ELBOW 33.4X4.55 SA234WPB | NO | 3 | 6 | 0.6 | 1.2
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | ORIFICE PLATE ASSY PIPE OD 114.3X6.02 SA106GRB L=300 | NO | 1 | 2 | 4.83 | 9.66
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | 0ORIFICE PLATE ASSY for Pipe NB100- SA515GR70 | NO | 1 | 2 | 1.026 | 2.052
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | SUPPORT PIPE OD88.9X7.62 L=254MM SA106GRB | NO | 2 | 4 | 7.76 | 15.52
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | SPARE PIPE DIA 114.3 X 6.02 SA106GRB | M | 2 | 4 | 32.149 | 64.298
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | PIPE DIA 114.3 X 6.02 SA106GRB | M | 47 | 94 | 755.5025 | 1511.005
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 9 | 18 | 34.56 | 69.12
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | BW LR 45DEG ELL OD114.3X6.02 SA234WPB | NO | 2 | 4 | 3.84 | 7.68
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 2 | 4 | 0.86 | 1.72
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 20 | 32.371 | 64.742
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | 90DEG BW LR ELBOW 33.4X4.55 SA234WPB | NO | 3 | 6 | 0.6 | 1.2
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | ORIFICE PLATE ASSY PIPE OD 114.3X6.02 SA106GRB L=300 | NO | 1 | 2 | 4.83 | 9.66
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | 0ORIFICE PLATE ASSY for Pipe NB100- SA515GR70 | NO | 1 | 2 | 0.026 | 0.052
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | SUPPORT PIPE OD88.9X7.62 L=254MM SA106GRB | NO | 2 | 4 | 7.76 | 15.52
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | SPARE PIPE DIA 114.3 X 6.02 SA106GRB | M | 2 | 4 | 32.149 | 64.298
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | PIPE DIA 114.3 X 6.02 SA106GRB | M | 35.589 | 71.178 | 572.076 | 1144.152
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 9 | 18 | 34.56 | 69.12
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | BW LR 45DEG ELL OD114.3X6.02 SA234WPB | NO | 1 | 2 | 1.92 | 3.84
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 2 | 4 | 0.86 | 1.72
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 20 | 32.371 | 64.742
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | 90DEG BW LR ELBOW 33.4X4.55 SA234WPB | NO | 3 | 6 | 0.6 | 1.2
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | ORIFICE PLATE ASSY PIPE OD 114.3X6.02 SA106GRB L=300 | NO | 1 | 2 | 4.83 | 9.66
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | 0ORIFICE PLATE ASSY for Pipe NB100- SA515GR70 | NO | 1 | 2 | 1.026 | 2.052
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | SUPPORT PIPE OD88.9X7.62 L=254MM SA106GRB | NO | 1 | 2 | 3.879 | 7.758
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | SUPPORT PLATE THICK10X100X100MM SA515 GR70 | NO | 1 | 2 | 0.785 | 1.57
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | SPARE PIPE DIA 114.3 X 6.02 SA106GRB | M | 2 | 4 | 32.149 | 64.298
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | PIPE DIA 355.6 X 9.53 SA106GRB | M | 40 | 80 | 3253.1937 | 6506.3874
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | PIPE OD 60.3x5.54 SA106GRB | M | 4 | 8 | 29.924 | 59.848
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | BW LR 90DEG ELL OD355.6X9.53 SA234WPB | NO | 4 | 8 | 272.4 | 544.8
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | BW LR 45DEG ELL OD355.6X9.53 SA234WPB | NO | 1 | 2 | 34.03 | 68.06
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | BW ELL 90 DEG OD 60.3x5.54 SA106GRB | NO | 5 | 10 | 4.5 | 9
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | BW UEQT 355.6X9.53/219.1x8.18 SA234WPB | NO | 1 | 2 | 65.93 | 131.86
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | BW REDUCER - OD355.6x9.53/OD323.9x9.53 SA234WPB | NO | 1 | 2 | 25.6184 | 51.2367
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | ASME B16.11 SW STUB NB25,CL:3000-SA105 | NO | 1 | 2 | 35.8206 | 71.6413
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | ASME B16.11 SW STUB NB50,CL:3000-SA105 | NO | 1 | 2 | 0.12807 | 0.25613
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | SUPPORT PIPE OD273X6.35 L=0.8 SA106GRB | M | 0.8 | 1.6 | 28.6565 | 57.313
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | SUPPORT PLATE THICK 10X300X300MM SA515GR70 | NO | 4 | 8 | 0.51227 | 1.0245
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | GAL WIRE MWSH 1.2x1200x2000 IS2062 FE410 | NO | 1 | 2 | 6.7519 | 13.5037
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | SPARE PIPE DIA 355.6 X 9.53 SA106GRB | M | 2 | 4 | 25.794 | 51.5879
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | PIPE DIA 355.6 X 9.53 SA106GRB | M | 32 | 64 | 40.7077 | 81.4155
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | PIPE DIA 273.0 X 6.35 SA106GRB | M | 3.5 | 7 | 11.7316 | 23.4632
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | BW LR 45DEG ELL OD355.6X9.53 SA234WPB | NO | 5 | 10 | 6.3606 | 12.7212
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | BW SR 90DEG ELL OD273X6.35 SA234WPB | NO | 5 | 10 | 124.88 | 249.76
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | BW RED 457.2X9.53/355.6X9.53 SA234WPB | NO | 5 | 10 | 179.1032 | 358.2064
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | DRIP PAN ASSY NB 250 (CS)-3.15THK,600DIA SA515GR70 | NO | 5 | 10 | 0.64033 | 1.2807
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | DRIP PAN ASSY NB 250 (CS)-3.15THK,100X1700 SA515GR70 | NO | 5 | 10 | 179.1032 | 358.2064
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | COVER PLATE FOR DRIP PAN - 10THK,600DIA SA515GR70 | NO | 5 | 10 | 0.64033 | 1.2807
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | SW RED NB25/15 CL3000 SA105 | NO | 5 | 10 | 0.65 | 1.3
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | NON-ASBESTOS JOINTING SHEET 3MM 1500X1500 | NO | 1 | 2 | 12.897 | 25.794
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | SOW FLANGE NB250 CL.150 SA105 | NO | 5 | 10 | 6.3606 | 12.7212
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | HEX.BOLT M24X120 IS1364 | NO | 75 | 150 | 251.391 | 502.782
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | HEX.NUT M24 IS1364 | NO | 75 | 150 | 95.4088 | 190.8175
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | GAL WIRE MESH 1.2X1200X2000 IS280 | NO | 5 | 10 | 31.2 | 62.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | SUPPORT PIPE OD219.1X6.35 SA106GRB | M | 5 | 10 | 166.575 | 333.15
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | BOTTOM PLATE 10X250X250 SA515GR70 | NO | 20 | 40 | 98.2 | 196.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | SPARE PIPE DIA 355.6 X 9.53 SA106GRB | M | 2 | 4 | 162.66 | 325.32
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | PIPE OD 355.6x9.53 - SA106GRB | M | 50 | 100 | 4065 | 8130
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | PIPE OD 273x6.35 - SA106GRB | M | 3 | 6 | 125.28 | 250.56
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | PIPE OD 168.3x7.11 - SA106GRB | M | 2 | 4 | 56.524 | 113.048
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | BW 90 DEG SR ELBOW 273X6.35 SA234WPB | NO | 2 | 4 | 49.952 | 99.904
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | BW 45 DEG LR ELBOW 355.6X9.53 SA234WPB | NO | 6 | 12 | 204.18 | 408.36
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | BW RED 457.2x9.53/355.6X9.53 SA234WPB | NO | 2 | 4 | 71.64 | 143.28
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | SW RED NB25/NB15 CL3000 SA234WPB | NO | 2 | 4 | 0.26 | 0.52
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | SUPPORT PIPE OD219.1x6.35 SA106GRB | M | 6 | 12 | 199.89 | 399.78
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | BOTTOM PLATE 10 THK 250X250-SA515GR70 | NO | 18 | 36 | 88.38 | 176.76
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | FLANGE 250NB CL150 SA515GR70 | NO | 2 | 4 | 30 | 60
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | DRIP PAN ASSY NB 250 (CS)-3.15THK,600DIA SA515GR70 | NO | 2 | 4 | 27.96 | 55.92
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | DRIP PAN ASSY NB 250 (CS)-3.15THK,100X1700 SA515GR70 | NO | 2 | 4 | 8.4 | 16.8
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | COVER PLATE FOR DRIP PAN - 10THK,600DIA SA515GR70 | NO | 2 | 4 | 0.44 | 0.88
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | HEX.BOLT M24x120 IS1364 | NO | 25 | 50 | 13.5 | 27
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | HEX.NUT M24 IS1364 | NO | 25 | 50 | 2.5 | 5
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | GALVANISED WIRE MESH 1.2 THKx1200x1200 IS280 | NO | 2 | 4 | 12 | 24
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | NON ASBESTOS JOINTING SHEET 3mm x1000x1000 | NO | 1 | 2 | 5.1 | 10.2
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | SPARE PIPE DIA 355.6 X 9.53 SA106GRB | M | 2 | 4 | 162.66 | 325.32
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | SOW FLANGE NB150 CL600 SA515GR70 | NO | 2 | 4 | 14.3 | 28.6
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | FT STUD M27X180 | NO | 2 | 4 | 1.54 | 3.08
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | NUT -M27 -2H | NO | 2 | 4 | 0.34 | 0.68
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | PIPE DIA 219.1x6.35 SA106GRB | M | 45 | 90 | 1499.175 | 2998.35
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | PIPE DIA 273x6.35 SA106GRB | M | 43 | 86 | 1796.1047 | 3592.2094
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | PIPE DIA 323.9x9.53 SA106GRB | M | 34 | 68 | 2511.92 | 5023.84
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW LR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 33 | 66 | 526.086 | 1052.172
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW LR 90DEG ELL OD273x6.35 SA234WPB | NO | 9 | 18 | 224.784 | 449.568
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW LR 90DEG ELL OD323.9x9.53 SA234WPB | NO | 5 | 10 | 265.2 | 530.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW EQT OD219.1x6.35 SA234WPB | NO | 4 | 8 | 77.08 | 154.16
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW UEQT OD323.9x9.53/OD219.1x6.35 SA234WPB | NO | 4 | 8 | 216.8 | 433.6
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW C.RED OD273x6.35/OD219.1x6.35 SA234WPB | NO | 8 | 16 | 54 | 108
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW C.RED OD323.9x9.53/OD219.1x6.35 SA234WPB | NO | 4 | 8 | 51.6 | 103.2
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | TEMPERATURE STUB M33X2, L=64 SA105 | NO | 6 | 12 | 2.1 | 4.2
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | PACKING RING M33x2 IS1972 SA105 | NO | 6 | 12 | 0.3 | 0.6
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SCREW PLUG M33 x 2 SA105 SA105 | NO | 6 | 12 | 2.4 | 4.8
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | PRESSURE STUB NB25 CLASS 3000 SA105 | NO | 6 | 12 | 1.2 | 2.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | FLAT END CLOSURE OD273x6.35 SA515 GR70 | NO | 4 | 8 | 69.84 | 139.68
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | CARRIER PLATE 16THK 80x50 SA515GR70 | NO | 20 | 40 | 10.04 | 20.08
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SUPPORT PIPE DIA 168.3 X 7.11 SA106GRB | M | 4 | 8 | 113.0471 | 226.0942
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SUPPORT PLATE TH10X200X200 SA515GR70 | NO | 10 | 20 | 6.28 | 12.56
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SPARE PIPE DIA 219.1x6.35 SA106GRB | M | 3 | 6 | 99.945 | 199.89
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SPARE PIPE DIA 273x6.35 SA106GRB | M | 2 | 4 | 83.539 | 167.078
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SPARE PIPE DIA 323.9x9.53 SA106GRB | M | 2 | 4 | 147.76 | 295.52
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | PIPE DIA 114.3 X 6.02 SA106GRB | M | 12 | 24 | 192.8304 | 385.6608
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | PIPE OD 60.3X 5.54 SA106GRB | M | 15 | 30 | 112.1999 | 224.3998
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 2 | 4 | 7.68 | 15.36
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | BW LR 45DEG ELL OD114.3X6.02 SA234WPB | NO | 1 | 2 | 1.92 | 3.84
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 SA234WPB | NO | 10 | 20 | 9 | 18
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | ASMEB16.9 BWLR 45DEG ELBOW OD60.3X5.54 SA234WPB | NO | 1 | 2 | 0.45 | 0.9
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | BW RED 114.3X6.02/60.3X5.54 SA234WPB | NO | 2 | 4 | 2.54 | 5.08
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | BW UEQT 114.3X6.02/60.3X5.54 SA234WPB | NO | 5 | 10 | 29.58 | 59.16
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | BW EQL TEE 60.3X5.54 SA234WPB | NO | 2 | 4 | 4.4 | 8.8
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | ORIFICE PLATE ASSY 200X200X10 SA515GR70 | NO | 5 | 10 | 15.7 | 31.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | SUPPORT PIPE OD48.3X5.08 SA106GRB | M | 2 | 4 | 11.492 | 22.984
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | SUPPORT PIPE OD88.9X7.62 SA106GRB | M | 3 | 6 | 45.8192 | 91.6385
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | PLATE 10THK 2000X1000 - SA515GR70 | NO | 1 | 2 | 157 | 314
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | CARRIER PLATE TH16X80X50 SA515GR70 | NO | 8 | 16 | 4 | 8
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | GAL WIRE MESH 1.2 X1200X1200 IS280 | NO | 1 | 2 | 6.24 | 12.48
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | SPARE PIPE DIA 114.3 X 6.02 SA106GRB | M | 1 | 2 | 16.069 | 32.138
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | SPARE PIPE OD 60.3X 5.54 SA106GRB | M | 1 | 2 | 7.479 | 14.958
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | PIPE DIA 168.3 X 7.11 SA106GRB | M | 38 | 76 | 1073.8802 | 2147.7604
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | PIPE OD 60.3X 5.54 SA106GRB | M | 48 | 96 | 359.0404 | 718.0808
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 5 | 10 | 52 | 104
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | BW 45 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 2 | 4 | 10.16 | 20.32
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 SA234WPB | NO | 19 | 38 | 17.1 | 34.2
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | ASMEB16.9 BWLR 45DEG ELBOW OD60.3X5.54 SA234WPB | NO | 2 | 4 | 0.9 | 1.8
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | BW RED 168.3X7.11/114.3X6.02 SA234WPB | NO | 2 | 4 | 6.7 | 13.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | BW RED 114.3X6.02/60.3X5.54 SA234WPB | NO | 2 | 4 | 2.54 | 5.08
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | SUPPORT PIPE OD114. 3X6.02 SA106GRB | M | 5 | 10 | 80.35 | 160.7
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | SUPPORT PIPE OD48.3X5.08 SA106GRB | M | 4 | 8 | 21.656 | 43.312
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | PLATE 10THK 750X750 - SA515GR70 | NO | 1 | 2 | 44.156 | 88.312
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | CARRIER PLATE 16X80X50 SA515GR70 | NO | 16 | 32 | 8.032 | 16.064
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | GAL WIRE MESH 1.2 X1200X2000 IS280 | NO | 1 | 2 | 6.2 | 12.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | SPARE PIPE DIA 168.3 X 7.11 SA106GRB | M | 2.5 | 5 | 70.65 | 141.3
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | SPARE PIPE OD 60.3X 5.54 SA106GRB | M | 3 | 6 | 22.44 | 44.88
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 508.00 X 9.53 - SA106GRB | M | 45 | 90 | 5271.525 | 10543.05
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 168.3 X 7.11 SA106GRB | M | 80 | 160 | 2260.8 | 4521.6
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 114.3 X 6.02 SA106GRB | M | 105 | 210 | 1687.875 | 3375.75
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 323.9 X 9.53 SA106GRB | M | 32 | 64 | 2364.16 | 4728.32
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BW LR 45DEG ELL OD508X9.53 SA234WPB | NO | 3 | 6 | 210.21 | 420.42
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | 90° BW LR ELBOW 323.9X9.53 SA234WPB | NO | 9 | 18 | 486 | 972
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BW LR 45DEG ELL 323.9X9.53SA234WPB | NO | 2 | 4 | 53 | 106
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 34 | 68 | 353.6 | 707.2
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BW 45 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 4 | 8 | 20.8 | 41.6
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 SA234WPB | NO | 30 | 60 | 115.2 | 230.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | ASMEB16.9 BWLR 45DEG ELBOW OD114.3X6.02 SA234WPB | NO | 2 | 4 | 3.84 | 7.68
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BWCONRED508X15.09/323.9X10.31 SA234WPB | NO | 2 | 4 | 153.88 | 307.76
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 12 | 24 | 5.16 | 10.32
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | TEMPERATURE STUB M33X2 L=45 SA105 | NO | 4 | 8 | 2 | 4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SCREW PLUG M33 X 2 SA105 | NO | 4 | 8 | 3.2 | 6.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PACKING RING IS1972 | NO | 4 | 8 | 0.4 | 0.8
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SUPPORT PIPE OD219.1x6.35 SA106GRB | M | 3 | 6 | 99.945 | 199.89
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SUPPORT PLATE 10 THK 250X250-SA515GR70 | NO | 8 | 16 | 39.2 | 78.4
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE OD 355.6x9.53 - SA106GRB | M | 4 | 8 | 325.32 | 650.64
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SUPPORT PLATE 10 THK 400X400-SA515GR70 | NO | 8 | 16 | 100.48 | 200.96
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | CARRIER PLATE 25X50X100 CS SA515GR70 | NO | 12 | 24 | 9.42 | 18.84
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | CARRIER PLATE 16X50X80 CS SA515GR70 | NO | 12 | 24 | 6.03 | 12.06
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | GI SHEET FOR RAIN HOOD 2.5X1200X2500 IS1079D | NO | 4 | 8 | 235.5 | 471
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | GAL WIRE MESH 1.2 X1200X2000 IS280 | NO | 2 | 4 | 12.48 | 24.96
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | ASBESTOS JOINTING SHEET 1.5MM | NO | 2 | 4 | 4.94 | 9.88
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SOW FLANGE NB 100 CL150 SA515GR70 | NO | 5 | 10 | 27.3 | 54.6
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SOW FLANGE NB150 CL150 SA515GR70 | NO | 6 | 12 | 42.9 | 85.8
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | FLAT END CLOSURE FOR OD114.3X6.02 SA234WPB | NO | 2 | 4 | 4.38 | 8.76
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BOLT-M16X90 -8.8-IS1364P1 | NO | 48 | 96 | 5.1 | 10.2
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | NUT -M16 -CL8-IS1364P3 | NO | 48 | 96 | 0.9 | 1.8
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | HEX HD BOLT M20X100,P.CL6.8 IS:1364(P-1) | NO | 48 | 96 | 20.262 | 40.524
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | NUT -M20 -CL6-IS1364P3 | NO | 48 | 96 | 4.29 | 8.58
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SPARE PIPE DIA 508.00 X 9.53 - SA106GRB | M | 2 | 4 | 234.29 | 468.58
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SPARE PIPE DIA 168.3 X 7.11 SA106GRB | M | 3 | 6 | 84.78 | 169.56
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SPARE PIPE DIA 114.3 X 6.02 SA106GRB | M | 3 | 6 | 48.21 | 96.42
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SPARE PIPE DIA 323.9 X 9.53 SA106GRB | M | 2 | 4 | 147.76 | 295.52
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 168.3 X 10.97 SA106GRB | M | 2 | 4 | 67.072 | 134.144
4 | Singrauli 2x800 MW Unit 1 & 2 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 114.3 X 13.49 SA106GRB | M | 2 | 4 | 67.072 | 134.144
4 Total | [10 empty] | 106377.1687
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | OD PIPE DIA 508.00 X 9.53 - SA106GRB | M | 85 | 170 | 9957.75 | 19915.5
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 8 | 16 | 1121.84 | 2243.68
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | BW LR 45DEG ELL OD508X9.53 SA234WPB | NO | 1 | 2 | 70.07 | 140.14
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | BW RED 610X10/508X9.53 SA234WPB | NO | 1 | 2 | 67.81 | 135.62
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | BRANCH PIPE OD 219.1 x 12.70 - SA106GRC L=1000 | M | 1 | 2 | 64.64 | 129.28
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SW STUB NB25 CL3000 CS SA105 | NO | 4 | 8 | 1.72 | 3.44
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SW STUB NB15 CL3000 CS SA105 | NO | 10 | 20 | 4.3 | 8.6
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | THERMOWELL STUB D65 H157 CS SA105 | NO | 2 | 4 | 7.2 | 14.4
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SW STUB 50NB SA105 OD80 L=80 | NO | 4 | 8 | 5.32 | 10.64
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | CARRIAR PLATE 20X55X120 SA515GR70 | NO | 4 | 8 | 4.12 | 8.24
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SUPPORT PIPE OD219.1X8.18 L=5M SA515GR70 | M | 5 | 10 | 212.7 | 425.4
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SUPPORT PLATE 12X2000X1000 SA515GR70 | NO | 1 | 2 | 188.4 | 376.8
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | LUG PLATE 16X628X390 SA515GR70 | NO | 1 | 2 | 19.5 | 39
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SPARE PIPE OD508.00 X 9.53 - SA106GRB | M | 2 | 4 | 234.3 | 468.6
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | TEMP STUB RC 1" L=45-SA105 | NO | 4 | 8 | 2.45 | 4.9
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SCREW PLUG RC 1" SA105 | NO | 4 | 8 | 0.7 | 1.4
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | PIPE DIA 660.0 X 10.0 SA672GRB70CL22 | M | 34 | 68 | 5450.2 | 10900.4
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | OD PIPE DIA 508.00 X 9.53 - SA106GRB | M | 27 | 54 | 3163.046 | 6326.0921
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW LR 90DEG ELL OD660.4X9.53 SA234WPB(W) | NO | 2 | 4 | 476.24 | 952.48
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW LR 30DEG ELL OD660.4X9.53 SA234WPB(W) | NO | 2 | 4 | 158.56 | 317.12
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW LR 53.8 DEG ELL OD660.4X9.53 SA234WPB(W) | NO | 1 | 2 | 142.205 | 284.41
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 3 | 6 | 420.69 | 841.38
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW LR 45DEG ELL OD508X9.53 SA234WPB | NO | 2 | 4 | 140.14 | 280.28
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW RED 610X10/508X9.53 SA234WPB(W) | NO | 2 | 4 | 135.62 | 271.24
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW RED 660X10/508X9.53 SA234WPB(W) | NO | 1 | 2 | 83.59 | 167.18
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW RED 660X10/610X10 SA234WPB(W) | NO | 2 | 4 | 188 | 376
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW UEQT 660X10/508X9.53 SA234WPB(W) | NO | 1 | 2 | 229 | 458
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BRANCH PIPE OD 219.1 X12.7 L=2.5 SA106GRB | M | 2.5 | 5 | 161.6 | 323.2
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SUPPORT PIPE OD 219.1 X12.7 L=1.5 SA106GRB | M | 1.5 | 3 | 96.96 | 193.92
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | FLAT END CLOSURE OD219.1X6.35 SA515GR70 | NO | 3 | 6 | 19.8 | 39.6
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | TEMP.STUB M33X2 (CS)L=64 SA105 | NO | 1 | 2 | 0.7 | 1.4
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SCREW PLUG CS (M33X2) SA105 | NO | 1 | 2 | 0.4 | 0.8
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | COPPER PACKING RING M33X2 IS1972 | NO | 1 | 2 | 0.1 | 0.2
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | TEMP STUB HWR SA105 OD80 L=45 | NO | 1 | 2 | 0.65 | 1.3
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SW STUB NB25 CL3000 CS SA105 OD50 H=54 | NO | 4 | 8 | 1.72 | 3.44
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SW STUB 50NB SA105 OD80 L=75 | NO | 4 | 8 | 5.32 | 10.64
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SW STUB 15NB SA105 OD36 L=44 | NO | 8 | 16 | 1.44 | 2.88
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | TEMP STUB RC 1" L=45-SA105 | NO | 4 | 8 | 2.45 | 4.9
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SCREW PLUG RC 1" SA105 | NO | 4 | 8 | 0.7 | 1.4
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | PIPE DIA 813.0 X 10.0 SA672GRB70CL22 | M | 24 | 48 | 4752 | 9504
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | PIPE DIA 660.0 X 10.0 SA672GRB70CL22 | M | 15 | 30 | 2404.5 | 4809
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 90DEG ELL OD813X10 SA234WPB(W) | NO | 1 | 2 | 379.19 | 758.38
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 30DEG ELL OD813X10 SA234WPB(W) | NO | 3 | 6 | 378 | 756
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 53.9 DEG ELL OD813X10 SA234WPB(W) | NO | 1 | 2 | 226 | 452
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 60DEG ELL OD813X10 SA234WPB(W) | NO | 2 | 4 | 504 | 1008
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW SR 90DEG ELL OD813X10 SA234WPB(W) | NO | 1 | 2 | 252 | 504
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 90DEG ELL OD660X10 SA234WPB | NO | 2 | 4 | 498.78 | 997.56
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 45DEG ELL OD660X10 SA234WPC(W) | NO | 5 | 10 | 623.45 | 1246.9
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW C RED 813X9.53/660.4X9.53 SA234WPB(W) | NO | 1 | 2 | 105 | 210
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW RED 660X9.53/610X9.53 SA234WPB(W) | NO | 2 | 4 | 179.5 | 359
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW RED 914X10/813X10 SA234WPB(W) | NO | 1 | 2 | 129.16 | 258.32
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW UEQT 813X9.53 /660.4X9.53 SA234WPB (W) | NO | 1 | 2 | 357 | 714
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BRANCH PIPE OD 323.9X 9.53 L=2.4 SA106GRB | M | 2.4 | 4.8 | 170.6667 | 341.3333
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | TEMP.STUB M33X2 (CS)L=64 SA105 | NO | 2 | 4 | 1.4 | 2.8
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SCREW PLUG CS (M33X2) SA105 | NO | 2 | 4 | 0.8 | 1.6
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | COPPER PACKING RING M33X2 IS1972 | NO | 2 | 4 | 0.2 | 0.4
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | TEMP STUB HWR SA105 OD80 L=45 | NO | 2 | 4 | 1.3 | 2.6
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SW STUB NB25 CL3000 CS SA105 OD50 H=54 | NO | 4 | 8 | 1.72 | 3.44
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SW STUB 50NB SA105 OD80 L=75 | NO | 4 | 8 | 5.32 | 10.64
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SW STUB 15NB SA105 OD36 L=44 | NO | 8 | 16 | 1.44 | 2.88
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SUPPORT PIPE OD508X9.53 L=800 SA106GRB | M | 0.8 | 1.6 | 93.716 | 187.432
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | TEMP STUB RC 1" L=45-SA105 | NO | 5 | 10 | 3.0625 | 6.125
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SCREW PLUG RC 1" SA105 | NO | 5 | 10 | 0.875 | 1.75
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BRANCH PIPE OD 219.1 X12.7 L=2.5 SA106GRB | M | 2.5 | 5 | 161.6 | 323.2
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | FLAT END CLOSURE for Pipe OD323.9X9.53 SA515GR70 | NO | 3 | 6 | 44.628 | 89.256
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | PIPE DIA 610.0 X 10.0 SA672GRB70CL22 | M | 45 | 90 | 6660 | 13320
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | PIPE DIA 406.4 X 9.53 SA106GRB | M | 85 | 170 | 7927.95 | 15855.9
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | PIPE OD-323.9X9.53-SA106GRC | M | 16 | 32 | 1182.08 | 2364.16
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | OD PIPE DIA 273.00 X 12.70-SA106GRC | M | 73 | 146 | 5950.96 | 11901.92
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | OD PIPE DIA 273.00 X 9.27 - SA106GRB | M | 25 | 50 | 1507 | 3014
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | PIPE 273.00 X 6.35 - SA106GRB | M | 69 | 138 | 2881.095 | 5762.19
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW LR 90DEG ELL 406.4X9.53SA234WPB | NO | 20 | 40 | 1787.4 | 3574.8
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW LR 45DEG ELL OD406.4X9.53 SA234WPB | NO | 5 | 10 | 223.3 | 446.6
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW LR 90DEG ELL OD323.9X9.53 SA234WPC | NO | 4 | 8 | 212.16 | 424.32
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW 90DEG SR ELBOW OD323.9X9.53 SA234WPC | NO | 2 | 4 | 74 | 148
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW LR 90DEG ELL OD273X12.7 SA234WPC | NO | 15 | 30 | 731.85 | 1463.7
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW LR 45DEG ELL OD273X12.7 SA234WPC | NO | 3 | 6 | 73.14 | 146.28
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW 90DEG LR EL OD273.1 X 9.27 SA234WPB | NO | 7 | 14 | 267.54 | 535.08
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW LR 90DEG ELL OD273X6.35 SA234WPB | NO | 6 | 12 | 157.2 | 314.4
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW LR 45DEG ELL OD273X6.35 SA234WPB | NO | 4 | 8 | 52.4 | 104.8
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW RED 610X9.53/559X9.53 SA234WPB | NO | 2 | 4 | 137.52 | 275.04
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | 16.9BW REDUCER OD610X9.53/406.4X9.53 SA234WPB | NO | 2 | 4 | 86 | 172
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW RED 323.9X9.53/273X6.35 SA234WPB | NO | 2 | 4 | 23.44 | 46.88
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW RED 406.4X9.53/323.9X9.53 SA234WPB | NO | 2 | 4 | 60.24 | 120.48
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW RED 406.4X9.53/273X6.35 SA234WPB | NO | 3 | 6 | 71.73 | 143.46
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW UNEQT 610 X 10/ 406.4 X 9.53 SA106GRB | NO | 1 | 2 | 263 | 526
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW UEQT 406.4X9.53/273X9.27 SA234WPB | NO | 4 | 8 | 376.16 | 752.32
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW UEQT 273X12.7/219.1X6.35 SA234WPC | NO | 4 | 8 | 204.08 | 408.16
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW EQT OD406.4X9.53 SA234WPB | NO | 2 | 4 | 180.98 | 361.96
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW EQT OD273X12.7 SA234WPC | NO | 2 | 4 | 113.66 | 227.32
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW UEQT 323.9X9.53/168.3X10.97 SA234WPC | no | 2 | 4 | 108.92 | 217.84
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | TEMP STUB RC 1";L=45 OD55 SA105 | NO | 6 | 12 | 6.618 | 13.236
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SCREW PLUG R 1" SA105 | NO | 6 | 12 | 2.07 | 4.14
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | TEMP STUB M33X2 L=45 CS SA105 | NO | 4 | 8 | 7.108 | 14.216
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SCREW PLUG M33X2 CS SA105 | NO | 4 | 8 | 2.772 | 5.544
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | COPPER PACKING RING M33X2 IS1972 | NO | 4 | 8 | 0.04 | 0.08
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SW STUB NB25 CL3000 SA105 | NO | 20 | 40 | 13.96 | 27.92
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | THERMOWELL STUB OD70H80 CS SA105 | NO | 2 | 4 | 3.4 | 6.8
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | CARRIER PLATE 20X50X120 CS SA515GR70 | NO | 36 | 72 | 36 | 72
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BRANCH PIPE OD 219.1 X12.7 L=400 SA106GRC | M | 2 | 4 | 129.28 | 258.56
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BRANCH PIPE DIA 114.30 X 11.13 - SA106GRB | M | 2 | 4 | 56.58 | 113.16
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD114.3X6.02 L=10500 SA106GRB | M | 10.5 | 21 | 168.782 | 337.564
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD168.3X7.11 L=1M SA106GRB | M | 1 | 2 | 28.2633 | 56.5267
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD219.1X8.18 L=5300 SA106GRB | M | 5.3 | 10.6 | 225.497 | 450.994
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | LUG PLATE 16X443X260 SA515GR70 | NO | 1 | 2 | 9.4 | 18.8
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | PLATE 20THKX4000X4000 SA515GR70 | NO | 1 | 2 | 2512 | 5024
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SW STUB 15NB SA105 OD36 L=44 | NO | 15 | 30 | 2.7 | 5.4
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | TEMP STUB RC 1";L=45 OD55 SA105 | NO | 6 | 12 | 6.618 | 13.236
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SCREW PLUG R 1" SA105 | NO | 6 | 12 | 2.07 | 4.14
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | TEMP STUB M33X2 L=45 CS SA105 | NO | 4 | 8 | 7.108 | 14.216
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SCREW PLUG M33X2 CS SA105 | NO | 4 | 8 | 2.772 | 5.544
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | COPPER PACKING RING M33X2 IS1972 | NO | 4 | 8 | 0.04 | 0.08
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SW STUB NB25 CL3000 SA105 | NO | 20 | 40 | 13.96 | 27.92
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | THERMOWELL STUB OD70H80 CS SA105 | NO | 2 | 4 | 3.4 | 6.8
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | CARRIER PLATE 20X50X120 CS SA515GR70 | NO | 36 | 72 | 36 | 72
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD114.3X6.02 L=10500 SA106GRB | M | 10.5 | 21 | 168.782 | 337.564
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD168.3X7.11 L=1M SA106GRB | M | 1 | 2 | 28.2633 | 56.5267
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD219.1X8.18 L=5300 SA106GRB | M | 5.3 | 10.6 | 225.497 | 450.994
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | LUG PLATE 16X443X260 SA515GR70 | NO | 1 | 2 | 9.4 | 18.8
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | PLATE 20THKX4000X4000 SA515GR70 | NO | 1 | 2 | 2512 | 5024
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SW STUB 15NB SA105 OD36 L=44 | NO | 15 | 30 | 2.7 | 5.4
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | PIPE OD965x38 SA672GRB70CL22 | M | 2.5 | 5 | 2171.675 | 4343.35
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | PIPE OD965x10 SA672GRB70CL22 | M | 10 | 20 | 2355 | 4710
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SPARE PIPE OD406.4x21.44 SA106 GR.C | M | 1 | 2 | 203.545 | 407.09
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | PIPE OD406.4X21.44, SA106GRC | M | 31 | 62 | 6309.895 | 12619.79
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | PIPE OD323.9X9.53, SA106GRB | M | 1.5 | 3 | 110.82 | 221.64
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BRANCH PIPE OD323.9X12.7, SA106GRB | M | 1 | 2 | 97.46 | 194.92
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BRANCH PIPE OD114.3X13.49, SA106GRC | M | 1 | 2 | 33.54 | 67.08
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BW LR 90DEG ELL OD965X10 SA234WPB(W) | NO | 3 | 6 | 1607.07 | 3214.14
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BW 90DEG LR ELBOW OD406.4x21.44 SA234WPC | NO | 7 | 14 | 1364.44 | 2728.88
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BW RED 965x38/711x10 SA234WPB | NO | 1 | 2 | 466.722 | 933.444
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BW UNEQT OD965X10/508X9.53 SA234WPB | NO | 1 | 2 | 476.81 | 953.62
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BW EQT OD965X10 SA234WPB | NO | 1 | 2 | 529.79 | 1059.58
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | FLAT END CLOSURE for Pipe OD323.9X9.53 SA515GR70 | NO | 1 | 2 | 31.617 | 63.234
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | FLAT END CLOSURE for Pipe OD219.1X8.18 SA515GR70 | NO | 1 | 2 | 8.63 | 17.26
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | FLAT END CLOSURE for Pipe OD114.3X6.02 SA515GR70 | NO | 1 | 2 | 2.77 | 5.54
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD273X9.53 L=1500 SA106GRB | M | 1.5 | 3 | 92.883 | 185.766
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD323X9.53 L=2500 SA106GRB | M | 2.5 | 5 | 184.7 | 369.4
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SW STUB NB25 CL6000 CS SA105 | NO | 8 | 16 | 4.56 | 9.12
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SW STUB NB25 CL3000 CS SA105 OD50 H=54 | NO | 5 | 10 | 2.15 | 4.3
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SW STUB NB15 CL3000 CS SA105 OD36 H=44 | NO | 14 | 28 | 2.52 | 5.04
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | TEMPERATURE STUB M33X2 (CS) SA105 ( D-78 , H-45) (ROD-80) | NO | 3 | 6 | 3.36 | 6.72
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SCREW PLUG M33X2 CS SA105 | NO | 3 | 6 | 1.2 | 2.4
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | PACKING RING IS1972 | NO | 3 | 6 | 0.03 | 0.06
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | TEMP.STUB L=45 SA105 ( HWR ) ROD-80 DIA | NO | 2 | 4 | 1.3 | 2.6
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | TEMP.STUB RC 1 "(CS) D55 , L=45 SA105 (ROD-D63) | NO | 8 | 16 | 5.6 | 11.2
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SCREW PLUG R 1 " (CS) SA105 (ROD-D40) | NO | 8 | 16 | 1.6 | 3.2
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | CARRIER PLATE 20X50X120 SA515GR70 | NO | 24 | 48 | 21.12 | 42.24
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | LUG PLATE 16X559X325 SA515GR70 | NO | 2 | 4 | 29.6 | 59.2
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SUPPORT PLATE 20X1500X2000 SA515GR70 | NO | 1 | 2 | 471 | 942
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SUPPORT PLATE 10X2000X1000 SA515GR70 | NO | 2 | 4 | 157 | 314
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | THERMOWELL STUB SA105 OD-70, H-80 (ROD-80) | NO | 5 | 10 | 8.5 | 17
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | PIPE OD323.9X21.44 SA335P22 | M | 28 | 56 | 4477.844 | 8955.688
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | PIPE OD273.00 X 18.26 - SA335P22 | M | 44 | 88 | 5047.416 | 10094.832
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SPARE PIPE OD273.00 X 18.26 - SA335P22 | M | 1.5 | 3 | 172.071 | 344.142
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | PIPE OD219.1X15.09 - SA335P22 | M | 19 | 38 | 1442.499 | 2884.998
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | PIPE OD114.30 X 8.56 - SA335P22 | M | 1.5 | 3 | 33.483 | 66.966
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW 90DEG LR ELBOW OD323.9X21.44 SA234WP22 | NO | 4 | 8 | 458.96 | 917.92
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW 90DEG LR ELBOW OD273X18.26 SA234WP22 | NO | 12 | 24 | 823.32 | 1646.64
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW LR 45DEG ELL 273 X 18.26 SA234WP22 | NO | 2 | 4 | 68.62 | 137.24
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW 90DEG LR ELBOW OD219.1X15.09 SA234WP22CL1 | NO | 3 | 6 | 109.05 | 218.1
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW LR 45DEG ELL 168.3X18.26 SA234WP22CL1 | NO | 2 | 4 | 25 | 50
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW C RED OD323.9x21.44 / 273x18.26 SA234WP22CL1 | NO | 3 | 6 | 89.82 | 179.64
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW C RED OD323.9x21.44 / 219.1X15.09 SA234WP22CL1 | NO | 1 | 2 | 27.69 | 55.38
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW C RED OD219.1X15.09 / 168.3X18.26 SA234WP22CL1 | NO | 2 | 4 | 23.88 | 47.76
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW C RED OD273.1X16/219.1X15.09,SA234WP22CL1 | NO | 2 | 4 | 36.9 | 73.8
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW UNEQT OD323.9X21.44/219.1X15.09 SA234WP22CL1 | NO | 1 | 2 | 117.66 | 235.32
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW UNEQT OD323.9X21.44/273X18.26 SA234WP22CL1 | NO | 1 | 2 | 123 | 246
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | STUB OD114.3X13.49 SA182 F22 CL3 L=250 | NO | 2 | 4 | 25.74 | 51.48
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | FLAT END CLOSURE OD114.3X8.56 SA387 GR22 (OD 115X30THK) | NO | 2 | 4 | 4.84 | 9.68
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SW STUB NB40 CL6000 SA182F22CL3 OD70 H=60 | NO | 2 | 4 | 3.4 | 6.8
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SW STUB NB50 CL6000 SA182F22CL3 OD84 H=60 | NO | 4 | 8 | 7.84 | 15.68
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SW STUB NB25 CL6000 SA182F22CL3 OD060 H=60 | NO | 16 | 32 | 9.12 | 18.24
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | THERMOWELL STUB D120 H-80 SA182F22CL3 | NO | 5 | 10 | 26 | 52
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | TEMPERATURE STUB RC-1.5'' OD124 L-45 SA182F22CL3 | NO | 14 | 28 | 39.62 | 79.24
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SCREW PLUG RC 1.5 '' SA182 F22 | NO | 14 | 28 | 7 | 14
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | CARRIER PLATE 20X55X120 SA387GR22CL2 | NO | 12 | 24 | 12.432 | 24.864
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SUPPORT PIPE OD114.3X13.49 L=1000 SA335P22 (2 - NO ) | M | 1 | 2 | 33.54 | 67.08
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SUPPORT PIPE OD168.3X18.26 L=1000 SA335P22 ( 2 - NO ) | M | 1 | 2 | 42.56 | 85.12
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | TEMPERATURE STUB M33X2 (AS) SA182F22 ( D-78 , H-45) (ROD-80) | NO | 2 | 4 | 2.24 | 4.48
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SCREW PLUG M33X2 SA182F22 | NO | 2 | 4 | 0.8 | 1.6
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | PACKING RING IS1972 | NO | 2 | 4 | 0.02 | 0.04
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | PIPE OD406.4X21.44 SA106GRC | M | 42 | 84 | 8548.89 | 17097.78
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SPARE PIPE OD406.4X21.44 SA106GRC | M | 1 | 2 | 203.545 | 407.09
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | PIPE 323.90 X 14.27 - SA106GRC | M | 18 | 36 | 1961.1 | 3922.2
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | BW 90DEG LR ELBOW OD406.4X21.44 SA234 WPC | NO | 13 | 26 | 2533.96 | 5067.92
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | BW 90DEG LR EL OD323.9X14.27 SA234WPC | NO | 11 | 22 | 859.98 | 1719.96
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | BW RED 323.9X14.27/273X12.7 SA234WPC | NO | 2 | 4 | 40.88 | 81.76
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | BW UEQT OD406.4X21.44/OD323.9X14.27 SA234WPC | NO | 2 | 4 | 370.62 | 741.24
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SUPPORT PIPE OD323.9X9.53 L=1000 SA106GRC | M | 1 | 2 | 73.88 | 147.76
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SUPPORT PIPE OD168.3X10.97 L=1000 SA106GRC | M | 1 | 2 | 42.56 | 85.12
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | TEMP.STUB RC 1-1/2"(CS) D98 L=45 SA105 (ROD-100) | NO | 10 | 20 | 17 | 34
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SCREW PLUG R 1-1/2"(CS) SA105 ( ROD-50) | NO | 10 | 20 | 5 | 10
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | TEMP.STUB- CS D78 L-45 M33X2 SA105 (ROD-80) | NO | 2 | 4 | 2.24 | 4.48
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SCREW PLUG CS (M33X2) SA105 (ROD-50) | NO | 2 | 4 | 0.8 | 1.6
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | COPPER PACKING RING M33X2 IS1972 | NO | 2 | 4 | 0.02 | 0.04
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SW STUB CS NB25 CL:6000 SA105 | NO | 10 | 20 | 5.7 | 11.4
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | THERMOWELL STUB WELDED D114 H95 CS SA105 (ROD-125mm) | NO | 4 | 8 | 19 | 38
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | CARRIER PLATE 20THKX50X120 SA515GR70 | NO | 4 | 8 | 3.52 | 7.04
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SUPPORT PLATE 10THKX1000X1000 SA515GR70 | NO | 1 | 2 | 78.5 | 157
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | PIPE OD 406.4X12.7 -SA335P22 | M | 47 | 94 | 5781 | 11562
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | SPARE PIPE OD 406.4X12.7 -SA335P22 | M | 1 | 2 | 123 | 246
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | PIPE DIA 273.0 X 9.27 SA335P22 | M | 9 | 18 | 542.79 | 1085.58
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | PIPE OD 355.6X12.7 -SA335P22 | M | 1 | 2 | 53.698 | 107.396
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | BW 90DEG LR ELBOW OD 406.4X12.7 -SA234 WP22 | NO | 9 | 18 | 1080 | 2160
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | BW LR 90DEG ELL OD273X9.27 SA234WP22CL1 | NO | 5 | 10 | 180.4 | 360.8
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | RED OD457X12.7/406.4X12.7 SA234 WP22 | NO | 1 | 2 | 50.065 | 100.13
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | RED OD406.4X12.7/355.6X12.7 SA234 WP22 | NO | 2 | 4 | 82.266 | 164.532
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | C RED OD406.4X12.7/OD273X12.7 SA234WP22CL1 | NO | 1 | 2 | 37.06 | 74.12
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | BW UEQT 406.4X12.7/273X9.27 SA234WP22CL1 | NO | 1 | 2 | 109 | 218
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | BW UEQT 406.4X12.7/168.3x7.11 SA234WP22CL1 | NO | 2 | 4 | 209.72 | 419.44
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | BRANCH PIPE OD168.3X10.97 L=1500 SA335P22 | M | 1.5 | 3 | 63.75 | 127.5
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | SUPPORT PIPE OD168.3X10.97 L=300 SA335P22 | M | 0.3 | 0.6 | 12.75 | 25.5
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | TEMPERATURE STUB RC 1-1/2'' OD125 L45 SA182F22CL3 | NO | 12 | 24 | 33.96 | 67.92
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | SCREW PLUG RC1-1/2'' SA182F22CL3 | NO | 12 | 24 | 6 | 12
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | TEMPERATURE STUB HWR OD50 : L=45 SA182F22CL3 | NO | 2 | 4 | 0.74 | 1.48
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | SW STUB NB25 CL6000 F22 SA182F22CL3 | NO | 14 | 28 | 7.98 | 15.96
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | THERMOWELL STUB(TW) OD78 H=64 SA182F22CL3 | NO | 5 | 10 | 9 | 18
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | SW STUB NB50 CL3000 F22 SA182F22CL3 | NO | 2 | 4 | 2.66 | 5.32
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | CARRIER PLATE 20X55X120 SA387GR22CL2 | NO | 4 | 8 | 4.144 | 8.288
5 | Singrauli 2x800 MW Unit 1 & 2 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | FLAT END CAP OD168.3X7.11 SA387 Gr22 OD169X32 | NO | 2 | 4 | 11.26 | 22.52
5 Total | [10 empty] | 249743.7098
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | PIPE DIA 323.9 X 9.53 SA106GRB | M | 4 | 8 | 295.52 | 591.04
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | PIPE DIA 219.1 X 6.35 X 6500 - SA106GRB | M | 50 | 100 | 1665.5 | 3331
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | PIPE DIA 168.3 X 7.11 SA106GRB | M | 77 | 154 | 2176.02 | 4352.04
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | PIPE DIA 114.3 X 6.02 SA106GRB | M | 27 | 54 | 433.89 | 867.78
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW LR 90DEG ELL OD219.1X6.35 SA234WPB | NO | 12 | 24 | 206.52 | 413.04
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW LR 60DEG ELL OD219.1X6.35 SA234WPB | NO | 1 | 2 | 12.09 | 24.18
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 16 | 32 | 179.68 | 359.36
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW 45°LR ELBOW 168.3X7.11 SA234WPB | NO | 2 | 4 | 11.22 | 22.44
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 7 | 14 | 26.88 | 53.76
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW LR 30DEG ELL OD114.3X6.02 SA234WPB | NO | 2 | 4 | 2.56 | 5.12
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW RED 323.9X9.53/168.3X7.11 SA234WPB | NO | 1 | 2 | 11.26 | 22.52
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW RED 219.1X6.35/168.3X7.11 SA234WPB | NO | 1 | 2 | 4.84 | 9.68
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW RED 168.3X7.11/114.3X6.02 SA234WPB | NO | 1 | 2 | 3.16 | 6.32
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW EQT OD168.3X7.11 SA234WPB | NO | 1 | 2 | 13.28 | 26.56
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW UEQT 323.9X6.35/114.3X6.02 SA234WPB | NO | 1 | 2 | 35.68 | 71.36
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | SUPPORT PIPE DIA 168.3 X 7.11 SA106GRB | M | 1.7 | 3.4 | 48.042 | 96.084
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | SUPPORT PIPE DIA 114.3 X 6.02 SA106GRB | M | 2 | 4 | 32.14 | 64.28
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | SUPPORT PIPE DIA 88.9X6.02 SA106GRB | M | 0.6 | 1.2 | 7.38 | 14.76
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BOTTOM PLATE 10MM THK 1000X1000 SA515GR70 | NO | 1 | 2 | 78.5 | 157
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | LUG PLATE 12MM THK 340X170 SA515GR70 | NO | 1 | 2 | 3.7 | 7.4
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | SW STUB NB25 CL3000 CS OD36,H=44 SA105 | NO | 4 | 8 | 1.72 | 3.44
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | CARRIER PLATE 16X50X120 SA515GR70 | NO | 4 | 8 | 3 | 6
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | PIPE OD114.3X6.02 SA106GRB | M | 36 | 72 | 578.88 | 1157.76
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | PIPE OD168.3X7.11 SA106GRB | M | 45 | 90 | 1271.7 | 2543.4
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 12 | 24 | 52.08 | 104.16
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 14 | 28 | 157.22 | 314.44
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | BW RED 168.3X7.11/114.3X6.02 SA234WPB | NO | 3 | 6 | 9.87 | 19.74
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | BW UEQT OD168.3X7.11/114.3X6.02 SA234WPB | NO | 3 | 6 | 42 | 84
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | SW STUB NB25 OD46 H=44 SA105 | NO | 4 | 8 | 1.72 | 3.44
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | SUPPORT PLATE 10MM THK 500x500 SA515GR70 | NO | 1 | 2 | 19.63 | 39.26
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | SUPPORT PIPE DIA 88.9X6.02 SA106GRB | M | 2 | 4 | 24.6 | 49.2
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | EQT 33.4X4.55 SA234WPB | NO | 2 | 4 | 0.86 | 1.72
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | ELBOW 90DEG OD33.4X4.55 SA234WPB | NO | 4 | 8 | 1 | 2
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | PIPE OD 33.4X4.55 SA106GRB | M | 6 | 12 | 19.44 | 38.88
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | PIPE OD 21.3X3.73 SA106GRB | M | 5 | 10 | 8.1 | 16.2
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | PIPE OD273x12.7x6000 - SA106 Gr.C | M | 200 | 400 | 16176 | 32352
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | PIPE OD323.9x12.7x6000 - SA106 Gr.C | M | 5 | 10 | 487.3 | 974.6
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SUPPORT PIPE OD273x12.7x6000 - SA106 Gr.C | M | 1 | 2 | 81.52 | 163.04
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SUPPORT PIPE OD219.1x12.7x6000 - SA106 Gr.C | M | 7.5 | 15 | 484.8 | 969.6
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SUPPORT PIPE OD114.3x6.02x6000 - SA106 Gr.C | M | 2 | 4 | 32.12 | 64.24
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW LR 90DEG ELL OD273x12.7 SA234WPC | NO | 50 | 100 | 2617.5 | 5235
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW LR 45DEG ELL OD273x12.7 SA234WPC | NO | 12 | 24 | 314.04 | 628.08
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW RED 273.1X12.7 / 168.3X8.56 SA234WPC | NO | 4 | 8 | 48.28 | 96.56
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW RED 273X12.7 / 219.1x12.7 SA234WPC | NO | 2 | 4 | 26.28 | 52.56
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW RED 323.9X12.7 / 219.1x12.7 SA234WPC | NO | 2 | 4 | 33.96 | 67.92
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW RED 323.9X12.7 / 273x12.7 SA234WPC | NO | 6 | 12 | 109.74 | 219.48
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | ASME B16.11 SW STUB NB25,CL:6000 SA105 | NO | 16 | 32 | 9.12 | 18.24
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | TEMP STUB RC 1.5" L=45-SA105 | NO | 18 | 36 | 31.86 | 63.72
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SCREW PLUG RC 1.5" SA105 | NO | 18 | 36 | 9 | 18
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | THERMOWEL STUB OD-63.5 H=154-SA105 C.S | NO | 4 | 8 | 12.408 | 24.816
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | CARRIER PLATE 12X80X40-SA515GR70 | NO | 16 | 32 | 4.816 | 9.632
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | LUG PLATE 16x443x260 SA515 GR70 | NO | 5 | 10 | 72.35 | 144.7
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BOTTOM PLATE 10THKX150X150 SA515 GR70 | NO | 4 | 8 | 7.04 | 14.08
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BOTTOM PLATE 10THKX250X250 SA515 GR70 | NO | 12 | 24 | 58.875 | 117.75
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BOTTOM PLATE 10THKX300X300 SA515 GR70 | NO | 1 | 2 | 7.065 | 14.13
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | TEMPERATURE STUB M33X2, L=64 SA105 | NO | 4 | 8 | 2.8 | 5.6
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | PACKING RING M33x2 IS1972 | NO | 4 | 8 | 0.04 | 0.08
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SCREW PLUG M33 x 2 SA105 SA105 | NO | 4 | 8 | 0.64 | 1.28
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SPARE PIPE OD273x12.7x6000 - SA106 Gr.C | M | 4 | 8 | 323.2 | 646.4
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | PIPE OD273X6.35x6000 - SA106 Gr.B | M | 175 | 350 | 7308 | 14616
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | PIPE OD273X12.7x6000 - SA106 Gr.B | M | 7 | 14 | 570.71 | 1141.42
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | PIPE OD323.9X12.7x6000 - SA106 Gr.B | M | 2.5 | 5 | 243.65 | 487.3
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SUPPORT PIPE OD114.3x6.02 SA106GR.B | M | 6 | 12 | 96.48 | 192.96
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SUPPORT PIPE OD168.3x7.11 SA106GR.B | M | 3 | 6 | 84.78 | 169.56
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SUPPORT PIPE OD219.1x12.7 SA106GR.B | M | 3 | 6 | 193.92 | 387.84
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SPARE PIPE OD273x6.35 SA106GR.B | M | 3 | 6 | 125.28 | 250.56
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW LR 90DEG ELL OD273x6.35 SA234WPB | NO | 29 | 58 | 777.49 | 1554.98
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW LR 60DEG ELL OD273x6.35 SA234WPB | NO | 3 | 6 | 54 | 108
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW LR 45DEG ELL OD273x6.35 SA234WPB | NO | 3 | 6 | 40.23 | 80.46
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW LR 30DEG ELL OD273x6.35 SA234WPB | NO | 4 | 8 | 36 | 72
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW LR 90DEG ELL OD 355.6x9.53 SA234WPB | NO | 2 | 4 | 136.2 | 272.4
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW RED 355.6x9.53 / 273X6.35 SA234WPB | NO | 4 | 8 | 95.204 | 190.408
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW RED 323.9X12.7 / 219.1x12.7 SA234WPC | NO | 2 | 4 | 43.968 | 87.936
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW RED 273.1X12.7 / 168.3X8.56 SA234WPC | NO | 4 | 8 | 48.32 | 96.64
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW RED 273X12.7 / 219.1x12.7 SA234WPC | NO | 2 | 4 | 26.28 | 52.56
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | ASME B16.11 SW STUB NB15,CL:3000 SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 6 | 12 | 2.58 | 5.16
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | TEMP STUB RC 1" L=45-SA105 | NO | 18 | 36 | 9.284 | 18.568
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SCREW PLUG RC 1" SA105 | NO | 18 | 36 | 3.6 | 7.2
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | THERMOWEL STUB OD-70 H=157-SA105 | NO | 4 | 8 | 14.4 | 28.8
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | LUG PLATE 16x443x260 SA515 GR70 | NO | 2 | 4 | 28.932 | 57.864
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BOTTOM PLATE 10THKX250X250 SA515 GR70 | NO | 4 | 8 | 19.624 | 39.248
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BOTTOM PLATE 10THKX200X200 SA515 GR70 | NO | 20 | 40 | 62.8 | 125.6
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BOTTOM PLATE 10THKX350X350 SA515 GR70 | NO | 2 | 4 | 19.232 | 38.464
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | PIPE OD219.1X6.35x6000 - SA106 Gr.B | M | 60 | 120 | 1999.2 | 3998.4
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | PIPE OD219.1X12.7x6000 - SA106 Gr.B | M | 4 | 8 | 258.56 | 517.12
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | SUPPORT PIPE OD168.3x7.11 SA106GR.B | M | 3.5 | 7 | 98.91 | 197.82
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW LR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 13 | 26 | 223.73 | 447.46
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW LR 45DEG ELL OD219.1x6.35 SA234WPB | NO | 2 | 4 | 17.2 | 34.4
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW LR 30DEG ELL OD219.1x12.7 SA234WPB | NO | 1 | 2 | 11.13 | 22.26
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW LR 90EG ELL OD273x12.7 SA234WPB | NO | 1 | 2 | 52.47 | 104.94
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW RED 273X6.35 / 219.1X6.35 SA234WPB | NO | 2 | 4 | 13.5 | 27
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW RED 273X12.7 / 219.1X12.7 SA234WPB | NO | 1 | 2 | 13.14 | 26.28
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW RED OD219.1x6.35/168.3x10.97 SA234WPB | NO | 2 | 4 | 8 | 16
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW RED OD219.1x12.7/168.3x10.97 SA234WPB | NO | 2 | 4 | 17.46 | 34.92
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW EQT 219.1x12.7 SA234WPB | NO | 1 | 2 | 37.4 | 74.8
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 3 | 6 | 1.29 | 2.58
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | TEMPERATURE STUB M33x2 L=64 -SA105 | NO | 1 | 2 | 0.7 | 1.4
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | SCREW PLUG M33 X 2-SA105 | NO | 1 | 2 | 0.16 | 0.32
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | PACKING RING M33x2 - IS1972 | NO | 1 | 2 | 0.01 | 0.02
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | TEMP STUB RC 1" L=64-SA105 | NO | 7 | 14 | 4.9 | 9.8
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | SCREW PLUG RC 1" SA105 | NO | 7 | 14 | 1.4 | 2.8
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BOTTOM PLATE 10THKX1000X1500 SA515 GR70 | NO | 1 | 2 | 117.75 | 235.5
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | PIPE OD273X12.7x6000 - SA106 Gr.B | M | 39 | 78 | 3179.28 | 6358.56
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | SUPPORT PIPE OD219.1x12.7 L=1.5 SA106GR.B | M | 1.5 | 3 | 96.96 | 193.92
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | BW LR 90DEG ELL OD273x12.7 SA234WPB | NO | 23 | 46 | 1206.81 | 2413.62
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | BW LR 60DEG ELL OD273x12.7 SA234WPB | NO | 3 | 6 | 104.94 | 209.88
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | BW EQT 273x12.7 SA234WPB | NO | 1 | 2 | 56.83 | 113.66
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | BW RED 406.4x17 / 273x12.7 SA234WPB | NO | 1 | 2 | 48.96 | 97.92
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 3 | 6 | 1.29 | 2.58
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | TEMP STUB RC 1" L=64-SA105 | NO | 6 | 12 | 4.2 | 8.4
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | SCREW PLUG RC 1" SA105 | NO | 6 | 12 | 1.2 | 2.4
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | TEMPERATURE STUB M33x2 L=64 -SA105 | NO | 2 | 4 | 1.4 | 2.8
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | SCREW PLUG M33 X 2-SA105 | NO | 2 | 4 | 0.32 | 0.64
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | PACKING RING M33x2 - IS1972 | NO | 2 | 4 | 0.02 | 0.04
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | LUG PLATE 16x443x260 SA515 GR70 | NO | 1 | 2 | 14.46 | 28.92
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | BOTTOM PLATE 10THKX250X250 SA515 GR70 | NO | 4 | 8 | 19.64 | 39.28
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | SPARE PIPE OD273X12.7 - SA106 Gr.B | M | 1 | 2 | 81.52 | 163.04
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | PIPE OD273X12.7x6000 - SA106 Gr.B | M | 34 | 68 | 2771.68 | 5543.36
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | PIPE OD2191.X6.35x6000 - SA106 Gr.B | M | 45 | 90 | 1498.95 | 2997.9
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SPARE PIPE OD219.1x12.7 SA106GR.B | M | 1 | 2 | 64.64 | 129.28
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SUPPORT PIPE OD168.3x7.11 SA106GR.B | M | 2 | 4 | 56.52 | 113.04
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW SR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 1 | 2 | 11.46 | 22.92
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW LR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 7 | 14 | 120.47 | 240.94
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW LR 45DEG ELL OD219.1x6.35 SA234WPB | NO | 5 | 10 | 43 | 86
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW LR 30DEG ELL OD219.1x6.35 SA234WPB | NO | 4 | 8 | 23 | 46
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW LR 90DEG ELL OD273x12.7 SA234WPB | NO | 11 | 22 | 577.17 | 1154.34
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW LR 45DEG ELL OD273x12.7 SA234WPB | NO | 1 | 2 | 26.24 | 52.48
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW RED 323.9x9.53 / 273x12.7 SA234WPB | NO | 1 | 2 | 13.88 | 27.76
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW RED 323.9x9.53/ 219.1X6.35 SA234WPB | NO | 1 | 2 | 12.9 | 25.8
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW RED 273x6.35/219.1X6.35 SA234WPB | NO | 1 | 2 | 6.75 | 13.5
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 2 | 4 | 0.86 | 1.72
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | TEMPERATURE STUB M33x2 L=64 -SA105 | NO | 2 | 4 | 1.4 | 2.8
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SCREW PLUG M33 X 2-SA105 | NO | 2 | 4 | 0.32 | 0.64
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | PACKING RING M33x2 - IS1972 | NO | 2 | 4 | 0.02 | 0.04
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | TEMP STUB RC 1" L=64-SA105 | NO | 4 | 8 | 2.8 | 5.6
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SCREW PLUG RC 1" SA105 | NO | 4 | 8 | 0.8 | 1.6
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | LUG PLATE 16x443x260 SA515 GR70 | NO | 1 | 2 | 14.47 | 28.94
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BOTTOM PLATE 10THKX250X250 SA515 GR70 | NO | 4 | 8 | 19.6 | 39.2
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SPARE PIPE OD273X12.7x6000 - SA106 Gr.B | M | 1 | 2 | 81.52 | 163.04
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | PIPE DIA 273.0 X 6.35 X 6500 SA106GRB | M | 68 | 136 | 2839.68 | 5679.36
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | PIPE OD-219.1X12.7X6000-SA106GRC | M | 39 | 78 | 2520.96 | 5041.92
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | PIPE DIA 88.9 X 5.49 SA106GRB | M | 38 | 76 | 429.02 | 858.04
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW LR 90DEG ELL OD273X6.35 SA234WPB | NO | 20 | 40 | 537.6 | 1075.2
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW LR 45DEG ELL OD273X6.35 SA234WPB | NO | 4 | 8 | 53.76 | 107.52
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW LR 90DEG ELL OD219.1X8.18 SA234WPC | NO | 15 | 30 | 329.7 | 659.4
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW LR 45DEG ELL OD219.1X8.18 SA234WPC | NO | 2 | 4 | 21.98 | 43.96
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 5 | 10 | 10.05 | 20.1
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW RED 323.9X6.35/273X6.35 SA234WPB | NO | 4 | 8 | 37.4 | 74.8
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW RED 323.9X12.7/219.1X12.7 SA234WPC | NO | 1 | 2 | 17 | 34
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW RED 219.1X8.18/168.3X7.11 SA234WPC | NO | 1 | 2 | 5.76 | 11.52
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW RED 168.3X7.11/88.9X5.49 SA234WPB | NO | 1 | 2 | 3.1 | 6.2
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW EQT OD273X6.35 SA234WPB | NO | 1 | 2 | 29.11 | 58.22
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW EQT OD219.1X8.18 SA234WPC | NO | 1 | 2 | 24.61 | 49.22
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW EQT OD88.9X5.49 SA234WPB | NO | 1 | 2 | 3.29 | 6.58
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | ASME B16.11 SW STUB NB25 CL 3000 SA105 | NO | 5 | 10 | 2.15 | 4.3
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | TEMP STUB-CS- RC1" L=64 - CS SA105 | NO | 9 | 18 | 6.3 | 12.6
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | CARBON STEEL PLUG 1" CS SA105 | NO | 9 | 18 | 1.8 | 3.6
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | TEMP STUB MX33X2 L=64CS SA105 | NO | 1 | 2 | 0.7 | 1.4
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SOW FLANGE NB 25 CL150 SA515GR 70 | NO | 2 | 4 | 1.8 | 3.6
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SOW FLANGE NB50 CL 150 SA515GR 70 | NO | 2 | 4 | 4 | 8
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | LUG PLATE 12THK 260X125 SA515GR 70 | NO | 3 | 6 | 9.18 | 18.36
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SUPPORT PIPE OD60.3X5.54 SA234WPB | M | 3 | 6 | 22.44 | 44.88
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SUPPORT PIPE OD219.1X6.35 SA234WPB | M | 4 | 8 | 133.24 | 266.48
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SUPPORT PIPE OD168.3X7.11 SA234WPB | NO | 4 | 8 | 113.04 | 226.08
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | CARRIER PLATE 16X50X120 CS SA515GR70 | NO | 12 | 24 | 9.12 | 18.24
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | STUD M12 X 1.75 X140 SA193B7 | NO | 8 | 16 | 0.896 | 1.792
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | NUT M12 SA194GR7 | NO | 16 | 32 | 0.32 | 0.64
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | STUD M16 X 2 X 110 SA193B7 | NO | 8 | 16 | 1.16 | 2.32
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | NUT M16 SA194GR7 | NO | 16 | 32 | 0.48 | 0.96
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | NON-ASBESTOS JOINTING SHT 1.5MMX500X500 | NO | 1 | 2 | 0.618 | 1.236
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | PIPE OD-323.9X12.7X6000-SA106GRC | M | 2 | 4 | 194.92 | 389.84
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | PIPE 88.9X5.49 - SA106GRB | M | 35 | 70 | 395.15 | 790.3
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | PIPE OD60.3X5.54 L=6000 SA106GRB | M | 12 | 24 | 89.76 | 179.52
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 10 | 20 | 20.2 | 40.4
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | BW LR 90DEG ELL 60.3 X 5.54 SA234WPB | NO | 6 | 12 | 6.36 | 12.72
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | BW UEQT 88.9X5.49/60.3X5.54 SA234WPB | NO | 2 | 4 | 5.94 | 11.88
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | SW STUB NB25 CL3000 SA105 | NO | 2 | 4 | 0.86 | 1.72
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | SW STUB NB15 CL3000 SA105 | NO | 2 | 4 | 0.36 | 0.72
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | SPARE PIPE 88.9X5.49 - SA106GRB | M | 1 | 2 | 11.29 | 22.58
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | SPARE PIPE OD60.3X5.54 L=6000 SA106GRB | M | 1 | 2 | 7.48 | 14.96
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | PIPE DIA 114.3 X 6.02 SA106GRB | M | 52 | 104 | 835.64 | 1671.28
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 SA234GRB | NO | 6 | 12 | 25.98 | 51.96
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | ASMEB16.9 BW EQUAL TEE OD114.3X6.02 SA234GRB | NO | 6 | 12 | 33.9 | 67.8
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | SOW FLANGE NB100 CL150-OD230X30 SA515GR70 | NO | 2 | 4 | 10.6 | 21.2
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | BOLT-M16x90 -8.8-IS1364P1 | NO | 8 | 16 | 1.36 | 2.72
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | NUT -M16 -CL4-IS1363P3 | NO | 8 | 16 | 0.24 | 0.48
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | NON-ASBESTOS JOINTING SHEET 1.5MM | NO | 1 | 2 | 2.47 | 4.94
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | BLIND FLANGE NB100 CL150 SA515GR70 | NO | 2 | 4 | 15.44 | 30.88
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | SPARE PIPE OD 114.3X6.02 L=2000 SA234GRB | M | 2 | 4 | 32.14 | 64.28
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | SUPPORT PIPE DIA 88.9 X 5.49, L=4000 SA234GRB | M | 4 | 8 | 45.16 | 90.32
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | PLATE 10.0 MM, 1000X500 SA515GR70 | NO | 1 | 2 | 39.25 | 78.5
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | PIPE DIA 323.9 X 6.35 SA106GRB L=195MM | NO | 1 | 2 | 9.697 | 19.394
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | BW RED 323.9X6.35/114.3X6.02 SA234WPB | NO | 1 | 2 | 8.16 | 16.32
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | PIPE OD 114.3X6.02 L=350MM SA106GRB | NO | 2 | 4 | 3.15 | 6.3
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | PIPE OD168.3x7.11x6000 - SA106 Gr.B | M | 60 | 120 | 1695.6 | 3391.2
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | PIPE OD219.1x12.7x6000 - SA106 Gr.B | M | 7 | 14 | 452.48 | 904.96
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | SUPPORT PIPE OD114.3x6.02 L=2M SA106GR.B | M | 2 | 4 | 32.16 | 64.32
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | SUPPORT PIPE OD168.3x7.11 L=1M-SA106GRB | M | 1 | 2 | 28.26 | 56.52
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW LR 90DEG ELL OD219.1X12.7 SA234WPB | NO | 5 | 10 | 166.95 | 333.9
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 12 | 24 | 134.4 | 268.8
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW LR 45DEG ELL OD168.3X7.11 SA234WPB | NO | 2 | 4 | 11.2 | 22.4
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW LR 30DEG ELL OD168.3X7.11 SA234WPB | NO | 1 | 2 | 3.73 | 7.46
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW RED 219.1x12.7/168.3x7.11 SA234WPB | NO | 3 | 6 | 26.19 | 52.38
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW RED 219.1x12.7/88.9X7.62 SA234WPB | NO | 1 | 2 | 7.31 | 14.62
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW RED 168.3x7.11/88.9x 7.62SA234WPB | NO | 1 | 2 | 3.09 | 6.18
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 5 | 10 | 2.15 | 4.3
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | TEMP STUB RC 1" L=64-SA105 | NO | 8 | 16 | 5.6 | 11.2
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | SCREW PLUG RC 1" SA105 | NO | 8 | 16 | 1.6 | 3.2
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | TEMPERATURE STUB M33x2 L=64 -SA105 | NO | 5 | 10 | 3.5 | 7
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | SCREW PLUG M33 X 2-SA105 | NO | 5 | 10 | 0.05 | 0.1
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | PACKING RING M33x2 - IS1972 | NO | 5 | 10 | 0.8 | 1.6
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | CARRIER PLATE 12X50X80-SA515GR70 | NO | 4 | 8 | 1.507 | 3.014
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BOTTOM PLATE 10THKX1000X500 SA515 GR70 | NO | 1 | 2 | 39.25 | 78.5
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 8 | 0.72 | 1.44
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | PIPE OD168.3X10.97x6000 - SA106 Gr.C | M | 29 | 58 | 1234.24 | 2468.48
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | PIPE OD219.1X12.7x6000 - SA106 Gr.C | M | 117 | 234 | 7562.9965 | 15125.993
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | SUPPORT PIPE OD114.3x6.02 L=1000 SA106GR.C | M | 2 | 4 | 32.14 | 64.28
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | SUPPORT PIPE OD168.3x7.11 L=3000 SA106GR.C | M | 3 | 6 | 84.78 | 169.56
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW LR 90DEG ELL OD168.3x10.97 SA234WPC | NO | 13 | 26 | 199.03 | 398.06
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW LR 45DEG ELL OD168.3x10.97 SA234WPC | NO | 2 | 4 | 15.31 | 30.62
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW LR 90DEG ELL OD219.1x12.7 SA234WPC | NO | 26 | 52 | 805.22 | 1610.44
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW LR 45DEG ELL OD219.1x12.7 SA234WPC | NO | 6 | 12 | 92.88 | 185.76
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW LR 30DEG ELL OD219.1x12.7 SA234WPC | NO | 1 | 2 | 15.48 | 30.96
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW RED 219.1x12.7 / 168.3x10.97 SA234WPC | NO | 4 | 8 | 37.2 | 74.4
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | ASME B16.11 SW STUB NB25,CL:6000 SA105 | NO | 14 | 28 | 7.98 | 15.96
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | TEMP STUB RC 1 1/2 " L=64-SA105 | NO | 16 | 32 | 37.504 | 75.008
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | SCREW PLUG RC 1 1/2 " SA105 | NO | 16 | 32 | 8 | 16
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | THERMOWEL STUB OD-70 H=157-SA105 | NO | 4 | 8 | 14.4 | 28.8
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | LUG PLATE 16x428x240 SA515 GR70 | NO | 1 | 2 | 12.901 | 25.802
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | LUG PLATE 12x340x170 SA515 GR70 | NO | 3 | 6 | 16.334 | 32.668
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BOTTOM PLATE 10THKX150X150 SA515 GR70 | NO | 2 | 4 | 3.532 | 7.064
6 | Singrauli 2x800 MW Unit 1 & 2 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BOTTOM PLATE 10THKX200X200 SA515 GR70 | NO | 6 | 12 | 18.84 | 37.68
6 Total | [10 empty] | 146522.871
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | PIPE OD 219.1 x 36 - SA106GRC | M | 48 | 96 | 7802.82 | 15605.64
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | SPARE PIPE OD 219.1 x 36 - SA106GRC | M | 2 | 4 | 325.118 | 650.236
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | PIPE DIA 168.3 X 27.5 SA106GRC | M | 7 | 14 | 668.425 | 1336.85
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | PIPE DIA 168.3 X 31 SA335 P22 | M | 2 | 4 | 209.934 | 419.868
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | PIPE DIA 114.3 X 6.02 SA106GRC | M | 1 | 2 | 16.075 | 32.15
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW LR 90DEG ELL OD219.1X36 SA234WPC | NO | 9 | 18 | 700.92 | 1401.84
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW LR 90DEG ELL OD168.3x27.5 SA234WPC | NO | 3 | 6 | 103.05 | 206.1
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW SR 90DEG ELL OD168.3x31 SA234WP22 | NO | 1 | 2 | 25.05 | 50.1
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW LR 90DEG ELL OD168.3x31 SA234WP22 | NO | 4 | 8 | 150.96 | 301.92
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW UEQT 219.1X36/168.3X27.5 SA234WPC | NO | 1 | 2 | 86.48 | 172.96
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW C.RED 219.1 X 36/168.3X27.5 SA234WPC | NO | 1 | 2 | 19.79 | 39.58
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | CARRIER PLATE 16X50X120-SA515 GR70 | NO | 4 | 8 | 3.04 | 6.08
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | ASME B16.11 SW STUB NB25,CL:9000-SA105 | NO | 4 | 8 | 3.24 | 6.48
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | TEMP STUB RC 1.5" OD98 L=64 - CS SA105 | NO | 1 | 2 | 2.344 | 4.688
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | SCREW PLUG RC 1.5" CS SA105 | NO | 1 | 2 | 0.5 | 1
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | ASME B16.11 SW STUB NB25,CL:9000-SA182F22 | NO | 2 | 4 | 1.62 | 3.24
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | LUGPLATE 16X340X170 SA387 GR22 | NO | 2 | 4 | 7.4 | 14.8
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | PIPE DIA 219.1x12.7 SA106GRC | M | 70 | 140 | 4524.87 | 9049.74
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | PIPE DIA 168.3x7.11 SA106GRB | M | 70 | 140 | 1978.2 | 3956.4
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | SPARE PIPE DIA 168.3x7.11 SA106GRB | M | 2 | 4 | 56.52 | 113.04
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | SPARE PIPE DIA 219.1x12.7 SA106GRC | M | 2 | 4 | 129.282 | 258.564
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | SUPP.PIPE DIA 114.3 X 8.56 SA106GRC | M | 3 | 6 | 66.963 | 133.926
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW LR 90DEG ELBOW OD219.1x12.7 SA234WPC | NO | 12 | 24 | 371.16 | 742.32
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW LR 30DEG ELBOW OD219.1x12.7 SA234WPC | NO | 1 | 2 | 10.31 | 20.62
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW LR 90DEG ELBOW OD168.3x7.11SA234WPB | NO | 8 | 16 | 81.12 | 162.24
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW LR 45DEG ELBOW OD168.3x7.11 SA234WPB | NO | 3 | 6 | 15.21 | 30.42
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW RED 219.1x12.7/168.3X7.11 SA234WPB | NO | 1 | 2 | 7.01 | 14.02
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW RED 323.9x12.7/219.1X12.7 SA234WPC | NO | 2 | 4 | 35 | 70
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | CARRIER PLATE 20X50X120-SA515 GR70 | NO | 28 | 56 | 91.448 | 182.896
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | PLATE 20X300X300 SA515 GR70 | NO | 4 | 8 | 56.52 | 113.04
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | PLATE 20X150X150 SA515 GR70 | NO | 9 | 18 | 31.788 | 63.576
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | PLATE 20X200X200 SA515 GR70 | NO | 1 | 2 | 6.28 | 12.56
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | ASME B16.11 SW STUB NB25,CL:9000-SA105 | NO | 1 | 2 | 0.81 | 1.62
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | ASME B16.11 SW STUB NB50,CL:9000 SA105 | NO | 6 | 12 | 14.64 | 29.28
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | PIPE DIA 168.3 X 21.95 - SA106GRC | M | 170 | 340 | 13467.4 | 26934.8
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | PIPE DIA 114.3x13.49 SA106GRC | M | 33 | 66 | 1107.15 | 2214.3
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | PIPE DIA 88.9x11.13 SA106GRC | M | 66 | 132 | 1409.1 | 2818.2
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SPARE PIPE DIA 168.3 X 21.95 - SA106GRC | M | 3 | 6 | 237.66 | 475.32
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SPARE PIPE DIA 114.3x13.49 SA106GRC | M | 1 | 2 | 33.55 | 67.1
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SPARE PIPE DIA 88.9x11.13 SA106GRC | M | 2 | 4 | 42.7 | 85.4
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW LR 90DEG ELBOW OD168.3x21.95 SA234WPC | NO | 25 | 50 | 712.5 | 1425
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW LR 90DEG ELBOW OD114.3x13.49 SA234WPC | NO | 11 | 22 | 88.11 | 176.22
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW LR 90DEG ELBOW OD88.9x11.13 SA234WPC | NO | 16 | 32 | 61.12 | 122.24
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW EQT OD168.3x21.95 SA234WPC | NO | 1 | 2 | 37.04 | 74.08
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW UEQT OD168.3x21.95/OD114.3X13.49 SA234WPC | NO | 1 | 2 | 32.04 | 64.08
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW RED OD168.3x21.95/OD114.3X13.49 SA234WPC | NO | 2 | 4 | 15.78 | 31.56
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW RED OD168.3x21.95/OD88.9X11.13 SA234WPC | NO | 1 | 2 | 6.89 | 13.78
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | ASME B16.11 SW STUB NB25,CL:6000-SA105 | NO | 1 | 2 | 0.57 | 1.14
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | ASME B16.11 SW STUB NB50,CL:6000 SA105 | NO | 5 | 10 | 9.8 | 19.6
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | THERMOWEL STUB OD70 H-146 CS SA105 | NO | 1 | 2 | 3.6 | 7.2
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | LUG PLATE 12x260x125 SA515 GR70 | NO | 1 | 2 | 2.2 | 4.4
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SUPPORT PIPE OD 114.3x13.49 SA106 GRC | M | 4.5 | 9 | 150.975 | 301.95
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SUPPORT PIPE OD 88.9x11.13 SA106 GRC | M | 3 | 6 | 64.05 | 128.1
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SUPPORT PIPE OD 60.3x11.07 SA106 GRC | M | 2 | 4 | 26.88 | 53.76
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BOTTOM PLATE 16THK 1500x2000 SA515 GR70 | NO | 1 | 2 | 376.8 | 753.6
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | TEMP STUB RC 1.5" OD98 L=64 - CS SA105 | NO | 4 | 8 | 9.376 | 18.752
7 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SCREW PLUG RC 1.5" CS SA105 | NO | 4 | 8 | 2 | 4
7 Total | [10 empty] | 71002.376
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | PIPE OD 323.9X 9.53 X 6000 - SA106GRB | M | 12 | 24 | 886.56 | 1773.12
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | PIPE OD 273x9.27 SA106GRB | M | 43 | 86 | 2592.384 | 5184.768
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | PIPE DIA 33.4X4.55 SA106GRB | M | 5 | 10 | 16.15 | 32.3
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | BW LR 90DEG ELL OD323.9x9.53 SA234WPB | NO | 1 | 2 | 54 | 108
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | BW LR 90DEG ELL OD273x9.27 SA234WPB | NO | 6 | 12 | 222 | 444
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | BW EQT OD323.9x9.53 SA234WPB | NO | 1 | 2 | 60.42 | 120.84
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | BW RED OD323.9x9.53/273x9.27 SA234WPB | NO | 1 | 2 | 13.8801 | 27.7603
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | ASME B16.11 SW STUB NB25 CL:6000-SA105 | NO | 2 | 4 | 2.9146 | 5.8291
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | BOTTEM PLATE 10 THK500x500 SA515 GR70 | NO | 1 | 2 | 2.4271 | 4.8542
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | SUPPORT PIPE OD219.1x12.7 SA106 GRB | M | 1 | 2 | 64.644 | 129.288
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | SPARE PIPE OD 323.9X 9.53 X 6000 - SA106GRB | M | 2 | 4 | 147.76 | 295.52
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | SPARE PIPE OD 273x9.27 X 6000 - SA106GRB | M | 2 | 4 | 120.58 | 241.16
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | PIPE OD 114.3X6.02 SA106GRB | M | 36 | 72 | 578.68 | 1157.36
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | PIPE OD 88.9X5.49 SA106GRB | M | 88 | 176 | 993.72 | 1987.44
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 20 | 32.37 | 64.74
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | 90DEG BW LR ELBOW 114.3X6.02 SA234WPB | NO | 4 | 8 | 20 | 40
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | 90DEG BW LR ELBOW 88.9X5.49 SA234WPB | NO | 21 | 42 | 48.3 | 96.6
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | BW RED 114.3X6.02/88.9X5.49 SA234WPB | NO | 1 | 2 | 1.46 | 2.92
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | BW EQUAL TEE OD 88.9 X 5.49 SA234WPB | NO | 2 | 4 | 7.6 | 15.2
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SW STUB-CS-NB 25 CLASS 6000 CS SA105 | NO | 5 | 10 | 2.15 | 4.3
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SW STUB-CS-NB 50 CLASS 6000 CS SA105 | NO | 2 | 4 | 1.8 | 3.6
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | TEMPERATURE STUB M33X2 L=45 SA105 | NO | 2 | 4 | 1 | 2
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SCREW PLUG M33 X 2 SA105 | NO | 2 | 4 | 1.6 | 3.2
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | PACKING RING IS1972 | NO | 2 | 4 | 0.2 | 0.4
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SUPPORT PIPE OD 60.3X 5.54 SA106GRB | M | 5.5 | 11 | 41.1461 | 82.2922
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SUPPORT PLATE TH 12X1500X1000MM SA515GR70 | NO | 1 | 2 | 141.3 | 282.6
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | CARRIER PLATE 10X50X80 SA515GR70 | NO | 4 | 8 | 1.256 | 2.512
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SPARE PIPE OD 114.3X6.02 SA106GRB | M | 2 | 4 | 32.149 | 64.298
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SPARE PIPE OD 88.9X5.49 SA106GRB | M | 2 | 4 | 22.5847 | 45.1693
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SUPPORT PIPE OD 88.9X5.49 SA106GRB | M | 1 | 2 | 11.2923 | 22.5847
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | BWUN EQUAL TEEOD 114.3X6.02/60.3X5.54 SA234WPB | NO | 2 | 4 | 9.86 | 19.72
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | TEMP STUB RC1 INCH SA105 | NO | 4 | 8 | 3.376 | 6.752
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | CARBON STEEL PLUG 1" SA105 | NO | 4 | 8 | 0.8 | 1.6
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PIPE OD 457 X 9.53X 6000 - SA106GRC | M | 72 | 144 | 7571.52 | 15143.04
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PIPE OD 457 X 12.7X 6000 - SA106GRC | M | 42 | 84 | 5844.3 | 11688.6
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SPARE PIPE OD457X9.53 SA106 GR.C | M | 2 | 4 | 210.32 | 420.64
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SPARE PIPE OD457X12.7 SA106 GR.C | M | 1 | 2 | 139.15 | 278.3
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SUPPORT PIPE OD406.4x9.53 L=5000 SA106GRC | M | 5 | 10 | 466.3 | 932.6
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SUPPORT PIPE OD219.1x12.7 L=2000 SA106GRC | M | 2 | 4 | 129.28 | 258.56
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SUPPORT PIPE OD168.3X7.11 L=4500 SA106GRC | M | 4.5 | 9 | 127.17 | 254.34
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 90DEG ELL OD457x12.7 SA234WPC | NO | 8 | 16 | 1200.16 | 2400.32
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW SR 90DEG ELL OD457x9.53 SA234WPC | NO | 2 | 4 | 150.9 | 301.8
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 45DEG ELL OD457x9.53 SA234WPC | NO | 1 | 2 | 56.63 | 113.26
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 30DEG ELL OD457x9.53 SA234WPC | NO | 1 | 2 | 37.75 | 75.5
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 90DEG ELL OD457x9.53 SA234WPC | NO | 12 | 24 | 1359.6 | 2719.2
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 90DEG ELL OD355.6x9.53 SA234WPC | NO | 2 | 4 | 136.2 | 272.4
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW SR 90DEG ELL OD457x12.7 SA234WPC | NO | 2 | 4 | 199.88 | 399.76
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 30DEG ELL OD457x12.7 SA234WPC | NO | 2 | 4 | 99.9 | 199.8
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW RED 457x9.53 /355.6x9.53 SA234WPC | NO | 2 | 4 | 72.24 | 144.48
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW RED 457x9.53 /406.4x9.53 SA234WPC | NO | 2 | 4 | 75.88 | 151.76
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW RED 559x12.7 / 457x12.7 SA234WPC | NO | 2 | 4 | 159.08 | 318.16
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW RED 610x10 / 457x9.53 SA234WPC | NO | 4 | 8 | 261.84 | 523.68
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BOTTOM PLATE 10 THK 450 X 450-SA515GR70 | NO | 7 | 14 | 111.272 | 222.544
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BOTTOM PLATE 10 THK 2000 X 2000-SA515GR70 | NO | 1 | 2 | 314 | 628
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | CARRIER PLATE 20X120X50-SA515GR70 | NO | 8 | 16 | 7.04 | 14.08
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | ASME B16.11 SW STUB NB15 CL:3000-SA105 | NO | 22 | 44 | 3.96 | 7.92
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SW STUB NB25 CL:3000-SA105 | NO | 8 | 16 | 3.44 | 6.88
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | ASME B16.11 SW STUB NB40 CL:3000-SA105 | NO | 2 | 4 | 1.5 | 3
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SW STUB NB50 CL:3000-SA105 | NO | 6 | 12 | 7.98 | 15.96
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | TEMP STUB RC 1" L=45-SA105 | NO | 3 | 6 | 2.532 | 5.064
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SCREW PLUG RC 1" (CS) SA105 | NO | 3 | 6 | 0.6 | 1.2
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | TEMP STUB RC 1.5" L=45 - CS SA105 | NO | 7 | 14 | 7 | 14
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SCREW PLUG RC 1.5"-CS SA105 | NO | 7 | 14 | 3.5 | 7
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | TEMPERATURE STUB M33x2 L=64 (CS)-SA105 | NO | 1 | 2 | 0.7 | 1.4
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SCREW PLUG M33 X 2-SA105 | NO | 1 | 2 | 0.8 | 1.6
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PACKING RING-COPPER | NO | 1 | 2 | 0.01 | 0.02
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | LUG PLATE 16 THK 400X650-SA515 GR70 | NO | 2 | 4 | 65.312 | 130.624
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PIPE OD 355.6 X 9.53 L=2000 -SA106GRC | M | 2 | 4 | 162.64 | 325.28
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PIPE OD 60.3 X 5.54 L=10M -SA106GRB | M | 10 | 20 | 74.8 | 149.6
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PIPE OD 33.9 X 4.55 L=10M -SA106GRB | M | 10 | 20 | 32.3 | 64.6
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 90DEG 60.3 X 5.54 SA234WPB | NO | 2 | 4 | 1.78 | 3.56
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 90DEG 33.4 X 4.55 -SA234WPB | NO | 2 | 4 | 0.38 | 0.76
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | PIPE OD 355.6 X 9.53 X 6000 - SA106GRC | M | 96 | 192 | 7808.064 | 15616.128
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SUPPORT PIPE OD 323.9 x 9.53 - SA106GRC | M | 1.5 | 3 | 110.82 | 221.64
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SUPPORT PIPE DIA 168.3 X 7.11 SA106GRC | M | 1 | 2 | 28.264 | 56.528
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SPARE PIPE OD355.6x9.53 SA106 GRC | M | 2 | 4 | 162.66 | 325.32
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | BW LR 90DEG ELL OD355.6X9.53 SA234WPC | NO | 15 | 30 | 1050 | 2100
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | BW RED 355.6X9.53/323.9X9.53 SA234WPC | NO | 4 | 8 | 102.4 | 204.8
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | BW RED 406.4X12.7/355.6X9.53 SA234WPC | NO | 1 | 2 | 45 | 90
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | BW RED 457X9.53/ 355.6X9.53 SA234WPC | NO | 2 | 4 | 72.24 | 144.48
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | ASME B16.11 SW STUB NB15 CL:3000-SA105 | NO | 9 | 18 | 1.62 | 3.24
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 5 | 10 | 2.15 | 4.3
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | ASME B16.11 SW STUB NB50 CL:3000-SA105 | NO | 4 | 8 | 5.32 | 10.64
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | TEMP STUB RC 1.5" L=45 - CS SA105 | NO | 7 | 14 | 7 | 14
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SCREW PLUG RC 1.5" CS SA105 | NO | 7 | 14 | 3.5 | 7
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | TEMP STUB RC 1" L=45-SA105 | NO | 3 | 6 | 2.532 | 5.064
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SCREW PLUG RC 1" (CS) SA105 | NO | 3 | 6 | 0.6 | 1.2
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | CARRIER PLATE T=20X50X120-SA515GR70 | NO | 12 | 24 | 10.56 | 21.12
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SUPPORT PLATE 10X350X350-SA515GR70 | NO | 4 | 8 | 38.464 | 76.928
8 | Singrauli 2x800 MW Unit 1 & 2 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | LUG PLATE 16 THK 546X315-SA515 GR70 | NO | 1 | 2 | 14 | 28
8 Total | [10 empty] | 69402.4078
Grand Total | [10 empty] | 1034295.6711
Notes- 1. For Schedule No 1, the quantity & weight for both boilers of a project are not the same (Boiler 1- 59.33 MT kg; Boiler 2- 41.83 MT). In view of the same, for Schedule No 1 alone, the quantity & weight has been seperately indicated for 2 boilers of the project. For rest of the Schedules, quantity & weight indicated is for 1 boiler of the project. 2. Suitable cushion +/-15% in quantity / weight shall be considered by the supplier in tender. 3. Pipe Size / Thickness / Specification mentioned in table may vary for very few cases during detail drawing stage. 4. IBR approval for applicable drawings / PGMA' are in vendor scope. 5. Fabrication drawings shall be prepared by vendor and shall be submitted to BHEL for review and approval prior to commencement of manufacturing. Please refer Technical Specification for better clarity. 6. All attachments like Stubs, Carrier Plates etc shall be welded on to the main pipe. These attachments have been indicated separately in the detailed BOM for better understanding the quantum involved. For better clarity regarding welding details / scope for these items, please refer Sl No 4.6 of the Technical Specification. 7. Items for which weight has been revised have been highlighed in Red.

## BOM- Sipat 1x800 MW
Enquiry No 4202600002 dt 14.01.2026 Procurement of TG Cycle Piping of IBR & Non IBR Systems for NTPC projects Annexure C- Detailed Piping System BOM (R01)
Schedule No | Project | Piping System | IBR / Non IBR | PGMA | Drawing No | Item Description | UOM | Quantity per Boiler of the project | Total Quantity for 1 Boiler | *Weight per Boiler of the project (kg) | Total Weight for 1 Boiler (kg)
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD355.6X9.53 SA106GRB | M | 4 | 4 | 325.32 | 325.32
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD219.1X6.35 SA106GRB | M | 5 | 5 | 166.55 | 166.55
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD168.3X7.11 SA106GRB | M | 5.5 | 5.5 | 155.43 | 155.43
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | PIPE OD88.9X5.49 SA106GRB | M | 5.5 | 5.5 | 62.095 | 62.095
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD355.6X9.53 SA234WPB | NO | 1 | 1 | 70 | 70
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 45DEG ELL OD355.6x9.53 SA234WPB | NO | 1 | 1 | 34.03 | 34.03
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 1 | 1 | 16.7 | 16.7
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 45DEG ELL OD219.1x6.35 SA234WPB | NO | 1 | 1 | 7.97 | 7.97
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 1 | 1 | 10.14 | 10.14
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 1 | 1 | 2.02 | 2.02
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M804/01p | BW LR 45DEG ELL OD88.9X5.49 SA234WPB | NO | 1 | 1 | 1.01 | 1.01
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PIPE OD 219.1 x 6.35 - SA106GRB | M | 60 | 60 | 1998.6 | 1998.6
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PIPE OD 219.1 x 12.7 - SA106GRC | M | 15 | 15 | 969.6 | 969.6
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PIPE DIA 114.3 X 6.02 SA106GRB | M | 1 | 1 | 16.07 | 16.07
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SUPPORT PIPE OD168.3x7.11 SA106GRB | M | 2.5 | 2.5 | 70.655 | 70.655
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 90DEG ELL OD219.1X6.35 SA234WPB | NO | 11 | 11 | 183.7 | 183.7
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 45DEG ELL OD219.1X6.35 SA234WPB | NO | 2 | 2 | 15.96 | 15.96
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 90DEG ELL OD219.1X12.7 SA234WPC | NO | 1 | 1 | 30.97 | 30.97
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW LR 45DEG ELL OD219.1X12.7 SA234WPC | NO | 2 | 2 | 30.96 | 30.96
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW REDUCER - OD273x12.7/OD219.1x12.7 SA234WPC | NO | 1 | 1 | 13.29 | 13.29
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | FLAT END CLOSURE OD114.3X6.02 SA515GR70 | NO | 1 | 1 | 2.2 | 2.2
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW UEQT 219.1X6.35/114.3X6.02 SA234WPB | NO | 1 | 1 | 17.18 | 17.18
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | BW EQT 219.1X6.35 SA234WPB | NO | 1 | 1 | 19.27 | 19.27
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | ASME B16.11 SW STUB NB40 CL:6000-SA105 | NO | 2 | 2 | 2.14 | 2.14
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | ASME B16.11 SW STUB NB25 CL:6000-SA105 | NO | 2 | 2 | 1.14 | 1.14
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | TEMPERATURE STUB M33x2 L=45 OD-78 -SA105 | NO | 1 | 1 | 1.12 | 1.12
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SCREW PLUG M33 X 2-SA105 | NO | 1 | 1 | 0.8 | 0.8
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | PACKING RING M33x2 | NO | 1 | 1 | 0.01 | 0.01
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | CARRIER PLATE T=8X50X80-SA515GR70 | NO | 8 | 8 | 2.009 | 2.009
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SUPPORT PIPE 168.3X7.11 SA106GRB | M | 3 | 3 | 84.78 | 84.78
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-339 | PE-DG-508-142-M801/01p | SUPPORT PLATE 10X200X200-SA515GR70 | NO | 8 | 8 | 25.12 | 25.12
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 508x9.53 - SA106 GRB | M | 15 | 15 | 1757.25 | 1757.25
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 355.6x9.53 - SA106 GRB | M | 4 | 4 | 325.2 | 325.2
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 273x9.27 - SA106 GRB | M | 40 | 40 | 2411.52 | 2411.52
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 168.3x7.11 - SA106 GRB | M | 8 | 8 | 226.096 | 226.096
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 219.1x6.35 - SA106 GRB | M | 1 | 1 | 33.31 | 33.31
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | PIPE OD 114.3x6.02 - SA106 GRB | M | 1 | 1 | 16.0733 | 16.0733
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 3 | 3 | 420.69 | 420.69
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 45DEG ELL OD508X9.53 SA234WPB | NO | 1 | 1 | 70.07 | 70.07
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD355.6X9.53 SA234WPB | NO | 2 | 2 | 136.2 | 136.2
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD273X9.27 SA234WPB | NO | 10 | 10 | 370 | 370
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 3 | 3 | 30.42 | 30.42
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW UEQT 273X9.27/114.3x6.02 SA234WPB | NO | 1 | 1 | 34.4 | 34.4
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW UEQT 273X9.27/168.3x7.11 SA234WPB | NO | 1 | 1 | 35.46 | 35.46
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW UEQT 508X9.53/219.1x6.35 SA234WPB | NO | 1 | 1 | 120.7 | 120.7
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW EQT 273X9.27 SA234WPB | NO | 1 | 1 | 38.83 | 38.83
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW EQT 508X9.53 SA234WPB | NO | 1 | 1 | 141.95 | 141.95
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 508X9.53/273x9.27 SA234WPB | NO | 2 | 2 | 93.28 | 93.28
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 355.6X9.53/168.3x7.11 SA234WPB | NO | 1 | 1 | 18.49 | 18.49
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 406.4x9.53/355.6X9.53 SA234WPB | NO | 1 | 1 | 31.21 | 31.21
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | BW RED 965X9.53/508X9.53 SA234WPB | NO | 1 | 1 | 117.84 | 117.84
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 8 | 8 | 3.44 | 3.44
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | FLAT END CLOSURE OD219.1X6.35 SA515GR70 | NO | 1 | 1 | 8.5 | 8.5
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | FLAT END CLOSURE OD114.3X6.02 SA515GR70 | NO | 1 | 1 | 2.2 | 2.2
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | CARRIER PLATE 16X120X50-SA515GR70 | NO | 8 | 8 | 7.04 | 7.04
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | CARRIER PLATE 16X80X50-SA515GR70 | NO | 8 | 8 | 3.84 | 3.84
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | LUG PLATE 16 THK 443x260 -SA515 GR70 | NO | 1 | 1 | 9.4 | 9.4
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | SUPPORT PLATE 12x500x500-SA515GR70 | NO | 4 | 4 | 94.2 | 94.2
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | SUPPORT PIPE OD 457 X 9.53 L=1000-SA106GRB | M | 1 | 1 | 105.3 | 105.3
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | ORIFICE PLATE ASSY-NB350 -SA515GR70 | NO | 1 | 1 | 30.788 | 30.788
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | SOW FLANGE NB350CL150 SA515GR70 | NO | 2 | 2 | 179.75 | 179.75
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | STUD M27 X 3 X 160 SA193B7 | NO | 12 | 12 | 8.1 | 8.1
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | NUT -M27 -2H | NO | 24 | 24 | 4.08 | 4.08
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-345 | PE-DG-508-142-M806/01p | NON-ASBESTOS JOINTING SHEET 3.0MM | NO | 1 | 1 | 5.69 | 5.69
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | PIPE DIA 88.9 X 5.49 SA106GRB | M | 68 | 68 | 767.72 | 767.72
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 14 | 14 | 28.28 | 28.28
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | ASMEB16.9 BWLR 45DEG ELBOW OD88.9X5.49 SA234WPB | NO | 2 | 2 | 2.02 | 2.02
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | TEMP STUB M33X2; L=64 SA105 | NO | 1 | 1 | 0.72 | 0.72
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | COPPER PACKING RING M33X2 IS1972 | NO | 1 | 1 | 0.01 | 0.01
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SCREW PLUG CS (M33X2) SA105 | NO | 1 | 1 | 0.4 | 0.4
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 4 | 4 | 4.3 | 4.3
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SW STUB NB15 CL 3000 SA105 | NO | 2 | 2 | 0.546 | 0.546
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SW STUB NB40 CL3000 CS SA105 | NO | 1 | 1 | 0.75 | 0.75
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | CARRIER PLATE 16X50X80 SA515GR70 | NO | 4 | 4 | 2.01 | 2.01
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SUPPORT PIPE OD60.3X5.54 L=4000 SA106GRB | M | 4 | 4 | 29.92 | 29.92
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | PLATE 10.0 MM 1000X1000 SA515GR70 | NO | 1 | 1 | 78.5 | 78.5
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | TEMP STUB RC 1" L=64-SA105 | NO | 3 | 3 | 1.8375 | 1.8375
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-349 | PE-DG-508-142-M805/01p | SCREW PLUG RC 1" SA105 | NO | 3 | 3 | 0.525 | 0.525
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | PIPE DIA 273.0 X 9.27 SA106GRB | M | 240 | 240 | 14469.12 | 14469.12
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BRANCH PIPE OD 168.30 x 7.11 X 6500 - SA106GRB | M | 3 | 3 | 84.78 | 84.78
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BRANCH PIPE DIA 114.3 X 6.02 SA106GRB | M | 3 | 3 | 48.21 | 48.21
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW LR 90DEG ELL OD273X9.27 SA234WPB | NO | 44 | 44 | 1587.52 | 1587.52
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW RED 355.6X9.53/273X9.27 SA234WPB | NO | 1 | 1 | 23.67 | 23.67
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW UEQT 355.6X9.53/273X9.27 SA234WPB | NO | 1 | 1 | 68.37 | 68.37
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW EQT OD273X9.27 SA234WPB | NO | 4 | 4 | 168.12 | 168.12
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW UEQT 273X9.27/114.3X6.02 SA234WPB | NO | 6 | 6 | 219.24 | 219.24
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | FLAT END CLOSURE FOR OD114.3X6.02 SA515GR70 | NO | 6 | 6 | 16.2 | 16.2
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | TEMP STUB M33X2; L=64 SA105 | NO | 4 | 4 | 2.88 | 2.88
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | COPPER PACKING RING M33X2 IS1972 | NO | 4 | 4 | 0.04 | 0.04
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | SCREW PLUG CS (M33X2) SA105 | NO | 4 | 4 | 1.6 | 1.6
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | SW STUB NB25 CL3000 SA105 | NO | 2 | 2 | 1.66 | 1.66
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | FLAT END CLOSURE OD273x9.27 SA515 GR70 | NO | 2 | 2 | 34.92 | 34.92
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | CARRIER PLATE 16X50X80 SA515GR70 | NO | 8 | 8 | 4.02 | 4.02
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | SUPPORT PIPE OD219.1X8.18 L=5M SA106GRB | M | 5 | 5 | 212.7 | 212.7
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | PLATE TH 10.0X2000X2500 SA515 GR70 | NO | 1 | 1 | 392.5 | 392.5
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | TEMPERATURE STUB RC 1" L=45 CS-SA105 | NO | 3 | 3 | 1.5 | 1.5
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | PLUG R 1" CS SA105 | NO | 3 | 3 | 0.6 | 0.6
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | BW UEQT 273X9.27/168.3X7.11 SA234WPB | NO | 2 | 2 | 75.42 | 75.42
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | SUPPORT PIPE OD114.3X6.02 L=5M SA106GRB | NO | 5 | 5 | 80.35 | 80.35
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-341 | PE-DG-508-142-M802/00 | FLAT END CLOSURE OD168.3x7.11 SA515 GR70 | NO | 2 | 2 | 9.3 | 9.3
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | PIPE DIA 457 X 9.53 - SA335P22 | M | 7 | 7 | 736.12 | 736.12
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | PIPE DIA 457 X 9.53 - SA335P11 | M | 1.5 | 1.5 | 157.74 | 157.74
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | PIPE DIA 457 X 9.53 - SA106 GR.B | M | 30 | 30 | 3154.8 | 3154.8
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SPARE PIPE DIA 457 X 9.53 - SA106 GR.B | M | 1 | 1 | 105.16 | 105.16
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SUPPORT PIPE OD323.9x9.53 SA335 P11 | M | 1.5 | 1.5 | 110.82 | 110.82
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SUPPORT PIPE OD406.4x12.7 SA106 GR.B | M | 3.5 | 3.5 | 431.55 | 431.55
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD457x9.53 SA234WPB | NO | 4 | 4 | 453.48 | 453.48
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD457x9.53 SA234WP22 | NO | 1 | 1 | 116.5 | 116.5
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW UEQT OD457x9.53/OD219.1x6.35 SA234WPB | NO | 9 | 9 | 913.68 | 913.68
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW UEQT OD457x9.53/OD273x9.27 SA234WPB | NO | 2 | 2 | 209.8 | 209.8
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW UEQT OD457x9.53/OD355.6x9.53 SA234WPB | NO | 2 | 2 | 220 | 220
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW RED OD457x9.53/OD219.1x8.18 SA234WP22 | NO | 1 | 1 | 30.787 | 30.787
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BRANCH PIPE OD114.3x13.49 SA106 GR.B | M | 2 | 2 | 67.08 | 67.08
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BRANCH PIPE OD168.3x10.97 SA106 GR.B | M | 2 | 2 | 85.12 | 85.12
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BRANCH PIPE OD88.9x11.13 SA106 GR.B | M | 2 | 2 | 30.54 | 30.54
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SPARE CONNN.PIPE DIA 114.3x6.02 SA106GRB | M | 2 | 2 | 32.14 | 32.14
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB15 CL:3000-SA105 | NO | 8 | 8 | 1.44 | 1.44
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 3 | 3 | 1.29 | 1.29
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | TEMP STUB RC 1" L=45 - CS SA105 | NO | 7 | 7 | 3.5 | 3.5
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | SCREW PLUG RC 1" CS SA105 | NO | 7 | 7 | 1.4 | 1.4
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW END CAP OD114.3x6.02 SA515GR70 | NO | 4 | 4 | 8.8 | 8.8
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | FLAT ENDCLOSURE OD219.1x6.35 SA515GR70 | NO | 2 | 2 | 17.86 | 17.86
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BW END CAP OD457x9.53 SA234WPB | NO | 1 | 1 | 77.77 | 77.77
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | CARRIER PLATE 20x50x120 SA515 GR70 | NO | 16 | 16 | 14.08 | 14.08
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-340 | PE-DG-508-142-M803/01 | BOTTOM PLATE 16THK 2000x1500 SA515 GR70 | NO | 1 | 1 | 376.8 | 376.8
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 114.3x8.56 SA106GRC | M | 45 | 45 | 1004.445 | 1004.445
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SPARE PIPE DIA 114.3x8.56 SA106GRC | M | 1 | 1 | 22.321 | 22.321
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SPARE PIPE DIA 219.1x6.35 SA106GRB | M | 1 | 1 | 33.31 | 33.31
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 219.1x12.7 SA106GRC | M | 1 | 1 | 64.641 | 64.641
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 219.1x6.35 SA106GRB | M | 30 | 30 | 999.3 | 999.3
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | PIPE DIA 114.3x6.02 SA106GRB | M | 0.5 | 0.5 | 8.035 | 8.035
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SUPP. PIPE OD88.9x7.62 SA106 GR.B | M | 3 | 3 | 45.81 | 45.81
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD114.3x8.56 SA234WPC | NO | 9 | 9 | 49.5 | 49.5
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW LR 90DEG ELBOW OD219.1x6.35 SA234WPB | NO | 8 | 8 | 133.6 | 133.6
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW EQT OD114.3x8.56 SA234WPC | NO | 1 | 1 | 7.7 | 7.7
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW EQT OD219.1x6.35 SA234WPC | NO | 1 | 1 | 19.27 | 19.27
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW UEQT OD219.1x6.35/OD114.3x6.02 SA234WPB | NO | 2 | 2 | 34.36 | 34.36
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW REDUCER OD219.1x12.7/114.3x8.56 SA234 WPC | NO | 2 | 2 | 18 | 18
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW REDUCER OD114.3x8.56/OD88.9x7.62 SA234 WPC | NO | 2 | 2 | 3.86 | 3.86
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BW END CAP OD114.3x6.02 SA234WPB | NO | 2 | 2 | 4.4 | 4.4
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | CARRIER PLATE 16x50x80 SA515 GR70 | NO | 4 | 4 | 1.92 | 1.92
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | BOTTOM PLATE 16THK 1000x1000 SA515 GR 70 | NO | 1 | 1 | 125 | 125
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB25 CL:6000-SA105 | NO | 12 | 12 | 6.84 | 6.84
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | ASME B16.11 SW STUB NB50 CL:6000-SA105 | NO | 5 | 5 | 9.8 | 9.8
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | TEMP STUB RC 1.5" OD78 L=64 - CS SA105 | NO | 5 | 5 | 7.5 | 7.5
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | SCREW PLUG RC 1.5" SA105 | NO | 5 | 5 | 2.5 | 2.5
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-324 | PE-DG-508-142-M803/01 | GI -SHEET FOR RAIN HOOD 0.63 THKx1000x2000 IS277 | NO | 1 | 1 | 9.892 | 9.892
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | PIPE OD711X10, SA672GRB70 | M | 27 | 27 | 4668.3 | 4668.3
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SPARE PIPE OD508x9.53 SA106 GRB | M | 2 | 2 | 234.3 | 234.3
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | PIPE OD508X9.53, SA106GRB | M | 84 | 84 | 9840.6 | 9840.6
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BRANCH PIPE OD219.1X16 , SA106GRB | M | 2 | 2 | 160.26 | 160.26
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW LR 90DEG ELL OD711X10 SA234WPB(W) | NO | 3 | 3 | 939 | 939
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW LR 45DEG ELL OD711X10 SA234WPB(W) | NO | 3 | 3 | 432.93 | 432.93
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 12 | 12 | 1682.76 | 1682.76
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW RED OD711X9.53/610X9.53 SA234WPB | NO | 1 | 1 | 93.9 | 93.9
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW RED OD711X10/508X9.53 SA234WPB | NO | 2 | 2 | 180.86 | 180.86
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | BW UNEQT OD711X10/610X9.53 SA234WPB | NO | 1 | 1 | 274.85 | 274.85
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | FLAT END CLOSURE OD219.1X8.18 SA515GR70 | NO | 2 | 2 | 17.26 | 17.26
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SW STUB NB25 CL6000 CS SA105 | NO | 8 | 8 | 4.56 | 4.56
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SW STUB NB25 CL3000 CS SA105 OD50 H=54 | NO | 5 | 5 | 2.15 | 2.15
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SW STUB NB15 CL3000 CS SA105 OD36 H=44 | NO | 14 | 14 | 2.52 | 2.52
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | TEMPERATURE STUB M33X2 (CS) SA105 ( D-78 , H-45) (ROD-80) | NO | 3 | 3 | 3.36 | 3.36
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SCREW PLUG M33X2 CS SA105 | NO | 3 | 3 | 1.2 | 1.2
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | PACKING RING IS1972 | NO | 3 | 3 | 0.03 | 0.03
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | TEMP.STUB L=45 SA105 ( HWR ) ROD-80 DIA | NO | 2 | 2 | 1.3 | 1.3
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | TEMP.STUB RC 1 "(CS) D55 , L=45 SA105 (ROD-D63) | NO | 8 | 8 | 5.6 | 5.6
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SCREW PLUG R 1 " (CS) SA105 (ROD-D40) | NO | 8 | 8 | 1.6 | 1.6
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | CARRIER PLATE 20X50X120 SA515GR70 | NO | 24 | 24 | 21.12 | 21.12
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD914X9.53 L=800 SA106GRB | M | 0.8 | 0.8 | 170 | 170
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD660X9.53 L=1000 SA106GRB | M | 1 | 1 | 152.876 | 152.876
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD457X9.53 L=1500 SA106GRB | M | 1.5 | 1.5 | 157.74 | 157.74
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | LUG PLATE 16X559X325 SA515GR70 | NO | 2 | 2 | 29.6 | 29.6
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PLATE 20X1500X2000 SA515GR70 | NO | 1 | 1 | 471 | 471
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | SUPPORT PLATE 10X2000X1000 SA515GR70 | NO | 2 | 2 | 157 | 157
1 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | IBR | 82-322 | PE-DG-508-150-M805/01p | THERMOWELL STUB SA105 OD-70, H-80 (ROD-80) | NO | 5 | 5 | 8.5 | 8.5
1 Total | [10 empty] | 59333.8518
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | PIPE OD2032x16 L=14980 SA672 GRB70 | M | 21 | 21 | 16704.03 | 16704.03
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | 90DEG MITRE BEND OD2032x16 R=1500 SA387GR12CL2(CERT) | NO | 6 | 6 | 12905.652 | 12905.652
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | 13.6DEG MITRE BEND OD2032x16 R=1500 SA387GR12CL2(CERT) | NO | 2 | 2 | 1863.592 | 1863.592
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | ASME B16.11 SW STUB NB15,CL:3000-SA105 OD36 H=44 | NO | 10 | 10 | 1.8 | 1.8
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | ASME B16.11 SW STUB NB50,CL:3000-SA105 OD80 H=60 | NO | 4 | 4 | 5.32 | 5.32
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | TEMP STUB RC 1" L=45-SA105 | NO | 8 | 8 | 4.9 | 4.9
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | SCREW PLUG RC 1" SA105 | NO | 8 | 8 | 1.4 | 1.4
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | BLIND FLANGE ASSY NB500 CL150 SA515GR70 | NO | 2 | 2 | 126 | 126
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | BRANCH PIPE OD508x12.7 L=500 SA106GRB | M | 1 | 1 | 155.1 | 155.1
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | SOW FLANGE NB500 CL150 SA515GR70 | NO | 2 | 2 | 108 | 108
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | BRANCH PIPE OD323.9x9.53 L=500 SA106GRB | M | 1 | 1 | 73.88 | 73.88
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | FLAT FACED FLANGE NB2000 SA515GR70 | NO | 4 | 4 | 546.656 | 546.656
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | NON ASBESTOS GASKET NB2000 PN10 NON-ASBESTOS | NO | 2 | 2 | 13.656 | 13.656
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | BOTTOM PLATE 20 THK 450X350-SA515GR70 | NO | 16 | 16 | 395.632 | 395.632
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | PAD PLATE 840x400x12 SA515GR70 | NO | 16 | 16 | 506.416 | 506.416
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | STIFFNER PLATE 607x427x16 SA515GR70 | NO | 32 | 32 | 1041.728 | 1041.728
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | STIFFNER PLATE 740x275x16 SA515GR70 | NO | 16 | 16 | 408.96 | 408.96
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | BOTTOM PLATE 25 THK 750X474-SA515GR70 | NO | 4 | 4 | 279.068 | 279.068
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | PAD PLATE 717x375x12 SA515GR70 | NO | 4 | 4 | 101.312 | 101.312
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | STUD M 30 X200 SA193B16 | NO | 44 | 44 | 37.4 | 37.4
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | HEX . NUT M30 SA194GR2H | NO | 88 | 88 | 20.328 | 20.328
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | STUD M 52 X5X340 SA193B7 | NO | 100 | 100 | 560 | 560
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-150-M811/01p | HEX . NUT M52x5 SA194GR2H | NO | 200 | 200 | 310 | 310
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | PIPE OD-323.9X9.53 SA106GRC | M | 54 | 54 | 3989.52 | 3989.52
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | BW LR 90DEG ELL OD323.9X9.53 SA234WPC | NO | 4 | 4 | 212.16 | 212.16
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | 45° BW LR ELBOW 323.9X9.53 SA234WPB | NO | 2 | 2 | 54 | 54
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | SUPPORT PIPE OD219.1X6.35 L=1000 SA106GRB | NO | 3 | 3 | 99.93 | 99.93
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | BOTTOM PLATE 10X1000X1000MM SA515GR70 | NO | 1 | 1 | 78.5 | 78.5
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | GAL WIRE MESH 1.2 X1200X2000 IS280 | NO | 1 | 1 | 6.24 | 6.24
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | SOW FLANGE NB 300 CL150 SA515GR70 | NO | 4 | 4 | 94.88 | 94.88
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | BOLT-M24X120 -4.6-IS1363P1 | NO | 26 | 26 | 13.676 | 13.676
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | NUT -M24 -CL4-IS1363 | NO | 26 | 26 | 2.86 | 2.86
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | NON-ASBESTOS JOINTING SHEET 3.0MMX500X500 | NO | 1 | 1 | 2.47 | 2.47
2 | Sipat 2x800 MW Unit 6 | Aux Steam Piping | Non IBR | 82-363 | PE-DG-508-149-M811/00 | SPARE PIPE OD-323.9X9.53X6000-SA106GRC | M | 2 | 2 | 147.76 | 147.76
2 Total | [10 empty] | 40872.826
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PIPE DIA 114.3 X 6.02 SA106GRB | M | 4 | 4 | 64.3 | 64.3
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PIPE DIA 323.9x9.53 SA106GRB | M | 17 | 17 | 1255.96 | 1255.96
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PIPE DIA 508 X 9.53 SA106GRB | M | 14 | 14 | 1640.0944 | 1640.0944
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PIPE DIA 660 X 10 SA672 B70 | M | 18 | 18 | 2865.15 | 2865.15
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PIPE DIA60.3x5.54 L=20000MM SA106 GRB | M | 20 | 20 | 149.62 | 149.62
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BW LR 49.2 DEG ELL OD660x9.53 SA234WPB | NO | 2 | 2 | 272.66 | 272.66
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BW LR 90DEG ELL OD323.9X9.53 SA234WPB | NO | 5 | 5 | 265.05 | 265.05
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BW UEQT OD660.4x9.53/323.9x9.53 SA234WPB | NO | 4 | 4 | 1052 | 1052
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BW UEQT OD660x9.53/508x9.53 SA234WPB | NO | 3 | 3 | 679.95 | 679.95
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BW C.RED 610x9.53/508x9.53 SA234WPB | NO | 3 | 3 | 198.6 | 198.6
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 9 | 9 | 3.87 | 3.87
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | ASME B16.11 SW STUB NB50,CL:3000 SA105 | NO | 5 | 5 | 6.65 | 6.65
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | ASME B16.11 SW STUB NB15,CL:3000 SA105 | NO | 9 | 9 | 1.62 | 1.62
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | TEMPERATURE STUB M33X2, L=64 SA105 | NO | 10 | 10 | 7 | 7
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | PACKING RING M33x2 IS1972 | NO | 10 | 10 | 10.1 | 10.1
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | SCREW PLUG M33 x 2 SA105 | NO | 10 | 10 | 8 | 8
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | FLAT END CLOSURE OD114.3x6.02 SA515 GR70( PLATE 120x120X8THK) | NO | 1 | 1 | 2.19 | 2.19
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | FLAT END CLOSURE OD660x10 SA515 GR70 (PLATE 660X660X10THK) | NO | 2 | 2 | 320 | 320
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | SOW FLANGE NB25 CL150 IS2062 | NO | 3 | 3 | 2.7 | 2.7
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | STUD M12X70 SA193GRB7 | NO | 20 | 20 | 1.2 | 1.2
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | HEX,NUT M12 SA194GR2H | NO | 40 | 40 | 0.8 | 0.8
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | SOW FLANGE NB50 CL150 IS2062 | NO | 3 | 3 | 6 | 6
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | STUD M16X100 SA193GRB7 | NO | 20 | 20 | 2.8 | 2.8
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | HEX,NUT M16 SA194GR2H | NO | 40 | 40 | 1.32 | 1.32
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | GASKET T=1.5MM 1000X1000 NON ASBESTOS | NO | 1 | 1 | 2.47 | 2.47
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BOTTOM SUPPORT PIPE OD406.4x9.53 L=5000 SA106 GRB | M | 5 | 5 | 466.35 | 466.35
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BOTTOM SUPPORT PIPE OD508x9.53 L=5000 SA106 GRB | M | 5 | 5 | 585.75 | 585.75
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | SUPPORT PIPE OD88.9x5.49 SA106 GRB | M | 1 | 1 | 11.29 | 11.29
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BOTTEM PLATE 10 THK 120x120 SA515 GR70 | NO | 2 | 2 | 2.26 | 2.26
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BOTTOM SUPPORT PIPE OD273X9.27 L=4000MM SA106 GRB | M | 4 | 4 | 241.5 | 241.5
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | BOTTOM SUPPORT PLATE 10x1500x3500 SA515 GR70 | NO | 1 | 1 | 412.125 | 412.125
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | TEMP STUB RC1 INCH SA105 | NO | 6 | 6 | 5.064 | 5.064
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-400 | PE-DG-508-153-M801 /01P | CARBON STEEL PLUG 1" SA105 | NO | 6 | 6 | 1.2 | 1.2
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | PIPE DIA 323.9 X 9.53 SA106GRC | M | 3 | 3 | 221.64 | 221.64
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | PIPE OD-323.9X9.53-SA106GRB | M | 40 | 40 | 2955.2 | 2955.2
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | PIPE DIA 273.0 X 9.27 SA106GRB | M | 7 | 7 | 422.17 | 422.17
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | BW LR 90DEG ELL OD323.9X9.53 SA234WPB | NO | 9 | 9 | 506.34 | 506.34
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | BW LR 90DEG ELL OD273X9.27 SA234WPB | NO | 3 | 3 | 116.43 | 116.43
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | BW UEQT 323.9X9.53/273X9.27 SA234WPB | NO | 2 | 2 | 108.92 | 108.92
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | BW RED 323.9X9.53/168.3X10.97 SA234WPC | NO | 2 | 2 | 24.14 | 24.14
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | SW STUB NB25 CL3000 CS OD34XH44 SA105 | NO | 6 | 6 | 2.58 | 2.58
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | SUPPORT PIPE OD273.0X9.27 L=2500 SA106GRB | M | 2.5 | 2.5 | 180.85 | 180.85
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-408 | PE-DG-508-153-M808/01p | BOTTOM SUPPORT PLATE 10x500x1000 SA515 GR70 | NO | 1 | 1 | 39.25 | 39.25
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 48.3X5.08 SA106GRB | M | 26 | 26 | 140.66 | 140.66
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 73.0X5.16 SA106GRB | M | 6 | 6 | 51.78 | 51.78
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | BW LR 90DEG ELL OD48.3X5.08 SA234WPB | NO | 9 | 9 | 5.58 | 5.58
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | BW LR 90DEG ELL OD73.0X5.16 SA234WPB | NO | 6 | 6 | 8.88 | 8.88
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | UNIONS 1/2"S.W.-1/2"NPT SA106GRB (OD21.3X3.73 L=200MM) | NO | 60 | 60 | 19.2 | 19.2
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | HEXAGONAL NIPPLES 1/2"NPT (M) -1/2"NPT (M) (OD21.3X3.73 L=200MM)SA106GRB | NO | 60 | 60 | 70.2 | 70.2
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 60.3X3.91 SA312TP304 | M | 120 | 120 | 651.6 | 651.6
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 60.3X5.54 SA106GRB | M | 230 | 230 | 1720.63 | 1720.63
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 33.4X4.55 SA106GRB | M | 175 | 175 | 567 | 567
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | PIPE OD 21.3X3.73 SA106GRB | M | 500 | 500 | 810 | 810
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ELBOW 90DEG OD60.3X3.91 SA312WP304 | NO | 20 | 20 | 15.4 | 15.4
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ELBOW 90DEG OD60.3X5.54 SA234WPB | NO | 42 | 42 | 44.52 | 44.52
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ELBOW 90DEG OD33.4X4.55 SA234WPB | NO | 23 | 23 | 5.75 | 5.75
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ELBOW 90DEG OD21.3X3.73 SA234WPB | NO | 60 | 60 | 4.8 | 4.8
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | REDUCER 60.3X5.54/33.4X4.55 SA234WPB | NO | 2 | 2 | 1.14 | 1.14
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | REDUCER 33.4X4.55/21.3X3.73 SA234WPB | NO | 30 | 30 | 5.1 | 5.1
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | UEQT 60.3X5.54/33.4X4.55 SA234WPB | NO | 10 | 10 | 14.2 | 14.2
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | EQT 60.3X5.54 SA234WPB | NO | 4 | 4 | 6.32 | 6.32
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | EQT 33.4X4.55 SA234WPB | NO | 26 | 26 | 11.18 | 11.18
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | UEQT 33.4X4.55/21.3x3.73 SA234WPB | NO | 40 | 40 | 15.2 | 15.2
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | EQT 33.4X3.73 SA234WPB | NO | 20 | 20 | 7.2 | 7.2
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | EQT 60.3X3.91 SA312WP304 | NO | 6 | 6 | 7.2 | 7.2
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ROUND DIA 63 L=70 SA105 (ORIFICE PLATE NB50) | NO | 1 | 1 | 0.665 | 0.665
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | ROUND DIA 40 L=60 SA105 (ORIFICE PLATE NB25) | NO | 1 | 1 | 0.25 | 0.25
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-407 | PE-DG-508-153-M815/01p | EQT 21.3X3.73 SA234WPB | NO | 15 | 15 | 3.45 | 3.45
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | PIPE OD 219.1 x 12.7 - SA106GRB | M | 52 | 52 | 3361.2797 | 3361.2797
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | PIPE DIA 33.4X4.55 SA106GRB | M | 7 | 7 | 22.519 | 22.519
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | BW LR 90DEG ELL OD219.1X12.7 SA234WPB | NO | 15 | 15 | 464.55 | 464.55
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | BW EQT OD219.1x12.7 SA234WPB | NO | 2 | 2 | 74.8 | 74.8
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | BW RED OD219.1x12.7/168.3x7.11 SA234WPB | NO | 2 | 2 | 17.456 | 17.456
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 3 | 3 | 1.29 | 1.29
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | LUG PLATE 16 THK 428X240 -SA515GR.70 | NO | 2 | 2 | 16.8 | 16.8
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | SUPPORT PIPE OD168.3x7.11 SA106 GRB | M | 4 | 4 | 113.048 | 113.048
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | BOTTOM PLATE 10 THK 1000x1000 SA515 GR70 | NO | 1 | 1 | 78.5 | 78.5
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M805 /01p | SPARE PIPE OD 219.1 x 12.7 - SA106GRB | M | 2 | 2 | 129.28 | 129.28
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | PIPE DIA 168.3 X 7.11 SA106GRB | M | 62 | 62 | 1752.1205 | 1752.1205
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 30 | 30 | 304.2 | 304.2
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | BW LR 45DEG ELL OD168.3X7.11 SA234WPB | NO | 4 | 4 | 20.32 | 20.32
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | SUPPORT PIPE OD114.3X6.02 SA106 GRB | M | 3.5 | 3.5 | 56.261 | 56.261
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | BOTTOM PLATE 10 THK 1000x1000 SA515 GR70 | NO | 1 | 1 | 78.5 | 78.5
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401 | PE-DG-508-153-M804 /01P | SPARE PIPE DIA 168.3 X 7.11 SA106GRB | M | 2 | 2 | 56.52 | 56.52
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 323.9 X 9.53 SA106GRB | M | 49 | 49 | 3620.12 | 3620.12
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 88.9 X 5.49 SA106GRB | M | 6 | 6 | 67.74 | 67.74
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 406.4 X 12.7 SA106GRB | M | 230 | 230 | 28359 | 28359
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 406.4 X 12.7 SA106GRC | M | 40 | 40 | 4932 | 4932
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 457.0 X 12.7 SA106GRC | M | 110 | 110 | 15306.17 | 15306.17
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 114.3 X 6.02 SA106GRB | M | 5 | 5 | 80.35 | 80.35
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 323.9 X 12.7 SA106GRB | M | 18 | 18 | 1754.28 | 1754.28
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PIPE DIA 273 X 9.27 SA106GRB | M | 30 | 30 | 1808.64 | 1808.64
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD273x9.27 SA234WPB | NO | 7 | 7 | 259 | 259
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD88.9x5.49 SA234WPB | NO | 6 | 6 | 12.18 | 12.18
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD114.3x6.02 SA234WPB | NO | 1 | 1 | 3.84 | 3.84
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD323.9x9.53 SA234WPB | NO | 12 | 12 | 648 | 648
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD323.9x9.53 SA234WPC | NO | 5 | 5 | 270 | 270
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 45DEG ELL OD323.9x9.53 SA234WPB | NO | 2 | 2 | 54 | 54
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD406.4x12.7 SA234WPB | NO | 53 | 53 | 5857.56 | 5857.56
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 60DEG ELL OD406.4x12.7 SA234WPB | NO | 1 | 1 | 73.68 | 73.68
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 45DEG ELL OD406.4x12.7 SA234WPB | NO | 9 | 9 | 497.34 | 497.34
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW SR 90DEG ELL OD406.4x12.7 SA234WPB | NO | 1 | 1 | 110.52 | 110.52
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD406.4x12.7 SA234WPC | NO | 6 | 6 | 663.12 | 663.12
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 90DEG ELL OD457.2x12.7 SA234WPC | NO | 24 | 24 | 3395.76 | 3395.76
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 45DEG ELL OD457.2x12.7 SA234WPC | NO | 3 | 3 | 212.22 | 212.22
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW LR 60DEG ELL OD457.2x12.7 SA234WPC | NO | 1 | 1 | 94.33 | 94.33
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW SR 90DEG ELL OD457.2x12.7 SA234WPC | NO | 2 | 2 | 282.38 | 282.38
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW SR 90DEG ELL OD508x9.53 SA234WPB | NO | 1 | 1 | 93.48 | 93.48
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD406.4x12.7/OD273x9.27 SA234WPB | NO | 1 | 1 | 37.06 | 37.06
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD850 NB/OD406.4x12.7 SA234WPB | NO | 2 | 2 | 250.04 | 250.04
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD406.4X12.7/OD323.9x9.53 SA234WPB | NO | 1 | 1 | 39.53 | 39.53
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD508x12.7/OD406.4X12.7 SA234WPB | NO | 4 | 4 | 284.04 | 284.04
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD508x14.27/OD457x12.7 SA234WPC | NO | 4 | 4 | 334.96 | 334.96
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD457x12.7/OD406.4X12.7 SA234WPC | NO | 2 | 2 | 100.14 | 100.14
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD457x12.7/OD323.9x9.53 SA234WPC | NO | 6 | 6 | 274.32 | 274.32
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW REDUCER - OD323.9x9.53/OD273x9.27 SA234WPB | NO | 2 | 2 | 27.76 | 27.76
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW EQT OD406.4x12.7 SA234WPB | NO | 7 | 7 | 837.34 | 837.34
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW EQT OD457x12.7 SA234WPC | NO | 4 | 4 | 607.48 | 607.48
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT 323.9X9.53/168.3x7.11 SA234WPB | NO | 3 | 3 | 154.17 | 154.17
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT 406.4x12.7/323.9X9.53SA234WPB | NO | 5 | 5 | 538.15 | 538.15
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT 406.4x12.7/219.1X12.7 SA234WPB | NO | 3 | 3 | 300.87 | 300.87
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT- OD457x12.7/OD406.4X12.7 SA234WPC | NO | 3 | 3 | 428.88 | 428.88
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT- OD457x12.7/OD323.9x9.53 SA234WPC | NO | 1 | 1 | 132.67 | 132.67
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BW UEQT- OD457x12.7/OD219.1x12.7 SA234WPC | NO | 1 | 1 | 125.66 | 125.66
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | ASME16.5 FLNAGE NB450 CL150 SA105 | NO | 8 | 8 | 1312 | 1312
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | ASME B16.11 SW STUBNB15 CL6000 SA105 | NO | 10 | 10 | 1.8 | 1.8
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | ASME B16.11 SW STUBNB25 CL6000 SA105 | NO | 76 | 76 | 43.32 | 43.32
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | ASME B16.11 SW STUBNB40 CL6000 SA105 | NO | 5 | 5 | 3.75 | 3.75
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | ASME B16.11 SW STUBNB50 CL6000 SA105 | NO | 5 | 5 | 6.65 | 6.65
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | TEMPERATURE STUB M33X2, L=64 (CS) SA105 | NO | 26 | 26 | 18.2 | 18.2
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PACKING RING M33x2 SA105 | NO | 26 | 26 | 0.26 | 0.26
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | COPPER PACKING RING M33X2 IS1972 | NO | 26 | 26 | 20.8 | 20.8
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | FLAT END CLOSURE OD114.3x6.02 SA515GR.70 | NO | 1 | 1 | 2.19 | 2.19
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BRANCH PIPE OD88.9x15.24 SA106GRB | M | 1.6 | 1.6 | 44.288 | 44.288
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | BRANCH PIPE OD114.3x15.24 SA106GRB | M | 2 | 2 | 74.44 | 74.44
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | CARRIER PLATE16X50X100 SA515 GR.70 | NO | 24 | 24 | 15.072 | 15.072
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | CARRIER PLATE12X50X80 SA515 GR.70 | NO | 12 | 12 | 4.521 | 4.521
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SUPPORT PIPE OD323.9x9.53 SA106GRB | M | 12 | 12 | 1097.6457 | 1097.6457
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PLATE 10 THK 2000X2000 SA515GR70 | NO | 1 | 1 | 314 | 314
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | PLATE 12 THK 2000x2000 SA515 GR70 | NO | 2 | 2 | 30.144 | 30.144
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SUPPORT PIPE OD219.1X12.7 SA106GRB | M | 2.5 | 2.5 | 161.6 | 161.6
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SUPPORT PIPE OD168.3X7.11 SA106GRB | M | 4 | 4 | 113.048 | 113.048
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | LUG PLATE 16 THK 559X325 -SA515GR.70 | NO | 2 | 2 | 29.6 | 29.6
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | LUG PLATE 16 THK 600X360 -SA515GR.70 | NO | 1 | 1 | 17.6 | 17.6
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 323.9 X 9.53 SA106GRB | M | 2 | 2 | 147.76 | 147.76
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 406.4 X 12.7 SA106GRB | M | 6 | 6 | 739.8 | 739.8
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 406.4 X 12.7 SA106GRC | M | 2 | 2 | 246.6 | 246.6
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 457.0 X 12.7 SA106GRC | M | 3 | 3 | 417.441 | 417.441
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 323.9 X 12.7 SA106GRB | M | 1 | 1 | 97.46 | 97.46
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SPARE PIPE DIA 273 X 9.27 SA106GRB | M | 5.1 | 5.1 | 307.4688 | 307.4688
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | TEMPERATURE STUB Rc1.5" SA105 OD98 L=H=45 | NO | 50 | 50 | 88.5 | 88.5
3 | Sipat 2x800 MW Unit 6 | Condensate Piping | Non IBR | 82-401,82-402,82-403 | PE-DG-508-153-M802/01P | SCREW PLUG Rc1.5" SA105 | NO | 50 | 50 | 25 | 25
3 Total | [10 empty] | 104168.2511
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | PIPE OD 813 x 10 - SA672 B70 | M | 18 | 18 | 3564 | 3564
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | PIPE OD 610 x 10 - SA672 B70 | M | 11 | 11 | 1628 | 1628
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | PIPE OD 323.9 x 9.53 - SA106GRC | M | 13 | 13 | 960.44 | 960.44
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SUPPORT PIPE OD559x9.53 L=700SA106GRB | M | 0.7 | 0.7 | 90.391 | 90.391
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SUPPORT PIPE OD273x12.7 L=700SA106GRC | M | 0.7 | 0.7 | 57.064 | 57.064
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | BW LR 90DEG ELL OD323.9X9.53 SA234WPC | NO | 5 | 5 | 281.3 | 281.3
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | BW LR 90DEG ELL OD610X10 SA234WPB | NO | 4 | 4 | 850.2 | 850.2
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | BW LR 30DEG ELL OD610X10 SA234WPB | NO | 1 | 1 | 70.85 | 70.85
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | BW MITRE BEND R0.75D 90DEG OD813x10 SA672 B70 | NO | 4 | 4 | 758.24 | 758.24
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 4 | 4 | 1.72 | 1.72
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | LUG PLATE 16 THK 520x632 -SA515 GR70 | NO | 3 | 3 | 123.84 | 123.84
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SUPPORT PLATE 12x600x600-SA515GR70 | NO | 1 | 1 | 33.91 | 33.91
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SUPPORT PLATE 10X300X300-SA515GR70 | NO | 1 | 1 | 7.07 | 7.07
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SPARE PIPE OD 813 x 10 - SA672 B70 | M | 1 | 1 | 198 | 198
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SPARE PIPE OD 610 x 10 - SA672 B70 | M | 1 | 1 | 148 | 148
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SPARE PIPE OD 323.9 x 9.53 - SA106GRC | M | 1 | 1 | 73.88 | 73.88
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-493,82-494, 82-495 | PE-DG-508-147-M811/01p | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 4 | 0.72 | 0.72
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | PIPE DIA 323.9 X 9.53 SA335P22 | M | 6 | 6 | 443.28 | 443.28
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | PIPE DIA 219.1 X 12.7 SA335P22 | M | 4 | 4 | 258.56 | 258.56
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | PIPE OD-219.1X12.7X6000-SA106GRC | M | 8 | 8 | 517.12 | 517.12
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | PIPE DIA 168.3 X 7.11 SA106GRB | M | 2.5 | 2.5 | 70.65 | 70.65
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | BW LR 30DEG ELL 219.1X12.7 SA234WP22CL1 | NO | 1 | 1 | 11.13 | 11.13
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | BW LR 60DEG ELL OD219.1X12.7 SA234WPC | NO | 2 | 2 | 44.52 | 44.52
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | BW EQT OD323.9X9.53 SA335WP22CL1 | NO | 2 | 2 | 120.84 | 120.84
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB25 SA105 CL:3000 | NO | 10 | 10 | 4.3 | 4.3
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB50 SA105 CL:3000 | NO | 14 | 14 | 18.62 | 18.62
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB50 SA182F22 CL:3000 | NO | 14 | 14 | 18.62 | 18.62
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB50 SA182F22 CL:9000 | NO | 8 | 8 | 10.64 | 10.64
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB25 SA182F22 CL:3000 | NO | 1 | 1 | 0.43 | 0.43
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | ASME B16.11 SW STUB NB40 SA182F22 CL:3000 | NO | 1 | 1 | 1.07 | 1.07
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD219.1X12.7-(PLATE OD219.1X48THK) SA515GR70 | NO | 3 | 3 | 43.2 | 43.2
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD168.3X7.11 (PLATE OD168.3X33THK) SA515GR70 | NO | 1 | 1 | 6.64 | 6.64
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD219.1X12.7 (PLATE OD219.1X48THK) SA387GR22CL2 | NO | 1 | 1 | 14.4 | 14.4
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD323.9X9.53-(PLATE OD324X48THK) SA387GR22CL2 | NO | 3 | 3 | 117 | 117
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD33.4X4.55 (PLATE OD33.4X20THK) SA387GR22CL2 | NO | 1 | 1 | 0.138 | 0.138
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD60.3X5.54 (PLATE OD60.3X20THK) SA515GR70 | NO | 2 | 2 | 22 | 22
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD60.3X5.54 - (PLATE OD60.3X20THK) SA387GR22CL2 | NO | 1 | 1 | 11 | 11
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | FLAT END CLOSURE OD33.4X4.55 (PLATE OD33.4X20THK) SA515GR70 | NO | 2 | 2 | 0.276 | 0.276
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | SUPPORT PIPE OD168.3X10.97 L= 350 SA335P11 | NO | 1 | 1 | 14.9 | 14.9
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | SUPPORT PIPE OD168.3X10.97 L= 1050- SA106GRB | NO | 1 | 1 | 44.69 | 44.69
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | SUPPORT PIPE OD114.3X6.02 L= 400 SA106GRB | NO | 1 | 1 | 6.43 | 6.43
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | SUPPORT PIPE OD273X6.35 L= 1050 SA335P11 | NO | 1 | 1 | 43.84 | 43.84
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | BOTTOM PLATE 12 THK,1500X1500 - SA515GR70 | NO | 1 | 1 | 211.95 | 211.95
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-457 | PE-DG-508-147-M814/01p | BOTTOM PLATE 12 THK, 1000X1000 - SA387GR11CL2 | NO | 1 | 1 | 94.2 | 94.2
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | PIPE OD 219.1 x 6.35 - SA106GRB | M | 4 | 4 | 133.24 | 133.24
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | SPARE PIPE OD 219.1 x 6.35 - SA106GRB | M | 1 | 1 | 33.31 | 33.31
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | PIPE OD 406.4x9.53 - SA106GRB | M | 24 | 24 | 2238.48 | 2238.48
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | SUPPORT PIPE OD168.3x7.11 L=2000 SA106GRB | M | 2 | 2 | 56.524 | 56.524
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | BW LR 90DEG ELL OD219.1X6.35 SA234WPB | NO | 4 | 4 | 66.8 | 66.8
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | BW LR 60DEG ELL OD219.1X6.35 SA234WPB | NO | 1 | 1 | 16.7 | 16.7
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | BW LR 45DEG ELL OD406.4x9.53 SA234WPB | NO | 3 | 3 | 133.98 | 133.98
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 4 | 4 | 1.72 | 1.72
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | CARRIER PLATE 16X120X50-SA515GR70 | NO | 4 | 4 | 3.52 | 3.52
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | SUPPORT PLATE 10X200X200-SA515GR70 | NO | 4 | 4 | 12.56 | 12.56
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-459 | PE-DG-508-147-M813/00 | SUPPORT PIPE OD323.9X9.53 L=1500 SA106GRB | M | 1.5 | 1.5 | 110.82 | 110.82
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | PIPE DIA 273.0 X 6.35 SA106GRB | M | 12 | 12 | 501.24 | 501.24
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | ASMEB16.9 BWLR 45DEG ELBOW OD355.6X9.53 SA234GRB | NO | 5 | 5 | 170.15 | 170.15
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | ASMEB16.9 BWLR 90DEG ELBOW OD273X6.35 SA234GRB | NO | 5 | 5 | 131 | 131
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | MACHINED REDUCER NB25/15 SA234WPB | NO | 5 | 5 | 20 | 20
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | SOW FLANGE NB 250 CL150 BMC16 SA515GR70 | NO | 5 | 5 | 72.5 | 72.5
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | STUD M 24 X 3 X 230 SA193B7 | NO | 70 | 70 | 49 | 49
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | NUT -M24 -GR7 | NO | 140 | 140 | 15.4 | 15.4
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | NON-ASBESTOS JOINTING SH 3.0MM 1000X1000 | NO | 1 | 1 | 6 | 6
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | GALVANISED WIRE MESH 1.2THKX1200X2000 IS280 | NO | 5 | 5 | 31.2 | 31.2
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | SUPPORT PIPE OD219.8X8.18 L=9000 SA106GRB | M | 9 | 9 | 382.86 | 382.86
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | SUPPORT PLATE 12THKX1200X800 SA515GR70 | NO | 1 | 1 | 90.432 | 90.432
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | DRIP PAN ASSY NB 250 (CS)-3.15THK,600DIA SA515GR70 | NO | 5 | 5 | 69.9 | 69.9
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | DRIP PAN ASSY NB 250 (CS)-3.15THK,100X1700 SA515GR70 | NO | 5 | 5 | 21 | 21
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-373 | PE-DG-508-142-M812/00 | COVER PLATE FOR DRIP PAN - 10THK,600DIA SA515GR70 | NO | 5 | 5 | 110.5 | 110.5
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | PIPE DIA 168.3 X 7.11 SA106GRB | M | 2 | 2 | 56.524 | 56.524
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 4 | 4 | 41.6 | 41.6
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | 45DEG BW LR ELBOW 168.3X7.11 SA234WPB | NO | 1 | 1 | 5.08 | 5.08
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 1 | 1 | 0.43 | 0.43
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 10 | 32.371 | 32.371
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | 90DEG BW LR ELBOW 33.4X4.55 SA234WPB | NO | 3 | 3 | 0.6 | 0.6
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | ORIFICE PLATE ASSY PIPE OD 168.3X7.11 SA106GRB L=300 | M | 0.3 | 0.3 | 8.4786 | 8.4786
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | ORIFICE PLATE ASSY For Pipe NB150- SA515GR70 | NO | 1 | 1 | 2.22 | 2.22
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | LUG PLATE THICK12x340x170 SA515 GR70 | NO | 1 | 1 | 3.7 | 3.7
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M802/01p | SPARE PIPE DIA 168.3 X 7.11 SA106GRB | M | 0.5 | 0.5 | 14.131 | 14.131
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | PIPE DIA 168.3 X 7.11 SA106GRB | M | 2 | 2 | 56.5238 | 56.5238
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 4 | 4 | 41.6 | 41.6
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | 45 DEG BW LR ELBOW 168.3X7.11 SA234WPB | NO | 1 | 1 | 5.08 | 5.08
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 1 | 1 | 0.43 | 0.43
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 10 | 32.371 | 32.371
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | 90DEG BW LR ELBOW 33.4X4.55 SA234WPB | NO | 3 | 3 | 0.6 | 0.6
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | ORIFICE PLATE ASSY PIPE OD 168.3X7.11 SA106GRB L=300 | M | 0.3 | 0.3 | 8.4786 | 8.4786
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | ORIFICE PLATE ASSY For Pipe NB150- SA515GR70 | NO | 1 | 1 | 2.22 | 2.22
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | LUG PLATE THICK12x340x170 SA515 GR70 | NO | 1 | 1 | 3.7 | 3.7
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M803/01p | SPARE PIPE DIA 168.3 X 7.11 SA106GRB | M | 0.5 | 0.5 | 14.131 | 14.131
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | PIPE DIA 114.3 X 6.02 SA106GRB | M | 42 | 42 | 675.1292 | 675.1292
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 9 | 9 | 34.56 | 34.56
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | BW LR 45DEG ELL OD114.3X6.02 SA234WPB | NO | 2 | 2 | 3.84 | 3.84
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 3 | 3 | 1.29 | 1.29
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 10 | 32.371 | 32.371
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | 90DEG BW LR ELBOW 33.4X4.55 SA234WPB | NO | 3 | 3 | 0.6 | 0.6
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | ORIFICE PLATE ASSY PIPE OD 114.3X6.02 SA106GRB L=300 | NO | 1 | 1 | 4.83 | 4.83
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | 0ORIFICE PLATE ASSY for Pipe NB100- SA515GR70 | NO | 1 | 1 | 1.026 | 1.026
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | SUPPORT PIPE OD88.9X7.62 L=254MM SA106GRB | NO | 2 | 2 | 7.76 | 7.76
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M804/00 | SPARE PIPE DIA 114.3 X 6.02 SA106GRB | M | 2 | 2 | 32.149 | 32.149
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | PIPE DIA 114.3 X 6.02 SA106GRB | M | 47 | 47 | 755.5025 | 755.5025
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 9 | 9 | 34.56 | 34.56
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | BW LR 45DEG ELL OD114.3X6.02 SA234WPB | NO | 2 | 2 | 3.84 | 3.84
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 2 | 2 | 0.86 | 0.86
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 10 | 32.371 | 32.371
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | 90DEG BW LR ELBOW 33.4X4.55 SA234WPB | NO | 3 | 3 | 0.6 | 0.6
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | ORIFICE PLATE ASSY PIPE OD 114.3X6.02 SA106GRB L=300 | NO | 1 | 1 | 4.83 | 4.83
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | 0ORIFICE PLATE ASSY for Pipe NB100- SA515GR70 | NO | 1 | 1 | 0.026 | 0.026
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | SUPPORT PIPE OD88.9X7.62 L=254MM SA106GRB | NO | 2 | 2 | 7.76 | 7.76
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M805/00 | SPARE PIPE DIA 114.3 X 6.02 SA106GRB | M | 2 | 2 | 32.149 | 32.149
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | PIPE DIA 114.3 X 6.02 SA106GRB | M | 35.589 | 35.589 | 572.076 | 572.076
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 9 | 9 | 34.56 | 34.56
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | BW LR 45DEG ELL OD114.3X6.02 SA234WPB | NO | 1 | 1 | 1.92 | 1.92
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 2 | 2 | 0.86 | 0.86
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 10 | 32.371 | 32.371
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | 90DEG BW LR ELBOW 33.4X4.55 SA234WPB | NO | 3 | 3 | 0.6 | 0.6
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | ORIFICE PLATE ASSY PIPE OD 114.3X6.02 SA106GRB L=300 | NO | 1 | 1 | 4.83 | 4.83
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | 0ORIFICE PLATE ASSY for Pipe NB100- SA515GR70 | NO | 1 | 1 | 1.026 | 1.026
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | SUPPORT PIPE OD88.9X7.62 L=254MM SA106GRB | NO | 1 | 1 | 3.879 | 3.879
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | SUPPORT PLATE THICK10X100X100MM SA515 GR70 | NO | 1 | 1 | 0.785 | 0.785
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-382 | PE-DG-508-149-M806/00 | SPARE PIPE DIA 114.3 X 6.02 SA106GRB | M | 2 | 2 | 32.149 | 32.149
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | PIPE DIA 355.6 X 9.53 SA106GRB | M | 40 | 40 | 3253.1937 | 3253.1937
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | PIPE OD 60.3x5.54 SA106GRB | M | 4 | 4 | 29.924 | 29.924
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | BW LR 90DEG ELL OD355.6X9.53 SA234WPB | NO | 4 | 4 | 272.4 | 272.4
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | BW LR 45DEG ELL OD355.6X9.53 SA234WPB | NO | 1 | 1 | 34.03 | 34.03
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | BW ELL 90 DEG OD 60.3x5.54 SA106GRB | NO | 5 | 5 | 4.5 | 4.5
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | BW UEQT 355.6X9.53/219.1x8.18 SA234WPB | NO | 1 | 1 | 65.93 | 65.93
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | BW REDUCER - OD355.6x9.53/OD323.9x9.53 SA234WPB | NO | 1 | 1 | 25.6184 | 25.6184
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | ASME B16.11 SW STUB NB25,CL:3000-SA105 | NO | 1 | 1 | 35.8206 | 35.8206
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | ASME B16.11 SW STUB NB50,CL:3000-SA105 | NO | 1 | 1 | 0.12807 | 0.12807
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | SUPPORT PIPE OD273X6.35 L=0.8 SA106GRB | M | 0.8 | 0.8 | 28.6565 | 28.6565
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | SUPPORT PLATE THICK 10X300X300MM SA515GR70 | NO | 4 | 4 | 0.51227 | 0.51227
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | GAL WIRE MWSH 1.2x1200x2000 IS2062 FE410 | NO | 1 | 1 | 6.7519 | 6.7519
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M815/00 | SPARE PIPE DIA 355.6 X 9.53 SA106GRB | M | 2 | 2 | 25.794 | 25.794
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | PIPE DIA 355.6 X 9.53 SA106GRB | M | 32 | 32 | 40.7077 | 40.7077
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | PIPE DIA 273.0 X 6.35 SA106GRB | M | 3.5 | 3.5 | 11.7316 | 11.7316
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | BW LR 45DEG ELL OD355.6X9.53 SA234WPB | NO | 5 | 5 | 6.3606 | 6.3606
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | BW SR 90DEG ELL OD273X6.35 SA234WPB | NO | 5 | 5 | 124.88 | 124.88
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | BW RED 457.2X9.53/355.6X9.53 SA234WPB | NO | 5 | 5 | 179.1032 | 179.1032
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | DRIP PAN ASSY NB 250 (CS)-3.15THK,600DIA SA515GR70 | NO | 5 | 5 | 0.64033 | 0.64033
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | DRIP PAN ASSY NB 250 (CS)-3.15THK,100X1700 SA515GR70 | NO | 5 | 5 | 179.1032 | 179.1032
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | COVER PLATE FOR DRIP PAN - 10THK,600DIA SA515GR70 | NO | 5 | 5 | 0.64033 | 0.64033
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | SW RED NB25/15 CL3000 SA105 | NO | 5 | 5 | 0.65 | 0.65
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | NON-ASBESTOS JOINTING SHEET 3MM 1500X1500 | NO | 1 | 1 | 12.897 | 12.897
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | SOW FLANGE NB250 CL.150 SA105 | NO | 5 | 5 | 6.3606 | 6.3606
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | HEX.BOLT M24X120 IS1364 | NO | 75 | 75 | 251.391 | 251.391
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | HEX.NUT M24 IS1364 | NO | 75 | 75 | 95.4088 | 95.4088
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | GAL WIRE MESH 1.2X1200X2000 IS280 | NO | 5 | 5 | 31.2 | 31.2
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | SUPPORT PIPE OD219.1X6.35 SA106GRB | M | 5 | 5 | 166.575 | 166.575
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | BOTTOM PLATE 10X250X250 SA515GR70 | NO | 20 | 20 | 98.2 | 98.2
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-419 | PE-DG-508-149-M809/01p | SPARE PIPE DIA 355.6 X 9.53 SA106GRB | M | 2 | 2 | 162.66 | 162.66
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | PIPE OD 355.6x9.53 - SA106GRB | M | 50 | 50 | 4065 | 4065
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | PIPE OD 273x6.35 - SA106GRB | M | 3 | 3 | 125.28 | 125.28
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | PIPE OD 168.3x7.11 - SA106GRB | M | 2 | 2 | 56.524 | 56.524
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | BW 90 DEG SR ELBOW 273X6.35 SA234WPB | NO | 2 | 2 | 49.952 | 49.952
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | BW 45 DEG LR ELBOW 355.6X9.53 SA234WPB | NO | 6 | 6 | 204.18 | 204.18
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | BW RED 457.2x9.53/355.6X9.53 SA234WPB | NO | 2 | 2 | 71.64 | 71.64
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | SW RED NB25/NB15 CL3000 SA234WPB | NO | 2 | 2 | 0.26 | 0.26
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | SUPPORT PIPE OD219.1x6.35 SA106GRB | M | 6 | 6 | 199.89 | 199.89
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | BOTTOM PLATE 10 THK 250X250-SA515GR70 | NO | 18 | 18 | 88.38 | 88.38
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | FLANGE 250NB CL150 SA515GR70 | NO | 2 | 2 | 30 | 30
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | DRIP PAN ASSY NB 250 (CS)-3.15THK,600DIA SA515GR70 | NO | 2 | 2 | 27.96 | 27.96
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | DRIP PAN ASSY NB 250 (CS)-3.15THK,100X1700 SA515GR70 | NO | 2 | 2 | 8.4 | 8.4
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | COVER PLATE FOR DRIP PAN - 10THK,600DIA SA515GR70 | NO | 2 | 2 | 0.44 | 0.44
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | HEX.BOLT M24x120 IS1364 | NO | 25 | 25 | 13.5 | 13.5
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | HEX.NUT M24 IS1364 | NO | 25 | 25 | 2.5 | 2.5
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | GALVANISED WIRE MESH 1.2 THKx1200x1200 IS280 | NO | 2 | 2 | 12 | 12
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | NON ASBESTOS JOINTING SHEET 3mm x1000x1000 | NO | 1 | 1 | 5.1 | 5.1
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | SPARE PIPE DIA 355.6 X 9.53 SA106GRB | M | 2 | 2 | 162.66 | 162.66
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | SOW FLANGE NB150 CL600 SA515GR70 | NO | 2 | 2 | 14.3 | 14.3
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | FT STUD M27X180 | NO | 2 | 2 | 1.54 | 1.54
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-375 | PE-DG-508-149-M810/01p | NUT -M27 -2H | NO | 2 | 2 | 0.34 | 0.34
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | PIPE DIA 219.1x6.35 SA106GRB | M | 45 | 45 | 1499.175 | 1499.175
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | PIPE DIA 273x6.35 SA106GRB | M | 43 | 43 | 1796.1047 | 1796.1047
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | PIPE DIA 323.9x9.53 SA106GRB | M | 34 | 34 | 2511.92 | 2511.92
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW LR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 33 | 33 | 526.086 | 526.086
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW LR 90DEG ELL OD273x6.35 SA234WPB | NO | 9 | 9 | 224.784 | 224.784
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW LR 90DEG ELL OD323.9x9.53 SA234WPB | NO | 5 | 5 | 265.2 | 265.2
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW EQT OD219.1x6.35 SA234WPB | NO | 4 | 4 | 77.08 | 77.08
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW UEQT OD323.9x9.53/OD219.1x6.35 SA234WPB | NO | 4 | 4 | 216.8 | 216.8
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW C.RED OD273x6.35/OD219.1x6.35 SA234WPB | NO | 8 | 8 | 54 | 54
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | BW C.RED OD323.9x9.53/OD219.1x6.35 SA234WPB | NO | 4 | 4 | 51.6 | 51.6
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | TEMPERATURE STUB M33X2, L=64 SA105 | NO | 6 | 6 | 2.1 | 2.1
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | PACKING RING M33x2 IS1972 SA105 | NO | 6 | 6 | 0.3 | 0.3
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SCREW PLUG M33 x 2 SA105 SA105 | NO | 6 | 6 | 2.4 | 2.4
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | PRESSURE STUB NB25 CLASS 3000 SA105 | NO | 6 | 6 | 1.2 | 1.2
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | FLAT END CLOSURE OD273x6.35 SA515 GR70 | NO | 4 | 4 | 69.84 | 69.84
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | CARRIER PLATE 16THK 80x50 SA515GR70 | NO | 20 | 20 | 10.04 | 10.04
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SUPPORT PIPE DIA 168.3 X 7.11 SA106GRB | M | 4 | 4 | 113.0471 | 113.0471
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SUPPORT PLATE TH10X200X200 SA515GR70 | NO | 10 | 10 | 6.28 | 6.28
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SPARE PIPE DIA 219.1x6.35 SA106GRB | M | 3 | 3 | 99.945 | 99.945
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SPARE PIPE DIA 273x6.35 SA106GRB | M | 2 | 2 | 83.539 | 83.539
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-388 | PE-DG-508-149-M801/01p | SPARE PIPE DIA 323.9x9.53 SA106GRB | M | 2 | 2 | 147.76 | 147.76
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | PIPE DIA 114.3 X 6.02 SA106GRB | M | 12 | 12 | 192.8304 | 192.8304
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | PIPE OD 60.3X 5.54 SA106GRB | M | 15 | 15 | 112.1999 | 112.1999
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 2 | 2 | 7.68 | 7.68
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | BW LR 45DEG ELL OD114.3X6.02 SA234WPB | NO | 1 | 1 | 1.92 | 1.92
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 SA234WPB | NO | 10 | 10 | 9 | 9
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | ASMEB16.9 BWLR 45DEG ELBOW OD60.3X5.54 SA234WPB | NO | 1 | 1 | 0.45 | 0.45
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | BW RED 114.3X6.02/60.3X5.54 SA234WPB | NO | 2 | 2 | 2.54 | 2.54
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | BW UEQT 114.3X6.02/60.3X5.54 SA234WPB | NO | 5 | 5 | 29.58 | 29.58
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | BW EQL TEE 60.3X5.54 SA234WPB | NO | 2 | 2 | 4.4 | 4.4
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | ORIFICE PLATE ASSY 200X200X10 SA515GR70 | NO | 5 | 5 | 15.7 | 15.7
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | SUPPORT PIPE OD48.3X5.08 SA106GRB | M | 2 | 2 | 11.492 | 11.492
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | SUPPORT PIPE OD88.9X7.62 SA106GRB | M | 3 | 3 | 45.8192 | 45.8192
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | PLATE 10THK 2000X1000 - SA515GR70 | NO | 1 | 1 | 157 | 157
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | CARRIER PLATE TH16X80X50 SA515GR70 | NO | 8 | 8 | 4 | 4
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | GAL WIRE MESH 1.2 X1200X1200 IS280 | NO | 1 | 1 | 6.24 | 6.24
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | SPARE PIPE DIA 114.3 X 6.02 SA106GRB | M | 1 | 1 | 16.069 | 16.069
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M814/00 | SPARE PIPE OD 60.3X 5.54 SA106GRB | M | 1 | 1 | 7.479 | 7.479
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | PIPE DIA 168.3 X 7.11 SA106GRB | M | 38 | 38 | 1073.8802 | 1073.8802
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | PIPE OD 60.3X 5.54 SA106GRB | M | 48 | 48 | 359.0404 | 359.0404
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 5 | 5 | 52 | 52
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | BW 45 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 2 | 2 | 10.16 | 10.16
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | ASMEB16.9 BWLR 90DEG ELBOW OD60.3X5.54 SA234WPB | NO | 19 | 19 | 17.1 | 17.1
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | ASMEB16.9 BWLR 45DEG ELBOW OD60.3X5.54 SA234WPB | NO | 2 | 2 | 0.9 | 0.9
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | BW RED 168.3X7.11/114.3X6.02 SA234WPB | NO | 2 | 2 | 6.7 | 6.7
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | BW RED 114.3X6.02/60.3X5.54 SA234WPB | NO | 2 | 2 | 2.54 | 2.54
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | SUPPORT PIPE OD114. 3X6.02 SA106GRB | M | 5 | 5 | 80.35 | 80.35
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | SUPPORT PIPE OD48.3X5.08 SA106GRB | M | 4 | 4 | 21.656 | 21.656
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | PLATE 10THK 750X750 - SA515GR70 | NO | 1 | 1 | 44.156 | 44.156
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | CARRIER PLATE 16X80X50 SA515GR70 | NO | 16 | 16 | 8.032 | 8.032
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | GAL WIRE MESH 1.2 X1200X2000 IS280 | NO | 1 | 1 | 6.2 | 6.2
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | SPARE PIPE DIA 168.3 X 7.11 SA106GRB | M | 2.5 | 2.5 | 70.65 | 70.65
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-385 | PE-DG-508-149-M813/00 | SPARE PIPE OD 60.3X 5.54 SA106GRB | M | 3 | 3 | 22.44 | 22.44
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 508.00 X 9.53 - SA106GRB | M | 45 | 45 | 5271.525 | 5271.525
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 168.3 X 7.11 SA106GRB | M | 80 | 80 | 2260.8 | 2260.8
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 114.3 X 6.02 SA106GRB | M | 105 | 105 | 1687.875 | 1687.875
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 323.9 X 9.53 SA106GRB | M | 32 | 32 | 2364.16 | 2364.16
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BW LR 45DEG ELL OD508X9.53 SA234WPB | NO | 3 | 3 | 210.21 | 210.21
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | 90° BW LR ELBOW 323.9X9.53 SA234WPB | NO | 9 | 9 | 486 | 486
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BW LR 45DEG ELL 323.9X9.53SA234WPB | NO | 2 | 2 | 53 | 53
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 34 | 34 | 353.6 | 353.6
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BW 45 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 4 | 4 | 20.8 | 20.8
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 SA234WPB | NO | 30 | 30 | 115.2 | 115.2
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | ASMEB16.9 BWLR 45DEG ELBOW OD114.3X6.02 SA234WPB | NO | 2 | 2 | 3.84 | 3.84
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BWCONRED508X15.09/323.9X10.31 SA234WPB | NO | 2 | 2 | 153.88 | 153.88
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SW STUB-CS-NB 25 CLASS 3000 CS SA105 | NO | 12 | 12 | 5.16 | 5.16
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | TEMPERATURE STUB M33X2 L=45 SA105 | NO | 4 | 4 | 2 | 2
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SCREW PLUG M33 X 2 SA105 | NO | 4 | 4 | 3.2 | 3.2
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PACKING RING IS1972 | NO | 4 | 4 | 0.4 | 0.4
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SUPPORT PIPE OD219.1x6.35 SA106GRB | M | 3 | 3 | 99.945 | 99.945
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SUPPORT PLATE 10 THK 250X250-SA515GR70 | NO | 8 | 8 | 39.2 | 39.2
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE OD 355.6x9.53 - SA106GRB | M | 4 | 4 | 325.32 | 325.32
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SUPPORT PLATE 10 THK 400X400-SA515GR70 | NO | 8 | 8 | 100.48 | 100.48
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | CARRIER PLATE 25X50X100 CS SA515GR70 | NO | 12 | 12 | 9.42 | 9.42
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | CARRIER PLATE 16X50X80 CS SA515GR70 | NO | 12 | 12 | 6.03 | 6.03
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | GI SHEET FOR RAIN HOOD 2.5X1200X2500 IS1079D | NO | 4 | 4 | 235.5 | 235.5
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | GAL WIRE MESH 1.2 X1200X2000 IS280 | NO | 2 | 2 | 12.48 | 12.48
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | ASBESTOS JOINTING SHEET 1.5MM | NO | 2 | 2 | 4.94 | 4.94
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SOW FLANGE NB 100 CL150 SA515GR70 | NO | 5 | 5 | 27.3 | 27.3
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SOW FLANGE NB150 CL150 SA515GR70 | NO | 6 | 6 | 42.9 | 42.9
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | FLAT END CLOSURE FOR OD114.3X6.02 SA234WPB | NO | 2 | 2 | 4.38 | 4.38
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | BOLT-M16X90 -8.8-IS1364P1 | NO | 48 | 48 | 5.1 | 5.1
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | NUT -M16 -CL8-IS1364P3 | NO | 48 | 48 | 0.9 | 0.9
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | HEX HD BOLT M20X100,P.CL6.8 IS:1364(P-1) | NO | 48 | 48 | 20.262 | 20.262
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | NUT -M20 -CL6-IS1364P3 | NO | 48 | 48 | 4.29 | 4.29
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SPARE PIPE DIA 508.00 X 9.53 - SA106GRB | M | 2 | 2 | 234.29 | 234.29
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SPARE PIPE DIA 168.3 X 7.11 SA106GRB | M | 3 | 3 | 84.78 | 84.78
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SPARE PIPE DIA 114.3 X 6.02 SA106GRB | M | 3 | 3 | 48.21 | 48.21
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | SPARE PIPE DIA 323.9 X 9.53 SA106GRB | M | 2 | 2 | 147.76 | 147.76
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 168.3 X 10.97 SA106GRB | M | 2 | 2 | 67.072 | 67.072
4 | Sipat 2x800 MW Unit 6 | Drain & Vents Piping | Non IBR | 82-379 | PE-DG-508-149-M807/01p | PIPE DIA 114.3 X 13.49 SA106GRB | M | 2 | 2 | 67.072 | 67.072
4 Total | [10 empty] | 53188.5843
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | OD PIPE DIA 508.00 X 9.53 - SA106GRB | M | 85 | 85 | 9957.75 | 9957.75
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 8 | 8 | 1121.84 | 1121.84
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | BW LR 45DEG ELL OD508X9.53 SA234WPB | NO | 1 | 1 | 70.07 | 70.07
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | BW RED 610X10/508X9.53 SA234WPB | NO | 1 | 1 | 67.81 | 67.81
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | BRANCH PIPE OD 219.1 x 12.70 - SA106GRC L=1000 | M | 1 | 1 | 64.64 | 64.64
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SW STUB NB25 CL3000 CS SA105 | NO | 4 | 4 | 1.72 | 1.72
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SW STUB NB15 CL3000 CS SA105 | NO | 10 | 10 | 4.3 | 4.3
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | THERMOWELL STUB D65 H157 CS SA105 | NO | 2 | 2 | 7.2 | 7.2
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SW STUB 50NB SA105 OD80 L=80 | NO | 4 | 4 | 5.32 | 5.32
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | CARRIAR PLATE 20X55X120 SA515GR70 | NO | 4 | 4 | 4.12 | 4.12
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SUPPORT PIPE OD219.1X8.18 L=5M SA515GR70 | M | 5 | 5 | 212.7 | 212.7
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SUPPORT PLATE 12X2000X1000 SA515GR70 | NO | 1 | 1 | 188.4 | 188.4
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | LUG PLATE 16X628X390 SA515GR70 | NO | 1 | 1 | 19.5 | 19.5
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SPARE PIPE OD508.00 X 9.53 - SA106GRB | M | 2 | 2 | 234.3 | 234.3
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | TEMP STUB RC 1" L=45-SA105 | NO | 4 | 4 | 2.45 | 2.45
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-334 | PE-DG-508-150-M806/01p | SCREW PLUG RC 1" SA105 | NO | 4 | 4 | 0.7 | 0.7
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | PIPE DIA 660.0 X 10.0 SA672GRB70CL22 | M | 34 | 34 | 5450.2 | 5450.2
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | OD PIPE DIA 508.00 X 9.53 - SA106GRB | M | 27 | 27 | 3163.046 | 3163.046
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW LR 90DEG ELL OD660.4X9.53 SA234WPB(W) | NO | 2 | 2 | 476.24 | 476.24
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW LR 30DEG ELL OD660.4X9.53 SA234WPB(W) | NO | 2 | 2 | 158.56 | 158.56
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW LR 53.8 DEG ELL OD660.4X9.53 SA234WPB(W) | NO | 1 | 1 | 142.205 | 142.205
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW LR 90DEG ELL OD508X9.53 SA234WPB | NO | 3 | 3 | 420.69 | 420.69
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW LR 45DEG ELL OD508X9.53 SA234WPB | NO | 2 | 2 | 140.14 | 140.14
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW RED 610X10/508X9.53 SA234WPB(W) | NO | 2 | 2 | 135.62 | 135.62
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW RED 660X10/508X9.53 SA234WPB(W) | NO | 1 | 1 | 83.59 | 83.59
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW RED 660X10/610X10 SA234WPB(W) | NO | 2 | 2 | 188 | 188
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BW UEQT 660X10/508X9.53 SA234WPB(W) | NO | 1 | 1 | 229 | 229
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | BRANCH PIPE OD 219.1 X12.7 L=2.5 SA106GRB | M | 2.5 | 2.5 | 161.6 | 161.6
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SUPPORT PIPE OD 219.1 X12.7 L=1.5 SA106GRB | M | 1.5 | 1.5 | 96.96 | 96.96
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | FLAT END CLOSURE OD219.1X6.35 SA515GR70 | NO | 3 | 3 | 19.8 | 19.8
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | TEMP.STUB M33X2 (CS)L=64 SA105 | NO | 1 | 1 | 0.7 | 0.7
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SCREW PLUG CS (M33X2) SA105 | NO | 1 | 1 | 0.4 | 0.4
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | COPPER PACKING RING M33X2 IS1972 | NO | 1 | 1 | 0.1 | 0.1
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | TEMP STUB HWR SA105 OD80 L=45 | NO | 1 | 1 | 0.65 | 0.65
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SW STUB NB25 CL3000 CS SA105 OD50 H=54 | NO | 4 | 4 | 1.72 | 1.72
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SW STUB 50NB SA105 OD80 L=75 | NO | 4 | 4 | 5.32 | 5.32
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SW STUB 15NB SA105 OD36 L=44 | NO | 8 | 8 | 1.44 | 1.44
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | TEMP STUB RC 1" L=45-SA105 | NO | 4 | 4 | 2.45 | 2.45
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-332 | PE-DG-508-150-M807/01p | SCREW PLUG RC 1" SA105 | NO | 4 | 4 | 0.7 | 0.7
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | PIPE DIA 813.0 X 10.0 SA672GRB70CL22 | M | 24 | 24 | 4752 | 4752
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | PIPE DIA 660.0 X 10.0 SA672GRB70CL22 | M | 15 | 15 | 2404.5 | 2404.5
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 90DEG ELL OD813X10 SA234WPB(W) | NO | 1 | 1 | 379.19 | 379.19
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 30DEG ELL OD813X10 SA234WPB(W) | NO | 3 | 3 | 378 | 378
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 53.9 DEG ELL OD813X10 SA234WPB(W) | NO | 1 | 1 | 226 | 226
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 60DEG ELL OD813X10 SA234WPB(W) | NO | 2 | 2 | 504 | 504
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW SR 90DEG ELL OD813X10 SA234WPB(W) | NO | 1 | 1 | 252 | 252
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 90DEG ELL OD660X10 SA234WPB | NO | 2 | 2 | 498.78 | 498.78
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW LR 45DEG ELL OD660X10 SA234WPC(W) | NO | 5 | 5 | 623.45 | 623.45
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW C RED 813X9.53/660.4X9.53 SA234WPB(W) | NO | 1 | 1 | 105 | 105
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW RED 660X9.53/610X9.53 SA234WPB(W) | NO | 2 | 2 | 179.5 | 179.5
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW RED 914X10/813X10 SA234WPB(W) | NO | 1 | 1 | 129.16 | 129.16
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BW UEQT 813X9.53 /660.4X9.53 SA234WPB (W) | NO | 1 | 1 | 357 | 357
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BRANCH PIPE OD 323.9X 9.53 L=2.4 SA106GRB | M | 2.4 | 2.4 | 170.6667 | 170.6667
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | TEMP.STUB M33X2 (CS)L=64 SA105 | NO | 2 | 2 | 1.4 | 1.4
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SCREW PLUG CS (M33X2) SA105 | NO | 2 | 2 | 0.8 | 0.8
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | COPPER PACKING RING M33X2 IS1972 | NO | 2 | 2 | 0.2 | 0.2
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | TEMP STUB HWR SA105 OD80 L=45 | NO | 2 | 2 | 1.3 | 1.3
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SW STUB NB25 CL3000 CS SA105 OD50 H=54 | NO | 4 | 4 | 1.72 | 1.72
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SW STUB 50NB SA105 OD80 L=75 | NO | 4 | 4 | 5.32 | 5.32
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SW STUB 15NB SA105 OD36 L=44 | NO | 8 | 8 | 1.44 | 1.44
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SUPPORT PIPE OD508X9.53 L=800 SA106GRB | M | 0.8 | 0.8 | 93.716 | 93.716
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | TEMP STUB RC 1" L=45-SA105 | NO | 5 | 5 | 3.0625 | 3.0625
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | SCREW PLUG RC 1" SA105 | NO | 5 | 5 | 0.875 | 0.875
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | BRANCH PIPE OD 219.1 X12.7 L=2.5 SA106GRB | M | 2.5 | 2.5 | 161.6 | 161.6
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-331 | PE-DG-508-150-M808/01p | FLAT END CLOSURE for Pipe OD323.9X9.53 SA515GR70 | NO | 3 | 3 | 44.628 | 44.628
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | PIPE DIA 610.0 X 10.0 SA672GRB70CL22 | M | 45 | 45 | 6660 | 6660
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | PIPE DIA 406.4 X 9.53 SA106GRB | M | 85 | 85 | 7927.95 | 7927.95
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | PIPE OD-323.9X9.53-SA106GRC | M | 16 | 16 | 1182.08 | 1182.08
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | OD PIPE DIA 273.00 X 12.70-SA106GRC | M | 73 | 73 | 5950.96 | 5950.96
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | OD PIPE DIA 273.00 X 9.27 - SA106GRB | M | 25 | 25 | 1507 | 1507
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | PIPE 273.00 X 6.35 - SA106GRB | M | 69 | 69 | 2881.095 | 2881.095
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW LR 90DEG ELL 406.4X9.53SA234WPB | NO | 20 | 20 | 1787.4 | 1787.4
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW LR 45DEG ELL OD406.4X9.53 SA234WPB | NO | 5 | 5 | 223.3 | 223.3
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW LR 90DEG ELL OD323.9X9.53 SA234WPC | NO | 4 | 4 | 212.16 | 212.16
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW 90DEG SR ELBOW OD323.9X9.53 SA234WPC | NO | 2 | 2 | 74 | 74
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW LR 90DEG ELL OD273X12.7 SA234WPC | NO | 15 | 15 | 731.85 | 731.85
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW LR 45DEG ELL OD273X12.7 SA234WPC | NO | 3 | 3 | 73.14 | 73.14
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW 90DEG LR EL OD273.1 X 9.27 SA234WPB | NO | 7 | 7 | 267.54 | 267.54
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW LR 90DEG ELL OD273X6.35 SA234WPB | NO | 6 | 6 | 157.2 | 157.2
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW LR 45DEG ELL OD273X6.35 SA234WPB | NO | 4 | 4 | 52.4 | 52.4
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW RED 610X9.53/559X9.53 SA234WPB | NO | 2 | 2 | 137.52 | 137.52
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | 16.9BW REDUCER OD610X9.53/406.4X9.53 SA234WPB | NO | 2 | 2 | 86 | 86
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW RED 323.9X9.53/273X6.35 SA234WPB | NO | 2 | 2 | 23.44 | 23.44
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW RED 406.4X9.53/323.9X9.53 SA234WPB | NO | 2 | 2 | 60.24 | 60.24
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW RED 406.4X9.53/273X6.35 SA234WPB | NO | 3 | 3 | 71.73 | 71.73
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW UNEQT 610 X 10/ 406.4 X 9.53 SA106GRB | NO | 1 | 1 | 263 | 263
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW UEQT 406.4X9.53/273X9.27 SA234WPB | NO | 4 | 4 | 376.16 | 376.16
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW UEQT 273X12.7/219.1X6.35 SA234WPC | NO | 4 | 4 | 204.08 | 204.08
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BW EQT OD406.4X9.53 SA234WPB | NO | 2 | 2 | 180.98 | 180.98
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW EQT OD273X12.7 SA234WPC | NO | 2 | 2 | 113.66 | 113.66
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BW UEQT 323.9X9.53/168.3X10.97 SA234WPC | no | 2 | 2 | 108.92 | 108.92
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | TEMP STUB RC 1";L=45 OD55 SA105 | NO | 6 | 6 | 6.618 | 6.618
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SCREW PLUG R 1" SA105 | NO | 6 | 6 | 2.07 | 2.07
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | TEMP STUB M33X2 L=45 CS SA105 | NO | 4 | 4 | 7.108 | 7.108
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SCREW PLUG M33X2 CS SA105 | NO | 4 | 4 | 2.772 | 2.772
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | COPPER PACKING RING M33X2 IS1972 | NO | 4 | 4 | 0.04 | 0.04
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SW STUB NB25 CL3000 SA105 | NO | 20 | 20 | 13.96 | 13.96
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | THERMOWELL STUB OD70H80 CS SA105 | NO | 2 | 2 | 3.4 | 3.4
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | CARRIER PLATE 20X50X120 CS SA515GR70 | NO | 36 | 36 | 36 | 36
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | BRANCH PIPE OD 219.1 X12.7 L=400 SA106GRC | M | 2 | 2 | 129.28 | 129.28
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | BRANCH PIPE DIA 114.30 X 11.13 - SA106GRB | M | 2 | 2 | 56.58 | 56.58
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD114.3X6.02 L=10500 SA106GRB | M | 10.5 | 10.5 | 168.782 | 168.782
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD168.3X7.11 L=1M SA106GRB | M | 1 | 1 | 28.2633 | 28.2633
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD219.1X8.18 L=5300 SA106GRB | M | 5.3 | 5.3 | 225.497 | 225.497
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | LUG PLATE 16X443X260 SA515GR70 | NO | 1 | 1 | 9.4 | 9.4
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | PLATE 20THKX4000X4000 SA515GR70 | NO | 1 | 1 | 2512 | 2512
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-329 | PE-DG-508-150-M812/01p | SW STUB 15NB SA105 OD36 L=44 | NO | 15 | 15 | 2.7 | 2.7
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | TEMP STUB RC 1";L=45 OD55 SA105 | NO | 6 | 6 | 6.618 | 6.618
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SCREW PLUG R 1" SA105 | NO | 6 | 6 | 2.07 | 2.07
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | TEMP STUB M33X2 L=45 CS SA105 | NO | 4 | 4 | 7.108 | 7.108
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SCREW PLUG M33X2 CS SA105 | NO | 4 | 4 | 2.772 | 2.772
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | COPPER PACKING RING M33X2 IS1972 | NO | 4 | 4 | 0.04 | 0.04
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SW STUB NB25 CL3000 SA105 | NO | 20 | 20 | 13.96 | 13.96
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | THERMOWELL STUB OD70H80 CS SA105 | NO | 2 | 2 | 3.4 | 3.4
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | CARRIER PLATE 20X50X120 CS SA515GR70 | NO | 36 | 36 | 36 | 36
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD114.3X6.02 L=10500 SA106GRB | M | 10.5 | 10.5 | 168.782 | 168.782
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD168.3X7.11 L=1M SA106GRB | M | 1 | 1 | 28.2633 | 28.2633
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SUPPORT PIPE OD219.1X8.18 L=5300 SA106GRB | M | 5.3 | 5.3 | 225.497 | 225.497
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | LUG PLATE 16X443X260 SA515GR70 | NO | 1 | 1 | 9.4 | 9.4
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | PLATE 20THKX4000X4000 SA515GR70 | NO | 1 | 1 | 2512 | 2512
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-323 | PE-DG-508-150-M812/01p | SW STUB 15NB SA105 OD36 L=44 | NO | 15 | 15 | 2.7 | 2.7
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | PIPE OD965x38 SA672GRB70CL22 | M | 2.5 | 2.5 | 2171.675 | 2171.675
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | PIPE OD965x10 SA672GRB70CL22 | M | 10 | 10 | 2355 | 2355
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SPARE PIPE OD406.4x21.44 SA106 GR.C | M | 1 | 1 | 203.545 | 203.545
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | PIPE OD406.4X21.44, SA106GRC | M | 31 | 31 | 6309.895 | 6309.895
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | PIPE OD323.9X9.53, SA106GRB | M | 1.5 | 1.5 | 110.82 | 110.82
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BRANCH PIPE OD323.9X12.7, SA106GRB | M | 1 | 1 | 97.46 | 97.46
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BRANCH PIPE OD114.3X13.49, SA106GRC | M | 1 | 1 | 33.54 | 33.54
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BW LR 90DEG ELL OD965X10 SA234WPB(W) | NO | 3 | 3 | 1607.07 | 1607.07
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BW 90DEG LR ELBOW OD406.4x21.44 SA234WPC | NO | 7 | 7 | 1364.44 | 1364.44
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BW RED 965x38/711x10 SA234WPB | NO | 1 | 1 | 466.722 | 466.722
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BW UNEQT OD965X10/508X9.53 SA234WPB | NO | 1 | 1 | 476.81 | 476.81
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | BW EQT OD965X10 SA234WPB | NO | 1 | 1 | 529.79 | 529.79
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | FLAT END CLOSURE for Pipe OD323.9X9.53 SA515GR70 | NO | 1 | 1 | 31.617 | 31.617
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | FLAT END CLOSURE for Pipe OD219.1X8.18 SA515GR70 | NO | 1 | 1 | 8.63 | 8.63
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | FLAT END CLOSURE for Pipe OD114.3X6.02 SA515GR70 | NO | 1 | 1 | 2.77 | 2.77
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD273X9.53 L=1500 SA106GRB | M | 1.5 | 1.5 | 92.883 | 92.883
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SUPPORT PIPE OD323X9.53 L=2500 SA106GRB | M | 2.5 | 2.5 | 184.7 | 184.7
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SW STUB NB25 CL6000 CS SA105 | NO | 8 | 8 | 4.56 | 4.56
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SW STUB NB25 CL3000 CS SA105 OD50 H=54 | NO | 5 | 5 | 2.15 | 2.15
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SW STUB NB15 CL3000 CS SA105 OD36 H=44 | NO | 14 | 14 | 2.52 | 2.52
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | TEMPERATURE STUB M33X2 (CS) SA105 ( D-78 , H-45) (ROD-80) | NO | 3 | 3 | 3.36 | 3.36
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SCREW PLUG M33X2 CS SA105 | NO | 3 | 3 | 1.2 | 1.2
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | PACKING RING IS1972 | NO | 3 | 3 | 0.03 | 0.03
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | TEMP.STUB L=45 SA105 ( HWR ) ROD-80 DIA | NO | 2 | 2 | 1.3 | 1.3
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | TEMP.STUB RC 1 "(CS) D55 , L=45 SA105 (ROD-D63) | NO | 8 | 8 | 5.6 | 5.6
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SCREW PLUG R 1 " (CS) SA105 (ROD-D40) | NO | 8 | 8 | 1.6 | 1.6
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | CARRIER PLATE 20X50X120 SA515GR70 | NO | 24 | 24 | 21.12 | 21.12
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | LUG PLATE 16X559X325 SA515GR70 | NO | 2 | 2 | 29.6 | 29.6
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SUPPORT PLATE 20X1500X2000 SA515GR70 | NO | 1 | 1 | 471 | 471
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | SUPPORT PLATE 10X2000X1000 SA515GR70 | NO | 2 | 2 | 157 | 157
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-335 | PE-DG-508-150-M805/01p | THERMOWELL STUB SA105 OD-70, H-80 (ROD-80) | NO | 5 | 5 | 8.5 | 8.5
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | PIPE OD323.9X21.44 SA335P22 | M | 28 | 28 | 4477.844 | 4477.844
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | PIPE OD273.00 X 18.26 - SA335P22 | M | 44 | 44 | 5047.416 | 5047.416
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SPARE PIPE OD273.00 X 18.26 - SA335P22 | M | 1.5 | 1.5 | 172.071 | 172.071
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | PIPE OD219.1X15.09 - SA335P22 | M | 19 | 19 | 1442.499 | 1442.499
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | PIPE OD114.30 X 8.56 - SA335P22 | M | 1.5 | 1.5 | 33.483 | 33.483
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW 90DEG LR ELBOW OD323.9X21.44 SA234WP22 | NO | 4 | 4 | 458.96 | 458.96
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW 90DEG LR ELBOW OD273X18.26 SA234WP22 | NO | 12 | 12 | 823.32 | 823.32
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW LR 45DEG ELL 273 X 18.26 SA234WP22 | NO | 2 | 2 | 68.62 | 68.62
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW 90DEG LR ELBOW OD219.1X15.09 SA234WP22CL1 | NO | 3 | 3 | 109.05 | 109.05
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW LR 45DEG ELL 168.3X18.26 SA234WP22CL1 | NO | 2 | 2 | 25 | 25
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW C RED OD323.9x21.44 / 273x18.26 SA234WP22CL1 | NO | 3 | 3 | 89.82 | 89.82
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW C RED OD323.9x21.44 / 219.1X15.09 SA234WP22CL1 | NO | 1 | 1 | 27.69 | 27.69
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW C RED OD219.1X15.09 / 168.3X18.26 SA234WP22CL1 | NO | 2 | 2 | 23.88 | 23.88
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW C RED OD273.1X16/219.1X15.09,SA234WP22CL1 | NO | 2 | 2 | 36.9 | 36.9
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW UNEQT OD323.9X21.44/219.1X15.09 SA234WP22CL1 | NO | 1 | 1 | 117.66 | 117.66
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | BW UNEQT OD323.9X21.44/273X18.26 SA234WP22CL1 | NO | 1 | 1 | 123 | 123
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | STUB OD114.3X13.49 SA182 F22 CL3 L=250 | NO | 2 | 2 | 25.74 | 25.74
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | FLAT END CLOSURE OD114.3X8.56 SA387 GR22 (OD 115X30THK) | NO | 2 | 2 | 4.84 | 4.84
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SW STUB NB40 CL6000 SA182F22CL3 OD70 H=60 | NO | 2 | 2 | 3.4 | 3.4
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SW STUB NB50 CL6000 SA182F22CL3 OD84 H=60 | NO | 4 | 4 | 7.84 | 7.84
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SW STUB NB25 CL6000 SA182F22CL3 OD060 H=60 | NO | 16 | 16 | 9.12 | 9.12
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | THERMOWELL STUB D120 H-80 SA182F22CL3 | NO | 5 | 5 | 26 | 26
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | TEMPERATURE STUB RC-1.5'' OD124 L-45 SA182F22CL3 | NO | 14 | 14 | 39.62 | 39.62
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SCREW PLUG RC 1.5 '' SA182 F22 | NO | 14 | 14 | 7 | 7
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | CARRIER PLATE 20X55X120 SA387GR22CL2 | NO | 12 | 12 | 12.432 | 12.432
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SUPPORT PIPE OD114.3X13.49 L=1000 SA335P22 (2 - NO ) | M | 1 | 1 | 33.54 | 33.54
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SUPPORT PIPE OD168.3X18.26 L=1000 SA335P22 ( 2 - NO ) | M | 1 | 1 | 42.56 | 42.56
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | TEMPERATURE STUB M33X2 (AS) SA182F22 ( D-78 , H-45) (ROD-80) | NO | 2 | 2 | 2.24 | 2.24
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | SCREW PLUG M33X2 SA182F22 | NO | 2 | 2 | 0.8 | 0.8
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-338 | PE-DG-508-150-M801/01p | PACKING RING IS1972 | NO | 2 | 2 | 0.02 | 0.02
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | PIPE OD406.4X21.44 SA106GRC | M | 42 | 42 | 8548.89 | 8548.89
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SPARE PIPE OD406.4X21.44 SA106GRC | M | 1 | 1 | 203.545 | 203.545
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | PIPE 323.90 X 14.27 - SA106GRC | M | 18 | 18 | 1961.1 | 1961.1
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | BW 90DEG LR ELBOW OD406.4X21.44 SA234 WPC | NO | 13 | 13 | 2533.96 | 2533.96
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | BW 90DEG LR EL OD323.9X14.27 SA234WPC | NO | 11 | 11 | 859.98 | 859.98
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | BW RED 323.9X14.27/273X12.7 SA234WPC | NO | 2 | 2 | 40.88 | 40.88
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | BW UEQT OD406.4X21.44/OD323.9X14.27 SA234WPC | NO | 2 | 2 | 370.62 | 370.62
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SUPPORT PIPE OD323.9X9.53 L=1000 SA106GRC | M | 1 | 1 | 73.88 | 73.88
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SUPPORT PIPE OD168.3X10.97 L=1000 SA106GRC | M | 1 | 1 | 42.56 | 42.56
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | TEMP.STUB RC 1-1/2"(CS) D98 L=45 SA105 (ROD-100) | NO | 10 | 10 | 17 | 17
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SCREW PLUG R 1-1/2"(CS) SA105 ( ROD-50) | NO | 10 | 10 | 5 | 5
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | TEMP.STUB- CS D78 L-45 M33X2 SA105 (ROD-80) | NO | 2 | 2 | 2.24 | 2.24
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SCREW PLUG CS (M33X2) SA105 (ROD-50) | NO | 2 | 2 | 0.8 | 0.8
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | COPPER PACKING RING M33X2 IS1972 | NO | 2 | 2 | 0.02 | 0.02
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SW STUB CS NB25 CL:6000 SA105 | NO | 10 | 10 | 5.7 | 5.7
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | THERMOWELL STUB WELDED D114 H95 CS SA105 (ROD-125mm) | NO | 4 | 4 | 19 | 19
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | CARRIER PLATE 20THKX50X120 SA515GR70 | NO | 4 | 4 | 3.52 | 3.52
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-337 | PE-DG-508-150-M802/01p | SUPPORT PLATE 10THKX1000X1000 SA515GR70 | NO | 1 | 1 | 78.5 | 78.5
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | PIPE OD 406.4X12.7 -SA335P22 | M | 47 | 47 | 5781 | 5781
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | SPARE PIPE OD 406.4X12.7 -SA335P22 | M | 1 | 1 | 123 | 123
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | PIPE DIA 273.0 X 9.27 SA335P22 | M | 9 | 9 | 542.79 | 542.79
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | PIPE OD 355.6X12.7 -SA335P22 | M | 1 | 1 | 53.698 | 53.698
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | BW 90DEG LR ELBOW OD 406.4X12.7 -SA234 WP22 | NO | 9 | 9 | 1080 | 1080
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | BW LR 90DEG ELL OD273X9.27 SA234WP22CL1 | NO | 5 | 5 | 180.4 | 180.4
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | RED OD457X12.7/406.4X12.7 SA234 WP22 | NO | 1 | 1 | 50.065 | 50.065
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | RED OD406.4X12.7/355.6X12.7 SA234 WP22 | NO | 2 | 2 | 82.266 | 82.266
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | C RED OD406.4X12.7/OD273X12.7 SA234WP22CL1 | NO | 1 | 1 | 37.06 | 37.06
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | BW UEQT 406.4X12.7/273X9.27 SA234WP22CL1 | NO | 1 | 1 | 109 | 109
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | BW UEQT 406.4X12.7/168.3x7.11 SA234WP22CL1 | NO | 2 | 2 | 209.72 | 209.72
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | BRANCH PIPE OD168.3X10.97 L=1500 SA335P22 | M | 1.5 | 1.5 | 63.75 | 63.75
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | SUPPORT PIPE OD168.3X10.97 L=300 SA335P22 | M | 0.3 | 0.3 | 12.75 | 12.75
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | TEMPERATURE STUB RC 1-1/2'' OD125 L45 SA182F22CL3 | NO | 12 | 12 | 33.96 | 33.96
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | SCREW PLUG RC1-1/2'' SA182F22CL3 | NO | 12 | 12 | 6 | 6
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | TEMPERATURE STUB HWR OD50 : L=45 SA182F22CL3 | NO | 2 | 2 | 0.74 | 0.74
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | SW STUB NB25 CL6000 F22 SA182F22CL3 | NO | 14 | 14 | 7.98 | 7.98
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | THERMOWELL STUB(TW) OD78 H=64 SA182F22CL3 | NO | 5 | 5 | 9 | 9
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | SW STUB NB50 CL3000 F22 SA182F22CL3 | NO | 2 | 2 | 2.66 | 2.66
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | CARRIER PLATE 20X55X120 SA387GR22CL2 | NO | 4 | 4 | 4.144 | 4.144
5 | Sipat 2x800 MW Unit 6 | Extraction Piping | IBR | 82-336 | PE-DG-508-150-M803/01p | FLAT END CAP OD168.3X7.11 SA387 Gr22 OD169X32 | NO | 2 | 2 | 11.26 | 11.26
5 Total | [10 empty] | 124871.8549
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | PIPE DIA 323.9 X 9.53 SA106GRB | M | 4 | 4 | 295.52 | 295.52
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | PIPE DIA 219.1 X 6.35 X 6500 - SA106GRB | M | 50 | 50 | 1665.5 | 1665.5
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | PIPE DIA 168.3 X 7.11 SA106GRB | M | 77 | 77 | 2176.02 | 2176.02
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | PIPE DIA 114.3 X 6.02 SA106GRB | M | 27 | 27 | 433.89 | 433.89
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW LR 90DEG ELL OD219.1X6.35 SA234WPB | NO | 12 | 12 | 206.52 | 206.52
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW LR 60DEG ELL OD219.1X6.35 SA234WPB | NO | 1 | 1 | 12.09 | 12.09
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 16 | 16 | 179.68 | 179.68
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW 45°LR ELBOW 168.3X7.11 SA234WPB | NO | 2 | 2 | 11.22 | 11.22
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 7 | 7 | 26.88 | 26.88
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW LR 30DEG ELL OD114.3X6.02 SA234WPB | NO | 2 | 2 | 2.56 | 2.56
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW RED 323.9X9.53/168.3X7.11 SA234WPB | NO | 1 | 1 | 11.26 | 11.26
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW RED 219.1X6.35/168.3X7.11 SA234WPB | NO | 1 | 1 | 4.84 | 4.84
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW RED 168.3X7.11/114.3X6.02 SA234WPB | NO | 1 | 1 | 3.16 | 3.16
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW EQT OD168.3X7.11 SA234WPB | NO | 1 | 1 | 13.28 | 13.28
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BW UEQT 323.9X6.35/114.3X6.02 SA234WPB | NO | 1 | 1 | 35.68 | 35.68
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | SUPPORT PIPE DIA 168.3 X 7.11 SA106GRB | M | 1.7 | 1.7 | 48.042 | 48.042
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | SUPPORT PIPE DIA 114.3 X 6.02 SA106GRB | M | 2 | 2 | 32.14 | 32.14
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | SUPPORT PIPE DIA 88.9X6.02 SA106GRB | M | 0.6 | 0.6 | 7.38 | 7.38
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | BOTTOM PLATE 10MM THK 1000X1000 SA515GR70 | NO | 1 | 1 | 78.5 | 78.5
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | LUG PLATE 12MM THK 340X170 SA515GR70 | NO | 1 | 1 | 3.7 | 3.7
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | SW STUB NB25 CL3000 CS OD36,H=44 SA105 | NO | 4 | 4 | 1.72 | 1.72
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-446 | PE-DG-508-153-M807/01p | CARRIER PLATE 16X50X120 SA515GR70 | NO | 4 | 4 | 3 | 3
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | PIPE OD114.3X6.02 SA106GRB | M | 36 | 36 | 578.88 | 578.88
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | PIPE OD168.3X7.11 SA106GRB | M | 45 | 45 | 1271.7 | 1271.7
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | BW LR 90DEG ELL OD114.3X6.02 SA234WPB | NO | 12 | 12 | 52.08 | 52.08
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | BW 90 DEG LR ELBOW 168.3X7.11 SA234WPB | NO | 14 | 14 | 157.22 | 157.22
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | BW RED 168.3X7.11/114.3X6.02 SA234WPB | NO | 3 | 3 | 9.87 | 9.87
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | BW UEQT OD168.3X7.11/114.3X6.02 SA234WPB | NO | 3 | 3 | 42 | 42
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | SW STUB NB25 OD46 H=44 SA105 | NO | 4 | 4 | 1.72 | 1.72
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | SUPPORT PLATE 10MM THK 500x500 SA515GR70 | NO | 1 | 1 | 19.63 | 19.63
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | SUPPORT PIPE DIA 88.9X6.02 SA106GRB | M | 2 | 2 | 24.6 | 24.6
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | EQT 33.4X4.55 SA234WPB | NO | 2 | 2 | 0.86 | 0.86
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | ELBOW 90DEG OD33.4X4.55 SA234WPB | NO | 4 | 4 | 1 | 1
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | PIPE OD 33.4X4.55 SA106GRB | M | 6 | 6 | 19.44 | 19.44
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-153-M814/01p | PIPE OD 21.3X3.73 SA106GRB | M | 5 | 5 | 8.1 | 8.1
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | PIPE OD273x12.7x6000 - SA106 Gr.C | M | 200 | 200 | 16176 | 16176
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | PIPE OD323.9x12.7x6000 - SA106 Gr.C | M | 5 | 5 | 487.3 | 487.3
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SUPPORT PIPE OD273x12.7x6000 - SA106 Gr.C | M | 1 | 1 | 81.52 | 81.52
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SUPPORT PIPE OD219.1x12.7x6000 - SA106 Gr.C | M | 7.5 | 7.5 | 484.8 | 484.8
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SUPPORT PIPE OD114.3x6.02x6000 - SA106 Gr.C | M | 2 | 2 | 32.12 | 32.12
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW LR 90DEG ELL OD273x12.7 SA234WPC | NO | 50 | 50 | 2617.5 | 2617.5
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW LR 45DEG ELL OD273x12.7 SA234WPC | NO | 12 | 12 | 314.04 | 314.04
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW RED 273.1X12.7 / 168.3X8.56 SA234WPC | NO | 4 | 4 | 48.28 | 48.28
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW RED 273X12.7 / 219.1x12.7 SA234WPC | NO | 2 | 2 | 26.28 | 26.28
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW RED 323.9X12.7 / 219.1x12.7 SA234WPC | NO | 2 | 2 | 33.96 | 33.96
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BW RED 323.9X12.7 / 273x12.7 SA234WPC | NO | 6 | 6 | 109.74 | 109.74
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | ASME B16.11 SW STUB NB25,CL:6000 SA105 | NO | 16 | 16 | 9.12 | 9.12
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | TEMP STUB RC 1.5" L=45-SA105 | NO | 18 | 18 | 31.86 | 31.86
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SCREW PLUG RC 1.5" SA105 | NO | 18 | 18 | 9 | 9
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | THERMOWEL STUB OD-63.5 H=154-SA105 C.S | NO | 4 | 4 | 12.408 | 12.408
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | CARRIER PLATE 12X80X40-SA515GR70 | NO | 16 | 16 | 4.816 | 4.816
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | LUG PLATE 16x443x260 SA515 GR70 | NO | 5 | 5 | 72.35 | 72.35
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BOTTOM PLATE 10THKX150X150 SA515 GR70 | NO | 4 | 4 | 7.04 | 7.04
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BOTTOM PLATE 10THKX250X250 SA515 GR70 | NO | 12 | 12 | 58.875 | 58.875
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | BOTTOM PLATE 10THKX300X300 SA515 GR70 | NO | 1 | 1 | 7.065 | 7.065
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | TEMPERATURE STUB M33X2, L=64 SA105 | NO | 4 | 4 | 2.8 | 2.8
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | PACKING RING M33x2 IS1972 | NO | 4 | 4 | 0.04 | 0.04
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SCREW PLUG M33 x 2 SA105 SA105 | NO | 4 | 4 | 0.64 | 0.64
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SPARE PIPE OD273x12.7x6000 - SA106 Gr.C | M | 4 | 4 | 323.2 | 323.2
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M802/01p | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 4 | 0.72 | 0.72
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | PIPE OD273X6.35x6000 - SA106 Gr.B | M | 175 | 175 | 7308 | 7308
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | PIPE OD273X12.7x6000 - SA106 Gr.B | M | 7 | 7 | 570.71 | 570.71
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | PIPE OD323.9X12.7x6000 - SA106 Gr.B | M | 2.5 | 2.5 | 243.65 | 243.65
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SUPPORT PIPE OD114.3x6.02 SA106GR.B | M | 6 | 6 | 96.48 | 96.48
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SUPPORT PIPE OD168.3x7.11 SA106GR.B | M | 3 | 3 | 84.78 | 84.78
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SUPPORT PIPE OD219.1x12.7 SA106GR.B | M | 3 | 3 | 193.92 | 193.92
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SPARE PIPE OD273x6.35 SA106GR.B | M | 3 | 3 | 125.28 | 125.28
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW LR 90DEG ELL OD273x6.35 SA234WPB | NO | 29 | 29 | 777.49 | 777.49
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW LR 60DEG ELL OD273x6.35 SA234WPB | NO | 3 | 3 | 54 | 54
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW LR 45DEG ELL OD273x6.35 SA234WPB | NO | 3 | 3 | 40.23 | 40.23
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW LR 30DEG ELL OD273x6.35 SA234WPB | NO | 4 | 4 | 36 | 36
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW LR 90DEG ELL OD 355.6x9.53 SA234WPB | NO | 2 | 2 | 136.2 | 136.2
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW RED 355.6x9.53 / 273X6.35 SA234WPB | NO | 4 | 4 | 95.204 | 95.204
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW RED 323.9X12.7 / 219.1x12.7 SA234WPC | NO | 2 | 2 | 43.968 | 43.968
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW RED 273.1X12.7 / 168.3X8.56 SA234WPC | NO | 4 | 4 | 48.32 | 48.32
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BW RED 273X12.7 / 219.1x12.7 SA234WPC | NO | 2 | 2 | 26.28 | 26.28
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | ASME B16.11 SW STUB NB15,CL:3000 SA105 | NO | 4 | 4 | 0.72 | 0.72
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 6 | 6 | 2.58 | 2.58
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | TEMP STUB RC 1" L=45-SA105 | NO | 18 | 18 | 9.284 | 9.284
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SCREW PLUG RC 1" SA105 | NO | 18 | 18 | 3.6 | 3.6
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | THERMOWEL STUB OD-70 H=157-SA105 | NO | 4 | 4 | 14.4 | 14.4
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | LUG PLATE 16x443x260 SA515 GR70 | NO | 2 | 2 | 28.932 | 28.932
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BOTTOM PLATE 10THKX250X250 SA515 GR70 | NO | 4 | 4 | 19.624 | 19.624
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BOTTOM PLATE 10THKX200X200 SA515 GR70 | NO | 20 | 20 | 62.8 | 62.8
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | BOTTOM PLATE 10THKX350X350 SA515 GR70 | NO | 2 | 2 | 19.232 | 19.232
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M803/01P | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 4 | 0.72 | 0.72
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | PIPE OD219.1X6.35x6000 - SA106 Gr.B | M | 60 | 60 | 1999.2 | 1999.2
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | PIPE OD219.1X12.7x6000 - SA106 Gr.B | M | 4 | 4 | 258.56 | 258.56
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | SUPPORT PIPE OD168.3x7.11 SA106GR.B | M | 3.5 | 3.5 | 98.91 | 98.91
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW LR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 13 | 13 | 223.73 | 223.73
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW LR 45DEG ELL OD219.1x6.35 SA234WPB | NO | 2 | 2 | 17.2 | 17.2
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW LR 30DEG ELL OD219.1x12.7 SA234WPB | NO | 1 | 1 | 11.13 | 11.13
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW LR 90EG ELL OD273x12.7 SA234WPB | NO | 1 | 1 | 52.47 | 52.47
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW RED 273X6.35 / 219.1X6.35 SA234WPB | NO | 2 | 2 | 13.5 | 13.5
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW RED 273X12.7 / 219.1X12.7 SA234WPB | NO | 1 | 1 | 13.14 | 13.14
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW RED OD219.1x6.35/168.3x10.97 SA234WPB | NO | 2 | 2 | 8 | 8
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW RED OD219.1x12.7/168.3x10.97 SA234WPB | NO | 2 | 2 | 17.46 | 17.46
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BW EQT 219.1x12.7 SA234WPB | NO | 1 | 1 | 37.4 | 37.4
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 3 | 3 | 1.29 | 1.29
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | TEMPERATURE STUB M33x2 L=64 -SA105 | NO | 1 | 1 | 0.7 | 0.7
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | SCREW PLUG M33 X 2-SA105 | NO | 1 | 1 | 0.16 | 0.16
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | PACKING RING M33x2 - IS1972 | NO | 1 | 1 | 0.01 | 0.01
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | TEMP STUB RC 1" L=64-SA105 | NO | 7 | 7 | 4.9 | 4.9
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | SCREW PLUG RC 1" SA105 | NO | 7 | 7 | 1.4 | 1.4
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | BOTTOM PLATE 10THKX1000X1500 SA515 GR70 | NO | 1 | 1 | 117.75 | 117.75
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M806/01P | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 4 | 0.72 | 0.72
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | PIPE OD273X12.7x6000 - SA106 Gr.B | M | 39 | 39 | 3179.28 | 3179.28
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | SUPPORT PIPE OD219.1x12.7 L=1.5 SA106GR.B | M | 1.5 | 1.5 | 96.96 | 96.96
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | BW LR 90DEG ELL OD273x12.7 SA234WPB | NO | 23 | 23 | 1206.81 | 1206.81
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | BW LR 60DEG ELL OD273x12.7 SA234WPB | NO | 3 | 3 | 104.94 | 104.94
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | BW EQT 273x12.7 SA234WPB | NO | 1 | 1 | 56.83 | 56.83
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | BW RED 406.4x17 / 273x12.7 SA234WPB | NO | 1 | 1 | 48.96 | 48.96
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 3 | 3 | 1.29 | 1.29
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | TEMP STUB RC 1" L=64-SA105 | NO | 6 | 6 | 4.2 | 4.2
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | SCREW PLUG RC 1" SA105 | NO | 6 | 6 | 1.2 | 1.2
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | TEMPERATURE STUB M33x2 L=64 -SA105 | NO | 2 | 2 | 1.4 | 1.4
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | SCREW PLUG M33 X 2-SA105 | NO | 2 | 2 | 0.32 | 0.32
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | PACKING RING M33x2 - IS1972 | NO | 2 | 2 | 0.02 | 0.02
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | LUG PLATE 16x443x260 SA515 GR70 | NO | 1 | 1 | 14.46 | 14.46
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | BOTTOM PLATE 10THKX250X250 SA515 GR70 | NO | 4 | 4 | 19.64 | 19.64
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | SPARE PIPE OD273X12.7 - SA106 Gr.B | M | 1 | 1 | 81.52 | 81.52
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M808/01p | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 4 | 0.72 | 0.72
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | PIPE OD273X12.7x6000 - SA106 Gr.B | M | 34 | 34 | 2771.68 | 2771.68
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | PIPE OD2191.X6.35x6000 - SA106 Gr.B | M | 45 | 45 | 1498.95 | 1498.95
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SPARE PIPE OD219.1x12.7 SA106GR.B | M | 1 | 1 | 64.64 | 64.64
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SUPPORT PIPE OD168.3x7.11 SA106GR.B | M | 2 | 2 | 56.52 | 56.52
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW SR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 1 | 1 | 11.46 | 11.46
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW LR 90DEG ELL OD219.1x6.35 SA234WPB | NO | 7 | 7 | 120.47 | 120.47
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW LR 45DEG ELL OD219.1x6.35 SA234WPB | NO | 5 | 5 | 43 | 43
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW LR 30DEG ELL OD219.1x6.35 SA234WPB | NO | 4 | 4 | 23 | 23
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW LR 90DEG ELL OD273x12.7 SA234WPB | NO | 11 | 11 | 577.17 | 577.17
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW LR 45DEG ELL OD273x12.7 SA234WPB | NO | 1 | 1 | 26.24 | 26.24
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW RED 323.9x9.53 / 273x12.7 SA234WPB | NO | 1 | 1 | 13.88 | 13.88
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW RED 323.9x9.53/ 219.1X6.35 SA234WPB | NO | 1 | 1 | 12.9 | 12.9
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BW RED 273x6.35/219.1X6.35 SA234WPB | NO | 1 | 1 | 6.75 | 6.75
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 2 | 2 | 0.86 | 0.86
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | TEMPERATURE STUB M33x2 L=64 -SA105 | NO | 2 | 2 | 1.4 | 1.4
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SCREW PLUG M33 X 2-SA105 | NO | 2 | 2 | 0.32 | 0.32
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | PACKING RING M33x2 - IS1972 | NO | 2 | 2 | 0.02 | 0.02
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | TEMP STUB RC 1" L=64-SA105 | NO | 4 | 4 | 2.8 | 2.8
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SCREW PLUG RC 1" SA105 | NO | 4 | 4 | 0.8 | 0.8
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | LUG PLATE 16x443x260 SA515 GR70 | NO | 1 | 1 | 14.47 | 14.47
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | BOTTOM PLATE 10THKX250X250 SA515 GR70 | NO | 4 | 4 | 19.6 | 19.6
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SPARE PIPE OD273X12.7x6000 - SA106 Gr.B | M | 1 | 1 | 81.52 | 81.52
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-443 | PE-DG-508-147-M809/01p | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 4 | 0.72 | 0.72
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | PIPE DIA 273.0 X 6.35 X 6500 SA106GRB | M | 68 | 68 | 2839.68 | 2839.68
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | PIPE OD-219.1X12.7X6000-SA106GRC | M | 39 | 39 | 2520.96 | 2520.96
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | PIPE DIA 88.9 X 5.49 SA106GRB | M | 38 | 38 | 429.02 | 429.02
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW LR 90DEG ELL OD273X6.35 SA234WPB | NO | 20 | 20 | 537.6 | 537.6
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW LR 45DEG ELL OD273X6.35 SA234WPB | NO | 4 | 4 | 53.76 | 53.76
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW LR 90DEG ELL OD219.1X8.18 SA234WPC | NO | 15 | 15 | 329.7 | 329.7
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW LR 45DEG ELL OD219.1X8.18 SA234WPC | NO | 2 | 2 | 21.98 | 21.98
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 5 | 5 | 10.05 | 10.05
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW RED 323.9X6.35/273X6.35 SA234WPB | NO | 4 | 4 | 37.4 | 37.4
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW RED 323.9X12.7/219.1X12.7 SA234WPC | NO | 1 | 1 | 17 | 17
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW RED 219.1X8.18/168.3X7.11 SA234WPC | NO | 1 | 1 | 5.76 | 5.76
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW RED 168.3X7.11/88.9X5.49 SA234WPB | NO | 1 | 1 | 3.1 | 3.1
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW EQT OD273X6.35 SA234WPB | NO | 1 | 1 | 29.11 | 29.11
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW EQT OD219.1X8.18 SA234WPC | NO | 1 | 1 | 24.61 | 24.61
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | BW EQT OD88.9X5.49 SA234WPB | NO | 1 | 1 | 3.29 | 3.29
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | ASME B16.11 SW STUB NB25 CL 3000 SA105 | NO | 5 | 5 | 2.15 | 2.15
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | TEMP STUB-CS- RC1" L=64 - CS SA105 | NO | 9 | 9 | 6.3 | 6.3
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | CARBON STEEL PLUG 1" CS SA105 | NO | 9 | 9 | 1.8 | 1.8
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | TEMP STUB MX33X2 L=64CS SA105 | NO | 1 | 1 | 0.7 | 0.7
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SOW FLANGE NB 25 CL150 SA515GR 70 | NO | 2 | 2 | 1.8 | 1.8
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SOW FLANGE NB50 CL 150 SA515GR 70 | NO | 2 | 2 | 4 | 4
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | LUG PLATE 12THK 260X125 SA515GR 70 | NO | 3 | 3 | 9.18 | 9.18
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SUPPORT PIPE OD60.3X5.54 SA234WPB | M | 3 | 3 | 22.44 | 22.44
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SUPPORT PIPE OD219.1X6.35 SA234WPB | M | 4 | 4 | 133.24 | 133.24
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SUPPORT PIPE OD168.3X7.11 SA234WPB | NO | 4 | 4 | 113.04 | 113.04
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | CARRIER PLATE 16X50X120 CS SA515GR70 | NO | 12 | 12 | 9.12 | 9.12
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | STUD M12 X 1.75 X140 SA193B7 | NO | 8 | 8 | 0.896 | 0.896
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | NUT M12 SA194GR7 | NO | 16 | 16 | 0.32 | 0.32
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | STUD M16 X 2 X 110 SA193B7 | NO | 8 | 8 | 1.16 | 1.16
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | NUT M16 SA194GR7 | NO | 16 | 16 | 0.48 | 0.48
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | NON-ASBESTOS JOINTING SHT 1.5MMX500X500 | NO | 1 | 1 | 0.618 | 0.618
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | PIPE OD-323.9X12.7X6000-SA106GRC | M | 2 | 2 | 194.92 | 194.92
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M807/01p | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 4 | 0.72 | 0.72
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | PIPE 88.9X5.49 - SA106GRB | M | 35 | 35 | 395.15 | 395.15
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | PIPE OD60.3X5.54 L=6000 SA106GRB | M | 12 | 12 | 89.76 | 89.76
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | BW LR 90DEG ELL OD88.9X5.49 SA234WPB | NO | 10 | 10 | 20.2 | 20.2
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | BW LR 90DEG ELL 60.3 X 5.54 SA234WPB | NO | 6 | 6 | 6.36 | 6.36
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | BW UEQT 88.9X5.49/60.3X5.54 SA234WPB | NO | 2 | 2 | 5.94 | 5.94
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | SW STUB NB25 CL3000 SA105 | NO | 2 | 2 | 0.86 | 0.86
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | SW STUB NB15 CL3000 SA105 | NO | 2 | 2 | 0.36 | 0.36
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | SPARE PIPE 88.9X5.49 - SA106GRB | M | 1 | 1 | 11.29 | 11.29
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-442 | PE-DG-508-147-M810/01p | SPARE PIPE OD60.3X5.54 L=6000 SA106GRB | M | 1 | 1 | 7.48 | 7.48
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | PIPE DIA 114.3 X 6.02 SA106GRB | M | 52 | 52 | 835.64 | 835.64
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | ASMEB16.9 BWLR 90DEG ELBOW OD114.3X6.02 SA234GRB | NO | 6 | 6 | 25.98 | 25.98
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | ASMEB16.9 BW EQUAL TEE OD114.3X6.02 SA234GRB | NO | 6 | 6 | 33.9 | 33.9
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | SOW FLANGE NB100 CL150-OD230X30 SA515GR70 | NO | 2 | 2 | 10.6 | 10.6
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | BOLT-M16x90 -8.8-IS1364P1 | NO | 8 | 8 | 1.36 | 1.36
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | NUT -M16 -CL4-IS1363P3 | NO | 8 | 8 | 0.24 | 0.24
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | NON-ASBESTOS JOINTING SHEET 1.5MM | NO | 1 | 1 | 2.47 | 2.47
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | BLIND FLANGE NB100 CL150 SA515GR70 | NO | 2 | 2 | 15.44 | 15.44
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | SPARE PIPE OD 114.3X6.02 L=2000 SA234GRB | M | 2 | 2 | 32.14 | 32.14
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | SUPPORT PIPE DIA 88.9 X 5.49, L=4000 SA234GRB | M | 4 | 4 | 45.16 | 45.16
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | PLATE 10.0 MM, 1000X500 SA515GR70 | NO | 1 | 1 | 39.25 | 39.25
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | PIPE DIA 323.9 X 6.35 SA106GRB L=195MM | NO | 1 | 1 | 9.697 | 9.697
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | BW RED 323.9X6.35/114.3X6.02 SA234WPB | NO | 1 | 1 | 8.16 | 8.16
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | PIPE OD 114.3X6.02 L=350MM SA106GRB | NO | 2 | 2 | 3.15 | 3.15
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-448 | PE-DG-508-147-M815/00 | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 4 | 0.72 | 0.72
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | PIPE OD168.3x7.11x6000 - SA106 Gr.B | M | 60 | 60 | 1695.6 | 1695.6
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | PIPE OD219.1x12.7x6000 - SA106 Gr.B | M | 7 | 7 | 452.48 | 452.48
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | SUPPORT PIPE OD114.3x6.02 L=2M SA106GR.B | M | 2 | 2 | 32.16 | 32.16
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | SUPPORT PIPE OD168.3x7.11 L=1M-SA106GRB | M | 1 | 1 | 28.26 | 28.26
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW LR 90DEG ELL OD219.1X12.7 SA234WPB | NO | 5 | 5 | 166.95 | 166.95
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW LR 90DEG ELL OD168.3X7.11 SA234WPB | NO | 12 | 12 | 134.4 | 134.4
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW LR 45DEG ELL OD168.3X7.11 SA234WPB | NO | 2 | 2 | 11.2 | 11.2
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW LR 30DEG ELL OD168.3X7.11 SA234WPB | NO | 1 | 1 | 3.73 | 3.73
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW RED 219.1x12.7/168.3x7.11 SA234WPB | NO | 3 | 3 | 26.19 | 26.19
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW RED 219.1x12.7/88.9X7.62 SA234WPB | NO | 1 | 1 | 7.31 | 7.31
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BW RED 168.3x7.11/88.9x 7.62SA234WPB | NO | 1 | 1 | 3.09 | 3.09
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | ASME B16.11 SW STUB NB25,CL:3000 SA105 | NO | 5 | 5 | 2.15 | 2.15
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | TEMP STUB RC 1" L=64-SA105 | NO | 8 | 8 | 5.6 | 5.6
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | SCREW PLUG RC 1" SA105 | NO | 8 | 8 | 1.6 | 1.6
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | TEMPERATURE STUB M33x2 L=64 -SA105 | NO | 5 | 5 | 3.5 | 3.5
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | SCREW PLUG M33 X 2-SA105 | NO | 5 | 5 | 0.05 | 0.05
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | PACKING RING M33x2 - IS1972 | NO | 5 | 5 | 0.8 | 0.8
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | CARRIER PLATE 12X50X80-SA515GR70 | NO | 4 | 4 | 1.507 | 1.507
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | BOTTOM PLATE 10THKX1000X500 SA515 GR70 | NO | 1 | 1 | 39.25 | 39.25
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-444 | PE-DG-508-147-M805/01P | SW STUB-CS-NB 15 CLASS 3000 CS SA105 | NO | 4 | 4 | 0.72 | 0.72
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | PIPE OD168.3X10.97x6000 - SA106 Gr.C | M | 29 | 29 | 1234.24 | 1234.24
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | PIPE OD219.1X12.7x6000 - SA106 Gr.C | M | 117 | 117 | 7562.9965 | 7562.9965
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | SUPPORT PIPE OD114.3x6.02 L=1000 SA106GR.C | M | 2 | 2 | 32.14 | 32.14
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | SUPPORT PIPE OD168.3x7.11 L=3000 SA106GR.C | M | 3 | 3 | 84.78 | 84.78
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW LR 90DEG ELL OD168.3x10.97 SA234WPC | NO | 13 | 13 | 199.03 | 199.03
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW LR 45DEG ELL OD168.3x10.97 SA234WPC | NO | 2 | 2 | 15.31 | 15.31
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW LR 90DEG ELL OD219.1x12.7 SA234WPC | NO | 26 | 26 | 805.22 | 805.22
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW LR 45DEG ELL OD219.1x12.7 SA234WPC | NO | 6 | 6 | 92.88 | 92.88
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW LR 30DEG ELL OD219.1x12.7 SA234WPC | NO | 1 | 1 | 15.48 | 15.48
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BW RED 219.1x12.7 / 168.3x10.97 SA234WPC | NO | 4 | 4 | 37.2 | 37.2
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | ASME B16.11 SW STUB NB25,CL:6000 SA105 | NO | 14 | 14 | 7.98 | 7.98
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | TEMP STUB RC 1 1/2 " L=64-SA105 | NO | 16 | 16 | 37.504 | 37.504
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | SCREW PLUG RC 1 1/2 " SA105 | NO | 16 | 16 | 8 | 8
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | THERMOWEL STUB OD-70 H=157-SA105 | NO | 4 | 4 | 14.4 | 14.4
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | LUG PLATE 16x428x240 SA515 GR70 | NO | 1 | 1 | 12.901 | 12.901
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | LUG PLATE 12x340x170 SA515 GR70 | NO | 3 | 3 | 16.334 | 16.334
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BOTTOM PLATE 10THKX150X150 SA515 GR70 | NO | 2 | 2 | 3.532 | 3.532
6 | Sipat 2x800 MW Unit 6 | Heater Drains Piping | Non IBR | 82-447 | PE-DG-508-147-M801/01p | BOTTOM PLATE 10THKX200X200 SA515 GR70 | NO | 6 | 6 | 18.84 | 18.84
6 Total | [10 empty] | 73261.4355
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | PIPE OD 219.1 x 36 - SA106GRC | M | 48 | 48 | 7802.82 | 7802.82
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | SPARE PIPE OD 219.1 x 36 - SA106GRC | M | 2 | 2 | 325.118 | 325.118
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | PIPE DIA 168.3 X 27.5 SA106GRC | M | 7 | 7 | 668.425 | 668.425
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | PIPE DIA 168.3 X 31 SA335 P22 | M | 2 | 2 | 209.934 | 209.934
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | PIPE DIA 114.3 X 6.02 SA106GRC | M | 1 | 1 | 16.075 | 16.075
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW LR 90DEG ELL OD219.1X36 SA234WPC | NO | 9 | 9 | 700.92 | 700.92
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW LR 90DEG ELL OD168.3x27.5 SA234WPC | NO | 3 | 3 | 103.05 | 103.05
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW SR 90DEG ELL OD168.3x31 SA234WP22 | NO | 1 | 1 | 25.05 | 25.05
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW LR 90DEG ELL OD168.3x31 SA234WP22 | NO | 4 | 4 | 150.96 | 150.96
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW UEQT 219.1X36/168.3X27.5 SA234WPC | NO | 1 | 1 | 86.48 | 86.48
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | BW C.RED 219.1 X 36/168.3X27.5 SA234WPC | NO | 1 | 1 | 19.79 | 19.79
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | CARRIER PLATE 16X50X120-SA515 GR70 | NO | 4 | 4 | 3.04 | 3.04
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | ASME B16.11 SW STUB NB25,CL:9000-SA105 | NO | 4 | 4 | 3.24 | 3.24
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | TEMP STUB RC 1.5" OD98 L=64 - CS SA105 | NO | 1 | 1 | 2.344 | 2.344
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | SCREW PLUG RC 1.5" CS SA105 | NO | 1 | 1 | 0.5 | 0.5
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | ASME B16.11 SW STUB NB25,CL:9000-SA182F22 | NO | 2 | 2 | 1.62 | 1.62
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-430 | PE-DG-508-141-M805/01P | LUGPLATE 16X340X170 SA387 GR22 | NO | 2 | 2 | 7.4 | 7.4
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | PIPE DIA 219.1x12.7 SA106GRC | M | 70 | 70 | 4524.87 | 4524.87
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | PIPE DIA 168.3x7.11 SA106GRB | M | 70 | 70 | 1978.2 | 1978.2
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | SPARE PIPE DIA 168.3x7.11 SA106GRB | M | 2 | 2 | 56.52 | 56.52
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | SPARE PIPE DIA 219.1x12.7 SA106GRC | M | 2 | 2 | 129.282 | 129.282
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | SUPP.PIPE DIA 114.3 X 8.56 SA106GRC | M | 3 | 3 | 66.963 | 66.963
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW LR 90DEG ELBOW OD219.1x12.7 SA234WPC | NO | 12 | 12 | 371.16 | 371.16
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW LR 30DEG ELBOW OD219.1x12.7 SA234WPC | NO | 1 | 1 | 10.31 | 10.31
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW LR 90DEG ELBOW OD168.3x7.11SA234WPB | NO | 8 | 8 | 81.12 | 81.12
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW LR 45DEG ELBOW OD168.3x7.11 SA234WPB | NO | 3 | 3 | 15.21 | 15.21
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW RED 219.1x12.7/168.3X7.11 SA234WPB | NO | 1 | 1 | 7.01 | 7.01
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | BW RED 323.9x12.7/219.1X12.7 SA234WPC | NO | 2 | 2 | 35 | 35
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | CARRIER PLATE 20X50X120-SA515 GR70 | NO | 28 | 28 | 91.448 | 91.448
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | PLATE 20X300X300 SA515 GR70 | NO | 4 | 4 | 56.52 | 56.52
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | PLATE 20X150X150 SA515 GR70 | NO | 9 | 9 | 31.788 | 31.788
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | PLATE 20X200X200 SA515 GR70 | NO | 1 | 1 | 6.28 | 6.28
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | ASME B16.11 SW STUB NB25,CL:9000-SA105 | NO | 1 | 1 | 0.81 | 0.81
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-421 | PE-DG-508-139-M803/01P | ASME B16.11 SW STUB NB50,CL:9000 SA105 | NO | 6 | 6 | 14.64 | 14.64
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | PIPE DIA 168.3 X 21.95 - SA106GRC | M | 170 | 170 | 13467.4 | 13467.4
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | PIPE DIA 114.3x13.49 SA106GRC | M | 33 | 33 | 1107.15 | 1107.15
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | PIPE DIA 88.9x11.13 SA106GRC | M | 66 | 66 | 1409.1 | 1409.1
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SPARE PIPE DIA 168.3 X 21.95 - SA106GRC | M | 3 | 3 | 237.66 | 237.66
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SPARE PIPE DIA 114.3x13.49 SA106GRC | M | 1 | 1 | 33.55 | 33.55
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SPARE PIPE DIA 88.9x11.13 SA106GRC | M | 2 | 2 | 42.7 | 42.7
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW LR 90DEG ELBOW OD168.3x21.95 SA234WPC | NO | 25 | 25 | 712.5 | 712.5
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW LR 90DEG ELBOW OD114.3x13.49 SA234WPC | NO | 11 | 11 | 88.11 | 88.11
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW LR 90DEG ELBOW OD88.9x11.13 SA234WPC | NO | 16 | 16 | 61.12 | 61.12
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW EQT OD168.3x21.95 SA234WPC | NO | 1 | 1 | 37.04 | 37.04
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW UEQT OD168.3x21.95/OD114.3X13.49 SA234WPC | NO | 1 | 1 | 32.04 | 32.04
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW RED OD168.3x21.95/OD114.3X13.49 SA234WPC | NO | 2 | 2 | 15.78 | 15.78
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BW RED OD168.3x21.95/OD88.9X11.13 SA234WPC | NO | 1 | 1 | 6.89 | 6.89
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | ASME B16.11 SW STUB NB25,CL:6000-SA105 | NO | 1 | 1 | 0.57 | 0.57
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | ASME B16.11 SW STUB NB50,CL:6000 SA105 | NO | 5 | 5 | 9.8 | 9.8
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | THERMOWEL STUB OD70 H-146 CS SA105 | NO | 1 | 1 | 3.6 | 3.6
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | LUG PLATE 12x260x125 SA515 GR70 | NO | 1 | 1 | 2.2 | 2.2
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SUPPORT PIPE OD 114.3x13.49 SA106 GRC | M | 4.5 | 4.5 | 150.975 | 150.975
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SUPPORT PIPE OD 88.9x11.13 SA106 GRC | M | 3 | 3 | 64.05 | 64.05
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SUPPORT PIPE OD 60.3x11.07 SA106 GRC | M | 2 | 2 | 26.88 | 26.88
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | BOTTOM PLATE 16THK 1500x2000 SA515 GR70 | NO | 1 | 1 | 376.8 | 376.8
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | TEMP STUB RC 1.5" OD98 L=64 - CS SA105 | NO | 4 | 4 | 9.376 | 9.376
7 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | IBR | 82-433 | PE-DG-508-141-M806/01P | SCREW PLUG RC 1.5" CS SA105 | NO | 4 | 4 | 2 | 2
7 Total | [10 empty] | 35501.188
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | PIPE OD 323.9X 9.53 X 6000 - SA106GRB | M | 12 | 12 | 886.56 | 886.56
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | PIPE OD 273x9.27 SA106GRB | M | 43 | 43 | 2592.384 | 2592.384
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | PIPE DIA 33.4X4.55 SA106GRB | M | 5 | 5 | 16.15 | 16.15
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | BW LR 90DEG ELL OD323.9x9.53 SA234WPB | NO | 1 | 1 | 54 | 54
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | BW LR 90DEG ELL OD273x9.27 SA234WPB | NO | 6 | 6 | 222 | 222
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | BW EQT OD323.9x9.53 SA234WPB | NO | 1 | 1 | 60.42 | 60.42
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | BW RED OD323.9x9.53/273x9.27 SA234WPB | NO | 1 | 1 | 13.8801 | 13.8801
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | ASME B16.11 SW STUB NB25 CL:6000-SA105 | NO | 2 | 2 | 2.9146 | 2.9146
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | BOTTEM PLATE 10 THK500x500 SA515 GR70 | NO | 1 | 1 | 2.4271 | 2.4271
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | SUPPORT PIPE OD219.1x12.7 SA106 GRB | M | 1 | 1 | 64.644 | 64.644
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | SPARE PIPE OD 323.9X 9.53 X 6000 - SA106GRB | M | 2 | 2 | 147.76 | 147.76
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-434 | PE-DG-508-153-M803 /01P | SPARE PIPE OD 273x9.27 X 6000 - SA106GRB | M | 2 | 2 | 120.58 | 120.58
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | PIPE OD 114.3X6.02 SA106GRB | M | 36 | 36 | 578.68 | 578.68
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | PIPE OD 88.9X5.49 SA106GRB | M | 88 | 88 | 993.72 | 993.72
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | PIPE DIA 33.4X4.55 SA106GRB | M | 10 | 10 | 32.37 | 32.37
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | 90DEG BW LR ELBOW 114.3X6.02 SA234WPB | NO | 4 | 4 | 20 | 20
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | 90DEG BW LR ELBOW 88.9X5.49 SA234WPB | NO | 21 | 21 | 48.3 | 48.3
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | BW RED 114.3X6.02/88.9X5.49 SA234WPB | NO | 1 | 1 | 1.46 | 1.46
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | BW EQUAL TEE OD 88.9 X 5.49 SA234WPB | NO | 2 | 2 | 7.6 | 7.6
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SW STUB-CS-NB 25 CLASS 6000 CS SA105 | NO | 5 | 5 | 2.15 | 2.15
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SW STUB-CS-NB 50 CLASS 6000 CS SA105 | NO | 2 | 2 | 1.8 | 1.8
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | TEMPERATURE STUB M33X2 L=45 SA105 | NO | 2 | 2 | 1 | 1
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SCREW PLUG M33 X 2 SA105 | NO | 2 | 2 | 1.6 | 1.6
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | PACKING RING IS1972 | NO | 2 | 2 | 0.2 | 0.2
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SUPPORT PIPE OD 60.3X 5.54 SA106GRB | M | 5.5 | 5.5 | 41.1461 | 41.1461
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SUPPORT PLATE TH 12X1500X1000MM SA515GR70 | NO | 1 | 1 | 141.3 | 141.3
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | CARRIER PLATE 10X50X80 SA515GR70 | NO | 4 | 4 | 1.256 | 1.256
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SPARE PIPE OD 114.3X6.02 SA106GRB | M | 2 | 2 | 32.149 | 32.149
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SPARE PIPE OD 88.9X5.49 SA106GRB | M | 2 | 2 | 22.5847 | 22.5847
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | SUPPORT PIPE OD 88.9X5.49 SA106GRB | M | 1 | 1 | 11.2923 | 11.2923
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | BWUN EQUAL TEEOD 114.3X6.02/60.3X5.54 SA234WPB | NO | 2 | 2 | 9.86 | 9.86
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | TEMP STUB RC1 INCH SA105 | NO | 4 | 4 | 3.376 | 3.376
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-435 | PE-DG-508-153-M806/00 | CARBON STEEL PLUG 1" SA105 | NO | 4 | 4 | 0.8 | 0.8
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PIPE OD 457 X 9.53X 6000 - SA106GRC | M | 72 | 72 | 7571.52 | 7571.52
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PIPE OD 457 X 12.7X 6000 - SA106GRC | M | 42 | 42 | 5844.3 | 5844.3
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SPARE PIPE OD457X9.53 SA106 GR.C | M | 2 | 2 | 210.32 | 210.32
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SPARE PIPE OD457X12.7 SA106 GR.C | M | 1 | 1 | 139.15 | 139.15
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SUPPORT PIPE OD406.4x9.53 L=5000 SA106GRC | M | 5 | 5 | 466.3 | 466.3
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SUPPORT PIPE OD219.1x12.7 L=2000 SA106GRC | M | 2 | 2 | 129.28 | 129.28
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SUPPORT PIPE OD168.3X7.11 L=4500 SA106GRC | M | 4.5 | 4.5 | 127.17 | 127.17
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 90DEG ELL OD457x12.7 SA234WPC | NO | 8 | 8 | 1200.16 | 1200.16
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW SR 90DEG ELL OD457x9.53 SA234WPC | NO | 2 | 2 | 150.9 | 150.9
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 45DEG ELL OD457x9.53 SA234WPC | NO | 1 | 1 | 56.63 | 56.63
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 30DEG ELL OD457x9.53 SA234WPC | NO | 1 | 1 | 37.75 | 37.75
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 90DEG ELL OD457x9.53 SA234WPC | NO | 12 | 12 | 1359.6 | 1359.6
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 90DEG ELL OD355.6x9.53 SA234WPC | NO | 2 | 2 | 136.2 | 136.2
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW SR 90DEG ELL OD457x12.7 SA234WPC | NO | 2 | 2 | 199.88 | 199.88
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 30DEG ELL OD457x12.7 SA234WPC | NO | 2 | 2 | 99.9 | 99.9
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW RED 457x9.53 /355.6x9.53 SA234WPC | NO | 2 | 2 | 72.24 | 72.24
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW RED 457x9.53 /406.4x9.53 SA234WPC | NO | 2 | 2 | 75.88 | 75.88
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW RED 559x12.7 / 457x12.7 SA234WPC | NO | 2 | 2 | 159.08 | 159.08
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW RED 610x10 / 457x9.53 SA234WPC | NO | 4 | 4 | 261.84 | 261.84
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BOTTOM PLATE 10 THK 450 X 450-SA515GR70 | NO | 7 | 7 | 111.272 | 111.272
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BOTTOM PLATE 10 THK 2000 X 2000-SA515GR70 | NO | 1 | 1 | 314 | 314
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | CARRIER PLATE 20X120X50-SA515GR70 | NO | 8 | 8 | 7.04 | 7.04
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | ASME B16.11 SW STUB NB15 CL:3000-SA105 | NO | 22 | 22 | 3.96 | 3.96
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SW STUB NB25 CL:3000-SA105 | NO | 8 | 8 | 3.44 | 3.44
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | ASME B16.11 SW STUB NB40 CL:3000-SA105 | NO | 2 | 2 | 1.5 | 1.5
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SW STUB NB50 CL:3000-SA105 | NO | 6 | 6 | 7.98 | 7.98
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | TEMP STUB RC 1" L=45-SA105 | NO | 3 | 3 | 2.532 | 2.532
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SCREW PLUG RC 1" (CS) SA105 | NO | 3 | 3 | 0.6 | 0.6
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | TEMP STUB RC 1.5" L=45 - CS SA105 | NO | 7 | 7 | 7 | 7
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SCREW PLUG RC 1.5"-CS SA105 | NO | 7 | 7 | 3.5 | 3.5
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | TEMPERATURE STUB M33x2 L=64 (CS)-SA105 | NO | 1 | 1 | 0.7 | 0.7
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | SCREW PLUG M33 X 2-SA105 | NO | 1 | 1 | 0.8 | 0.8
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PACKING RING-COPPER | NO | 1 | 1 | 0.01 | 0.01
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | LUG PLATE 16 THK 400X650-SA515 GR70 | NO | 2 | 2 | 65.312 | 65.312
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PIPE OD 355.6 X 9.53 L=2000 -SA106GRC | M | 2 | 2 | 162.64 | 162.64
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PIPE OD 60.3 X 5.54 L=10M -SA106GRB | M | 10 | 10 | 74.8 | 74.8
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | PIPE OD 33.9 X 4.55 L=10M -SA106GRB | M | 10 | 10 | 32.3 | 32.3
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 90DEG 60.3 X 5.54 SA234WPB | NO | 2 | 2 | 1.78 | 1.78
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M802 /01p | BW LR 90DEG 33.4 X 4.55 -SA234WPB | NO | 2 | 2 | 0.38 | 0.38
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | PIPE OD 355.6 X 9.53 X 6000 - SA106GRC | M | 96 | 96 | 7808.064 | 7808.064
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SUPPORT PIPE OD 323.9 x 9.53 - SA106GRC | M | 1.5 | 1.5 | 110.82 | 110.82
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SUPPORT PIPE DIA 168.3 X 7.11 SA106GRC | M | 1 | 1 | 28.264 | 28.264
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SPARE PIPE OD355.6x9.53 SA106 GRC | M | 2 | 2 | 162.66 | 162.66
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | BW LR 90DEG ELL OD355.6X9.53 SA234WPC | NO | 15 | 15 | 1050 | 1050
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | BW RED 355.6X9.53/323.9X9.53 SA234WPC | NO | 4 | 4 | 102.4 | 102.4
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | BW RED 406.4X12.7/355.6X9.53 SA234WPC | NO | 1 | 1 | 45 | 45
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | BW RED 457X9.53/ 355.6X9.53 SA234WPC | NO | 2 | 2 | 72.24 | 72.24
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | ASME B16.11 SW STUB NB15 CL:3000-SA105 | NO | 9 | 9 | 1.62 | 1.62
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | ASME B16.11 SW STUB NB25 CL:3000-SA105 | NO | 5 | 5 | 2.15 | 2.15
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | ASME B16.11 SW STUB NB50 CL:3000-SA105 | NO | 4 | 4 | 5.32 | 5.32
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | TEMP STUB RC 1.5" L=45 - CS SA105 | NO | 7 | 7 | 7 | 7
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SCREW PLUG RC 1.5" CS SA105 | NO | 7 | 7 | 3.5 | 3.5
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | TEMP STUB RC 1" L=45-SA105 | NO | 3 | 3 | 2.532 | 2.532
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SCREW PLUG RC 1" (CS) SA105 | NO | 3 | 3 | 0.6 | 0.6
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | CARRIER PLATE T=20X50X120-SA515GR70 | NO | 12 | 12 | 10.56 | 10.56
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | SUPPORT PLATE 10X350X350-SA515GR70 | NO | 4 | 4 | 38.464 | 38.464
8 | Sipat 2x800 MW Unit 6 | Spray / Feed Water Piping | Non IBR | 82-420 | PE-DG-508-139-M801/01p | LUG PLATE 16 THK 546X315-SA515 GR70 | NO | 1 | 1 | 14 | 14
8 Total | [10 empty] | 34701.2039
Grand Total | [10 empty] | 525899.1956
Notes- 1. Suitable cushion +/-15% in quantity / weight shall be considered by the supplier in tender. 2. Pipe Size / Thickness / Specification mentioned in table may vary for very few cases during detail drawing stage. 3. IBR approval for applicable drawings / PGMA' are in vendor scope. 4. Fabrication drawings shall be prepared by vendor and shall be submitted to BHEL for review and approval prior to commencement of manufacturing. Please refer Technical Specification for better clarity. 5. All attachments like Stubs, Carrier Plates etc shall be welded on to the main pipe. These attachments have been indicated separately in the detailed BOM for better understanding the quantum involved. For better clarity regarding welding details / scope for these items, please refer Sl No 4.6 of the Technical Specification. 6. Items for which weight has been revised have been highlighed in Red.