## Sheet1
BHARAT HEAVY ELECTRICAL LIMITED, JHANSI
Specification No.
Item No.
|  |  | Location | Generator House
|  |  | Quantity | 2 Numbers
SCOPE :
SUPPLY , INSTALLATION, TESTING & COMMISSIONING OF 2 NOS. 1500 KVA DIESEL GENERATING SET, COMPLYING AS PER SPECIFICATION BELOW
NOTE :
1 | VENDOR must submit complete information against clause No. 15.0 ( Qualifying condition). The offer meeting this clause would only be processed.
2 | The " offered" Column and where applicable, the " Deviations" Column of this format shall be filled in by the Vender and submitted along with the offer.Technical details also submitted with the offer. Inadequate / incomplete, ambiguous, or unsustainable information against any of the clauses of the specification / requirements shall be treated as non - compliance.
3 | The offer and all documents enclosed with offer should be in English language only.
SPECIFICATION CUM COMPLIANCE CERTIFICATE OF 1500 KVA DIESEL GENERATOR SET
S.NO. | DESCRIPTION FOR BHEL REQUIREMENT |  |  | SPECIFIED / TO BE CONFIRMED BY | OFFERED | DEVIATIONS IF ANY
1 | PURPOSE & WORK PIECE MATERIAL:
1.1 | Two numbers 1500 KVA diesel generating sets are required for generating power supply 11kv, 50 hz, 3 phase 3 wire. |  |  | VENDER TO CONFIRM
2 | EQUIPMENT CONFIGURATION :- Diesel generating set shall consist of Diesel engine (complete with air intake system, exhaust system, coolant system Lubrication system, fuel system, safety controls, instrument panel), an alternator, control panel with synchronizing panel etc. Complete equipment shall be of " State of art" latest design & technology. The equipment shall consists of various components / sub assemblies as listed below: |  |  | VENDER TO CONFIRM
2.1 | DIESEL ENGINE
2.1.1 | Diesel engine shall be fuel efficient, robust in construction, water cooled four stroke 16 cylinder engine and shall be confirming to BS : 5514 . |  |  | VENDER TO CONFIRM
2.1.2 | Engine shall be electric start turbocharged and after cooled with capacity of 10% over load for one hourin 12 hours duration and to run continuously for a long duration upto 72 hours. |  |  | VENDER TO CONFIRM
2.1.3 | Engine shall have sufficient BHP to meet 1500 KVA requirement of alternator. |  |  | VENDER TO SPECIFY
2.1.4 | Noise level of engine shall be as per environmental rule. |  |  | VENDER TO CONFIRM
2.1.5 | Engine shall be mounted on AVM pads and a common base frame for engine and Alternator. |  |  | VENDER TO CONFIRM
2.1.6 | Following details of engine shall be furnised by the vender
2.1.7 | Make & model of the engine |  |  | VENDER TO SPECIFY
2.1.8 | BHP of the engine |  |  | VENDER TO SPECIFY
2.1.9 | RPM of the engine |  |  | VENDER TO SPECIFY
2.2 | AIR INTAKE SYSTEM
2.2.1 | It shall consists of air intake manifold |  |  | VENDER TO CONFIRM
2.2.2 | Dry type air cleaner |  |  | VENDER TO CONFIRM
2.2.3 | Vacuum indicator |  |  | VENDER TO CONFIRM
2.3 | EXHAUST SYSTEM |  |  | VENDER TO CONFIRM
2.3.1 | It shall consists of turbocharger |  |  | VENDER TO CONFIRM
2.3.2 | Flexible connection |  |  | VENDER TO CONFIRM
2.3.3 | Exhaust manifold |  |  | VENDER TO CONFIRM
2.3.4 | Rsidential silenser - 2 Nos. each. |  |  | VENDER TO CONFIRM
2.4 | COOLENT SYSTEM |  |  | VENDER TO CONFIRM
2.4.1 | It shall consists of Engine water pump |  |  | VENDER TO CONFIRM
2.4.2 | Radiator |  |  | VENDER TO CONFIRM
2.4.3 | Coolent additive concentrate |  |  | VENDER TO CONFIRM
2.4.4 | By pass thermostat |  |  | VENDER TO CONFIRM
2.5 | LUBRICATING SYSTEM
2.5.1 | It shall consists of oil pan |  |  | VENDER TO CONFIRM
2.5.2 | Engine mounted Lub oil pump |  |  | VENDER TO CONFIRM
2.5.3 | Full flow Lube oil filter |  |  | VENDER TO CONFIRM
2.5.4 | Lube oil by-pass filter |  |  | VENDER TO CONFIRM
2.5.5 | A.C. motor driven Lube oil priming pump |  |  | VENDER TO CONFIRM
2.6 | FUEL SYSTEM
2.6.1 | It shall consists of PT fuel pump |  |  | VENDER TO SPECIFY
2.6.2 | PTD injector |  |  | VENDER TO SPECIFY
2.6.3 | 24 Volt D.C. solenoid coil |  |  | VENDER TO SPECIFY
2.6.4 | Replaceable fuel filter |  |  | VENDER TO CONFIRM
2.7 | STARTING SYSTEM
2.7.1 | It shall consists of 24 Volt D.C. electric starter |  |  | VENDER TO SPECIFY
2.7.2 | 24 Volt D.C. battery charging alternator |  |  | VENDER TO SPECIFY
3 | ALTERNATOR
3.1 | Alternator shall be 1500 KVA rating , 11KV at 0.8 PF(lagg), 50HZ, 3 phase 3 wire self excited self regulated with brushless excitation. The alternator shall be confirming to IS : 4722/IEC-34 standard |  |  | VENDER TO SPECIFY
3.2 | Voltage regulation of Alternator shall be : ±1.0% of rated voltage from No. load to Full load |  |  | VENDER TO SPECIFY
3.3 | Voltage adjustment shall be : ±5% of rated voltage |  |  | VENDER TO SPECIFY
3.4 | Alternator encloser : IP 23 |  |  | VENDER TO SPECIFY
3.5 | Alternator insulation : Class 'F' with temperature rise limited to class 'f' insulation limit |  |  | VENDER TO SPECIFY
4 | BASE FRAME
4.1 | Base frame shall be suitable to mount engine and alternator. These shall be coupled and aligned on a comman channel iron fabricated base frame with pre drilled holes. |  |  | VENDER TO CONFIRM
5 | FUEL TANK
5.1 | Daily service fuel tank shall be provided for each set. The size of tank shall be minimum 990 Lit. capacity. |  |  | VENDER TO CONFIRM
5.2 | The tank shall be made from 14 SWG sheet steel metal complete with drain valve, air vent, inlet and out let connections. |  |  | VENDER TO CONFIRM
5.3 | The fuel tank shall be suitable for floor mounting insatallation out side the acoustic enclosure. |  |  | VENDER TO CONFIRM
6 | BATTERIES
6.1 | Suitable battery bank shall be provided for starting the D.G.set. All batteries shaould be supplied in full charged and ready to use condition. |  |  | VENDER TO CONFIRM
6.2 | Battery details to be submitted with offer i.e No. of batteries used in eack set, battery voltage, battery capacity in AH, make of the battery etc. |  |  | VENDER TO CONFIRM
7 | INTEGRATED DG SET CONTROLLER
7.1 | Controller shall be Microprocessor based DG set power command module complatible for remote, monitoring and data logging with operator interface to the Genset, digital voltage regulation through in-built AVR and digital governing. |  |  | VENDER TO CONFIRM
7.2 | Data logger to store data ( running hours, number of start attempt, KWH produced since last reset) |  |  | VENDER TO CONFIRM
7.3 | Digital inbuilt AVR to provide voltage regulation of ±0.5% for any loads between no loads to full load |  |  | VENDER TO CONFIRM
7.4 | Digital Engine speed Governing control to provide isochronous engine speed within ±0.25 % for any steady state load from no load to full load |  |  | VENDER TO CONFIRM
7.5 | Amp sentry protection for true alternator over current protection |  |  | VENDER TO CONFIRM
7.6 | Sensor failure indication |  |  | VENDER TO CONFIRM
7.7 | Compatibility for remote monitoring & data logging |  |  | VENDER TO CONFIRM
7.8 | Smart starting. Integrated fuel ramping to limit black smoke & frequency overshoot in addition to optimise cold weather starting |  |  | VENDER TO CONFIRM
7.9 | Generator set protective function shall be as below:. |  |  | VENDER TO CONFIRM
A | CONTROL
| (i) OFF/Manual/Auto control switch |  |  | VENDER TO CONFIRM
| (ii) Emergency stop |  |  | VENDER TO CONFIRM
| (iii) Manual run/Stop control switch |  |  | VENDER TO CONFIRM
| (iv) Panel lamp / lamp test control switch |  |  | VENDER TO CONFIRM
| (v) Operator adjustment for time delay start/Stop & Alternator Voltage / Frequency |  |  | VENDER TO CONFIRM
B | METERING
B-1 | ENGINE
| (i) Starting Battery Voltage |  |  | VENDER TO CONFIRM
| (ii) Lube oil Pressure |  |  | VENDER TO CONFIRM
| (iii) Engine control Temperature |  |  | VENDER TO CONFIRM
B-2 | ELECTRICAL
| (i) Current |  |  | VENDER TO CONFIRM
| (ii) Voltage |  |  | VENDER TO CONFIRM
| (iii) Frequency |  |  | VENDER TO CONFIRM
| (iv) KW |  |  | VENDER TO CONFIRM
| (v) KWH |  |  | VENDER TO CONFIRM
| (vi) PF |  |  | VENDER TO CONFIRM
| (vii) KVA |  |  | VENDER TO CONFIRM
C | PROTECTION / WARNING
C-1 | ENGINE
| (i)Over speed shutdown |  |  | VENDER TO CONFIRM
| (ii) Low Lube oil pressure warning / shutdown |  |  | VENDER TO CONFIRM
| (iii) High coolent Temperature warning / shutdown |  |  | VENDER TO CONFIRM
| (iv) Low coolent level warning / shutdown |  |  | VENDER TO CONFIRM
| (v) Low coolent temperature warning |  |  | VENDER TO CONFIRM
| (vi) Low & High battery voltage warning |  |  | VENDER TO CONFIRM
| (vii) Weak battery warning |  |  | VENDER TO CONFIRM
| (viii) Bead battery shutdown |  |  | VENDER TO CONFIRM
| (ix) Over Crank (Fail to start) shutdown |  |  | VENDER TO CONFIRM
| (x) Fail to crank shutdown |  |  | VENDER TO CONFIRM
C-2 | ALTERNATOR
| (i) Over current warning/ shutdown |  |  | VENDER TO CONFIRM
| (ii) Short circuit shutdown |  |  | VENDER TO CONFIRM
| (iii) High / low voltage shutdown |  |  | VENDER TO CONFIRM
| (iv) Under / Over frequency shutdown/ warning |  |  | VENDER TO CONFIRM
| (v) Reverse power (KVA & KVAr) shutdown |  |  | VENDER TO CONFIRM
| (vi) Excitation fault (Loss of voltage sensing input to control) shutdoen |  |  | VENDER TO CONFIRM
8 | CONTROL PANELS FOR D.G.SET |  |  | VENDER TO CONFIRM
8.1 | H.T.SWITCHGEAR PANEL |  |  | VENDER TO CONFIRM
A | Genarator panel - 3 Nos. (one each for two sets and one for out going ) |  |  | VENDER TO CONFIRM
i | Each generator incomming panel shall be comprised of 1 number 11 kv, 400 Amp. 26 KA, 3 phase 50HZ, metal clad, fully draw out, vertical isolation, horizontal draw out type, motorised spring charging, 24 volt D.C. closing & tripping coil vacuum circuit breaker complete with 11KV/110 Volt , 100 VA PT, and Duel core 100/5+5, 15 VA, Class -1 /5P CT's for metering/ protection. |  |  | VENDER TO CONFIRM
B | Neutral isolating panel - 2 nos. (one each for two sets) |  |  | VENDER TO CONFIRM
i | Each panel shall be provided with 1 number motorised isolating switch for neutral isolation and 1 set of CT's for differentail protection. |  |  | VENDER TO CONFIRM
C | Neutral grounding resistor panel (1 No.) |  |  | VENDER TO CONFIRM
i | The neutral grounding resistor shall be designed to limit the volt current to full load value. The neutral grounding resistor shall be housed in a cubical and shall be of Stainless steel or Cu/Ni Alloy. The rating of Neutral grounding resistor shall be for 10 second with temperature rise |  |  | VENDER TO CONFIRM
8.2 | GENERATOR MONITORING AND PROTECTION PANEL- (2 NOS.) |  |  | VENDER TO CONFIRM
8.2.1 | Each monitoring panel shall be comprised of the following: |  |  | VENDER TO CONFIRM
8.2.1 (a) | Metering and control |  |  | VENDER TO CONFIRM
i | 1 No. engine start push buttor |  |  | VENDER TO CONFIRM
ii | 1 No. Engine stop push button |  |  | VENDER TO CONFIRM
iii | 1 No. Engine priming pump start push button |  |  | VENDER TO CONFIRM
iv | 1 No. Auto/Mains /Test master selector switch |  |  | VENDER TO CONFIRM
v | 1 No. DOL starter for pre lube oil pump |  |  | VENDER TO CONFIRM
9.2.1(b) | Protection relays |  |  | VENDER TO CONFIRM
i | Over current warning/shutdown |  |  | VENDER TO CONFIRM
ii | Short circuit shutdown |  |  | VENDER TO CONFIRM
iii | High/Low voltage shutdown |  |  | VENDER TO CONFIRM
iv | Under /over frequency shutdown/warning |  |  | VENDER TO CONFIRM
v | Reverse power (KVA& KVAr) shutdown |  |  | VENDER TO CONFIRM
vi | Excitation fault (Loss of voltage sensing (Input to control) shutdown |  |  | VENDER TO CONFIRM
8.2.1( c) | Battery charger |  |  | VENDER TO CONFIRM
i | Battery charger shall comprise of : |  |  | VENDER TO CONFIRM
ii | 1 No. transformer |  |  | VENDER TO CONFIRM
iii | 1 No. rectifier |  |  | VENDER TO CONFIRM
iv | 1 No. DC ammeter |  |  | VENDER TO CONFIRM
v | 1 No. DC voltmeter |  |  | VENDER TO CONFIRM
vi | 1 No. DC ON indication lamp |  |  | VENDER TO CONFIRM
vii | 1 No. Trickle / boost select switch |  |  | VENDER TO CONFIRM
8.3 | AUTO/MANUAL SYNCHRONIZING CONTROL PANEL |  |  | VENDER TO CONFIRM
8.3.1 | 1 No. GCU/PLC based system for Auto start/ stop, Auto load shearing, Auto synchoronizing and load management of 2 Nos. D.G.Sets. |  |  | VENDER TO CONFIRM
9 | ECOSTIC ENCLOSER
9.1 | Suitable ecostic encloser shall be provided in both D.G.Set. Details of encloser to be submitted with the offer. |  |  | VENDER TO SPECIFY
10 | EXHAUST SYSTEM
10.1 | Vertical Exhaust piping system to be provided as per IS norms. |  |  | VENDER TO CONFIRM
10.2 | Necessary support structure to be provided for supporting exhaust piping system |  |  | VENDER TO CONFIRM
10.3 | Necessary SS below s with matching flanges and other accessaries to be provided |  |  | VENDER TO CONFIRM
10.4 | Aviation light & lighting arrestor system to be provided |  |  | VENDER TO CONFIRM
11 | EARTHING SYSTEM
11.1 | Galvanised iron plate earthing of suitable number to be provided for the system earthing, grounding, and lightining arrestor |  |  | VENDER TO CONFIRM
12 | CABLES
12.1 | 3 Core 11 KV grade of suitable rating HT cable along with termination to be provided to connect the Alternator to HT panels |  |  | VENDER TO CONFIRM
12.2 | Suitable rating LT cable along with termination to be provided for D.G.auxilaries and other equipments |  |  | VENDER TO CONFIRM
12.3 | Suitable control cable along with termination to be provided for synchronising panel |  |  | VENDER TO CONFIRM
13 | DOCUMANTATION
13.1 | Following documantation shall be provided with each set: |  |  | VENDER TO CONFIRM
a | Operation and mainenance manual of diesel engine |  |  | VENDER TO CONFIRM
b | Test certificate of diesel engine |  |  | VENDER TO CONFIRM
c | Operation and maintenance of Alternator |  |  | VENDER TO CONFIRM
d | Test certificate of alternator |  |  | VENDER TO CONFIRM
e | Test certificate of D.G.Set |  |  | VENDER TO CONFIRM
14 | SHEDULE OF PRICES FOR 2 X1500 KVA DG SET
14.1 | Prices should be submitted as per annexure -I |  |  | VENDER TO SUBMIT
15 | Qualifying condition
| Only those vender, who have supplied and commissioned at least two Diesel Generating set for similar specification/ application in the past five years and such oven is presently working satisfactorily for more than one year (more than six month if supplied to BHEL) after commissioning should quote. The following information is to be submitted by the vender about the companies where similar Diesel Generating sets have been supplied. This is required from venders for qualifications of their offers. |  |  | VENDER TO SPECIFY
| 1 . Name of the customer / company where similar Diesel Generating set is installed. (copy of purchase order to be furnised) |  |  | VENDER TO SUBMIT
| 2 . Complete postal address of the customer. |  |  | VENDER TO SUBMIT
| 3. Year of suppling / commissioning. |  |  | VENDER TO SUBMIT
| 4 . Application for which Diesel Generating set is supplied with details. |  |  | VENDER TO SUBMIT
| 5 . Name and designation of the contact person of the customer. |  |  | VENDER TO SUBMIT
| 6 . Phone. FAX, no andE-mail address of the contact person of fhe customer. |  |  | VENDER TO SUBMIT
| 7 . Performance certificate from the customer regarding satisfactory performance of Diesel Generating set supplied to them |  |  | VENDER TO SUBMIT
| 8. BHEL reserves the right to verify information submited by vender. In case the information is found to be false/ incorrect, the offer shall be rejected. |  |  | VENDER TO CONFIRM
Prepared by |  | Checked by |  | Approved by
Inder Mathur |  | S.C.Srivastava |  | S.J.Chakraborty | A.K.Srivastava
Manager (WE&S) |  | Sr. Manager (WE&S) |  | DGM (WE&S) | AGM (FW)

## Sheet2
ANNEXURE - I
SCHEDULE OF PRISES FOR 2X 1500 KVA DIESEL GENERATOR SET
S.NO. | DESCRIPTION | QTY | UNIT | UNIT RATE | AMOUNT IN RS.
1 | Supply of 1500 KVA D.G.Set comprising of Engine (Make & Model ) developing required BHP coupled to 1500 KVA , 11KV, (make & model) alternator mounted on a common base frame complete with: | 2 | Set
(a) 990 Lts.,capacity day oil tank
(b) 4 Nos. 12 Volt 180 AH capacity batteries with battery leads
(c ) Integrated D.G.set controller and contral (Specification point No. 2.0 to 7.0)
2 | Supply of incomer HT braker panel (Specificartion point No. 8.1-A) | 2 | Nos
3 | Supply of neutral Isolation panel (Specification point No. 8.1-B) | 2 | Nos
4 | Supply of Neutral grounding resistor panel (1 for 2 nos. D.G.set) (Specification point No. 8.1-C) | 1 | No.
5 | Supply of Generator control panel (Specification Point No. 8.2) | 2 | Nos
6 | Auto synchronization/ auto load shearing panel for 2 D.G.set ( Specification point No. 8.3) | 1 | No.
7 | Supply of ecostic encloser for each D.G.Set (Specification point No. 9.0) | 2 | Nos.
8 | EXHAUST SYSTEM
8.1 | Supply of M.S. black pipe B class (10 Inch), complete with bends & flanges for piping inside the D.G.room | 80 | Meter
8.2 | Supply of thermal insulation with mineral wool 50 mm thich wire mesh and 26 gauge aluminum clading (within the D.G.room) | 80 | Meter
8.3 | Supply of M.S.black pipe A class (14 inch) complete with bends & flanges ( for 30 Meter verical piping) (Specification point No. 10.1) | 240 | Meter
8.4 | Supply of SS belows with matching flanges and other accessories (Specification point No. 10.3) | 8 | Nos.
8.5 | Support structure for exhaust piping (Specification point No. 10.2) | 30000 | Kg.
8.6 | Aviation light & lighting arrestor system (Specification point No. 10.4) | 2 | Nos.
9 | FUEL SYSTEM
9.1 | Supply of M.S.pipe 25/40 mm with bends, flanges, NRV, stainer ETC packing as required from day oil tank to the engine | 60 | Meter
10 | EARTHING SYSTEM (SPECIFICATION POINT NO. 11.0)
10.1 | Galvanised Iron plate earthing | 10 | Nos.
10.2 | GI MS flat size 50x5 mm | 200 | Meter
11 | CABLES (SPECIFICATION POINT NO. 12.0)
11.1 | HT cable 11 KV 3 core of suitable size Aluminium conductor. (for generator to panel) | As required | Meter
11.2 | Termination for above HT cable | 4 | Nos.
11.3 | Supply of LT power cable for termination of DG auxilary with termination, 4 core of suitable rating PVC insulated 1.1 KV grade | As required | Meter
11.4 | Supply of armoured copper control cable with termination 16 core 2.5 sq.mm | As required | Meter
11.5 | Supply of control cable for synchronising panel with termination, 3 core x 1 sq.mm copper conductor shielded cable | As required | Meter
11.6 | Termination box (1 for each D.G.set) | 2 | Nos.
12 | Labour charges for installation & commissioning of DG set | 1 | Job