## Sheet1
BHARAT HEAVY ELECTRICAL LIMITED, JHANSI
|  |  | Specification No. | 9229
|  |  | Item No. | SP/ELEC/9229
|  |  | Location | Bay-9 ( Power Testing )
|  |  | Quantity | 1 No.
SCOPE :
SUPPLY , ERECTION & COMMISSIONING OF 10 MVA MOTOR GENERATOR SET, COMPLYING AS PER SPECIFICATION BELOW
NOTE :
1 | VENDOR must submit complete information against clause No. 16.0 ( Qualifying condition). The offer meeting this clause would only be processed.
2 | The " offered" Column and where applicable, the " Deviations" Column of this format shall be filled in by the Vender and submitted along with the offer.Technical details also submitted with the offer. Inadequate / incomplete, ambiguous, or unsustainable information against any of the clauses of the specification / requirements shall be treated as non - compliance.
3 | The offer and all documents enclosed with offer should be in English language only.
SPECIFICATION CUM COMPLIANCE CERTIFICATE OF 10 MVA MOTOR GENERATOR SET
S.NO. | DESCRIPTION FOR BHEL REQUIREMENT |  |  | SPECIFIED / TO BE CONFIRMED BY | OFFERED | DEVIATIONS
1 | PURPOSE & WORK PIECE MATERIAL:
1.1 | Design, Engineering, Manufacturing, supply , installation, testing and commissioning of 10 MVA Motor Generator set. The set is required for the testing of various tranformers. |  |  | VENDER TO CONFIRM
2 | EQUIPMENT CONFIGURATION :- Motor generator set shall consist of an Motor as prime mover, A.C. Generator, Control panels, Incoming & generator breakers, Transformer, winding change over panel, and other accecessaries. Complete set shall be of an " State of art" latest design & technology. |  |  | VENDER TO CONFIRM
2.1 | MOTOR
2.1.1 | The motor shall be suitable for generator operation. Motor shall be D.C.motor |  |  | VENDER TO CONFIRM
2.1.2 | Following details to be submitted:
2.1.2.1 | Motor rating |  |  | VENDER TO SPECIFY
2.1.2.2 | Motor voltage- |  |  | VENDER TO SPECIFY
2.1.2.3 | Motor speed - 0 to 1000 RPM |  |  | VENDER TO SPECIFY
2.1.2.4 | Class of insulation - F |  |  | VENDER TO SPECIFY
2.1.2.5 | Winding - Shunt compensated |  |  | VENDER TO SPECIFY
2.1.2.6 | Duty - Continious |  |  | VENDER TO SPECIFY
2.1.2.7 | Cooling |  |  | VENDER TO SPECIFY
2.1.2.8 | Noise level |  |  | VENDER TO SPECIFY
2.1.2.9 | Accessories |  |  | VENDER TO SPECIFY
2.2 | MOTOR BREAKER PANEL
2.2.1 | Motor breaker panel shall be suitable for the incoming supply to drive motor. |  |  | VENDER TO CONFIRM
2.2.2 | Following details to be submitted:
2.2.2.1 | Rating |  |  | VENDER TO SPECIFY
2.2.2.2 | Breaking capacity |  |  | VENDER TO SPECIFY
2.2.2.3 | No. of poles - 3 |  |  | VENDER TO SPECIFY
2.2.2.4 | Voltage rating- 11 KV |  |  | VENDER TO SPECIFY
2.2.2.5 | Protection- Over current and earth fault |  |  | VENDER TO SPECIFY
2.2.2.6 | Metering - Voltage and current |  |  | VENDER TO SPECIFY
2.2.2.7 | Accessories - CT's and PT's |  |  | VENDER TO SPECIFY
2.2.2.8 | Cable entry - Bottom |  |  | VENDER TO SPECIFY
2.2.2.9 | Auxilary contacts- 8 NO + 8 NC |  |  | VENDER TO SPECIFY
2.2.2.10 | Shunt trip - 110 Volt DC |  |  | VENDER TO SPECIFY
2.3 | TRANSFORMER
2.3.1 | Suitable transformer shall be provided for the operation of D.C.Motor |  |  | VENDER TO CONFIRM
2.3.2 | Following details to be submitted:
2.3.2.1 | Rating of transformer |  |  | VENDER TO SPECIFY
2.3.2.2 | Primary voltage - 11KV, 50Hz, 3 Phase |  |  | VENDER TO SPECIFY
2.3.2.3 | Secondary voltage |  |  | VENDER TO SPECIFY
2.3.2.4 | Duty |  |  | VENDER TO SPECIFY
2.3.2.5 | Vector group |  |  | VENDER TO SPECIFY
2.3.2.6 | Installation - Out door |  |  | VENDER TO SPECIFY
2.3.2.7 | Accessories |  |  | VENDER TO SPECIFY
2.3.2.8 | Tappings |  |  | VENDER TO SPECIFY
2.3.2.9 | Cooling |  |  | VENDER TO SPECIFY
2.3.2.10 | Termination boxes - both for HT and LT |  |  | VENDER TO SPECIFY
2.4 | D.C.DRIVE
2.4.1 | Suitable D.C.drive shall be provided |  |  | VENDER TO CONFIRM
3.4.2 | Following details to be submitted:
2.4.2.1 | Rated current |  |  | VENDER TO SPECIFY
2.4.2.2 | Rated in put voltage |  |  | VENDER TO SPECIFY
2.4.2.3 | Rated output voltage |  |  | VENDER TO SPECIFY
2.4.2.4 | Range of speed control |  |  | VENDER TO SPECIFY
2.4.2.5 | Direction of rotation |  |  | VENDER TO SPECIFY
2.4.2.6 | Bridge configuration |  |  | VENDER TO SPECIFY
2.4.2.7 | Control system |  |  | VENDER TO SPECIFY
2.4.2.8 | Field control |  |  | VENDER TO SPECIFY
2.4.2.9 | Cooling of converters |  |  | VENDER TO CONFIRM
2.4.2.10 | Provision of local & remote control to be provided |  |  | VENDER TO CONFIRM
3 | A.C. GENERATOR
3.1 | 10 MVA rating 3 phase, 50 Hz A.C. generator shall be provided |  |  | VENDER TO CONFIRM
3.1.1 | Following details to be submitted:
3.1.1.1 | Rating of A.C.Generator - 10MVA 3 Phase |  |  | VENDER TO SPECIFY
3.1.1.2 | Rated voltage - 0- 11 KV |  |  | VENDER TO SPECIFY
3.1.1.3 | Frequency - 50 HZ |  |  | VENDER TO SPECIFY
3.1.1.4 | Rated speed - 1000 RPM |  |  | VENDER TO SPECIFY
3.1.1.5 | Rated current |  |  | VENDER TO SPECIFY
3.1.1.6 | Power factor |  |  | VENDER TO SPECIFY
3.1.1.7 | No. of poles |  |  | VENDER TO SPECIFY
3.1.1.8 | Excitor |  |  | VENDER TO SPECIFY
3.1.1.9 | Excitation |  |  | VENDER TO SPECIFY
3.1.1.10 | Insulation |  |  | VENDER TO SPECIFY
3.1.1.11 | Duty - Continuous |  |  | VENDER TO SPECIFY
3.1.1.12 | Cooling |  |  | VENDER TO SPECIFY
3.1.1.13 | Bearing - Type , Cooling etc |  |  | VENDER TO SPECIFY
3.1.1.14 | Accessories
3.2 | EXCITATION CONTROL PANEL
3.2.1 | Suitable excitation panel for A.C. generator shall be provided to obtain variable output from Generator (0 - 11KV) |  |  | VENDER TO CONFIRM
3.2.2 | Following details to be submitted:
3.2.2.1 | Mounting of panel- on Floor |  |  | VENDER TO SPECIFY
3.2.2.2 | Control provide in the panel (brief descrption to be provided) |  |  | VENDER TO SPECIFY
3.2.2.3 | Inpurt supply - 240 Volt A.C. single phase available |  |  | VENDER TO CONFIRM
3.2.2.4 | Rating of excitation controller |  |  | VENDER TO SPECIFY
3.2.2.5 | Protection |  |  | VENDER TO SPECIFY
3.2.2.6 | Local and remote control - Required |  |  | VENDER TO SPECIFY
3.2.2.7 | Accessories |  |  | VENDER TO SPECIFY
3.3 | GENERATOR BREAKER PANEL
3.3.1 | Generator breaker panel shall be provided suitable for the outgoing supply |  |  | VENDER TO CONFIRM
3.3.2 | Following details to be submitted:
3.3.2.1 | Rating |  |  | VENDER TO SPECIFY
3.3.2.2 | Breaking capacity |  |  | VENDER TO SPECIFY
3.3.2.3 | No. of poles - 3 |  |  | VENDER TO CONFIRM
3.3.2.4 | Voltage rating- 11 KV |  |  | VENDER TO SPECIFY
3.3.2.5 | Protection- Over current and earth fault |  |  | VENDER TO SPECIFY
3.3.2.6 | Metering - Voltage and current |  |  | VENDER TO SPECIFY
3.3.2.7 | Accessories - CT's and PT's |  |  | VENDER TO SPECIFY
3.3.2.8 | Cable entry - Bottom |  |  | VENDER TO CONFIRM
3.3.2.9 | Auxilary contacts- 8 NO + 8 NC |  |  | VENDER TO CONFIRM
3.3.2.10 | Shunt trip - 110 Volt DC |  |  | VENDER TO CONFIRM
4 | WINDING CHANGE OVER PANEL
4.1 | Suitable winding change over panel is required to select the winding of A.C.Generator |  |  | VENDER TO CONFIRM
4.2 | Winding selection shall be star- series, star- parallel, Delta - Parallel, Delta - series connection |  |  | VENDER TO CONFIRM
4.3 | Details of change over panel to be submitted |  |  | VENDER TO SPECIFY
5 | CABLES
5.1 | All veriety of power and control cable shall be provided for the suitable length of minimum 100 meter, Details of cable to be submitted |  |  | VENDER TO SPECIFY
6 | SAFETY ARRANGEMENTS:
6.1 | Following safety features in addition to other standard safety features should be provided on the generator |  |  | VENDER TO CONFIRM
6.2 | Generator should have adequate and reliable safety interlocks/ devices to avoid damage to the generator, work piece and the operator due to the malfunctioning or mistakes. Generator functions should be continuously monitored and alarm/warning indications through lights/ alarm number with messages ( on panels ) should be available . |  |  | VENDER TO CONFIRM
6.3 | All the pipes. Cables etc . On the generator should be well supported and protected . |  |  | VENDER TO CONFIRM
6.4 | All the rotating parts used on generator should be statically & dynamically balanced to avoid undue vibrations . |  |  | VENDER TO CONFIRM
6.5 | ELCB/ Earth foult relay to be provided in the the circuit to protect the equipment for Earth fault. |  |  | VENDER TO CONFIRM
6.6 | Emergency Switches at suitable locations as per International Norms are to be provided. |  |  | VENDER TO CONFIRM
7 | ENVIRONMENTAL PERFORMANCE TO THE MACHINE :
7.1 | The Generator shall conform to following factors related to environment : |  |  | VENDER TO CONFIRM
7.2 | Maximum noise level shall be 85 dB (A) at normal load condition, this will be measured as per international standards like DIN 45635-16. Supplier to demonstrate compliance to noise level . if so required. |  |  | VENDER TO CONFIRM
7.3 | If any safety / environmental protection enclosure is required it should be built in the machine/ generator by the vendor |  |  | VENDER TO CONFIRM
7.4 | Paint of the machine/ generator should be oil / coolant resistant and should not peel off. |  |  | VENDER TO CONFIRM
8 | LEVELLING & ANCHORING SYSTEM
8.1 | Complete anchoring system including foundation bolts, anchoring materials, fixators, leveling shoes etc, shall be supplied for the Machine/ generator . |  |  | VENDER TO CONFIRM
9 | TOOLS FOR ERECTION, OPERATION & MAINTENANCE :
9.1 | Special tools and equipment required for erection of the machine/ generator shall be brought by the vendor. Necessary tools like Torque Wrench, Spanners, Keys, grease guns etc for operation and maintenance of the machine should be supplied. List of such tools should be submitted with offer . |  |  | VENDER TO CONFIRM
10 | SPARES :
10.1 | Itemised break - up of mechanical, hydraulic, electrical and electronic spares used on the machine/generator in sufficient quantity as per recommendation of Vendor for 2 years of trouble free operation on three shifts continuous running basis should be offered by vender. The list to include following, in addition to other recommended spares :( Unit Price of each item of spare should be offered ) |  |  | VENDER TO CONFIRM
11 | DOCUMENTATION : Five sets of following documents ( hard copies) in English language should be supplied along with the machine. |  |  | VENDER TO CONFIRM
11.1 | Operating manual of machine |  |  | VENDER TO CONFIRM
11.2 | Programming manuals of machine |  |  | VENDER TO CONFIRM
11.3 | Detailed maintenance manual of machine with all drawings of machine assemblies / sub assemblies / parts including electrical/ pneumatic / hydraulic circuit diagrams. All assemblies / sub- assemblies drawings shall be supplied with the part list also. |  |  | VENDER TO CONFIRM
11.4 | Catalogues , O&M manuals of all bought out items including drawings where ever applicable in english lenguage. |  |  | VENDER TO CONFIRM
12 | TRAINING
12.1 | BHEL persons should be trained at supplier works for mutually agreed period in the area of a - Mechanical, Electrical and electronic maintenance for machine and other supplied equipments b- Operator for machine operation |  |  | VENDER TO CONFIRM
13 | FOUNDATION
13.1 | vendor shall submit the preliminary layout drawing for getting BHEL"s approval within one month from the date of Letter of Intent ( LOI)/P.O. , whichever is earlier . Soil condition data will be furnished by BHEL along with the approval. Complete foundation Design including details, like Static/Dynamic load details etc . and final layout Drawings shall be submitted by the supplier within one month after getting BHEL"s approval . The Layout should consist of all requirements pertaining to complete machine and all accessories including space requirement. BHEL shall construct complete foundation for machine & supplier shall check & approve the same before erection. Vendor should arrange equipment required for the testing of foundation, if required. The vendor shall also indicate detailed specifications of grouting compound and grouting procedure etc. for foundation bolts of the machine. |  |  | VENDER TO CONFIRM
14 | ERECTION & COMMISSIONING
14.1 | Supplier to take full responsibility for carrying out the erection, start up , testing of machine/generator, it's control system & all types of other supplied equipment, machining of test pieces etc. Service requirement like power, air & water shall be provided by BHEL at only one point to be indicated by supplier in their foundation/ layout drawings . Other requirements like crane, lifting tackles etc. shall also be provided by BHEL if availabe. Details of these requirements should be informed by vendor in advance. |  |  | VENDER TO CONFIRM
14.2 | The M.G.set is to be installed on our prepared foundation, details of which will be furnished by manufacturer. |  |  | VENDER TO CONFIRM
14.3 | The offer should include the charges for complete transportation, erection and commissioning of the M.G.Set and auxilary equipments with duration. Your commissioning engineer's services should also be available at site for setting all controls while demonstrating the working of the M.G.set.
15 | MISCELLANEOUS
15.1 | The offer should be descriptive and complete. Details of all equipments and accessories with general arrangement drawings and catalogues to be enclosed with the offer. Offer with out complete details are liable to be rejected. |  |  | VENDER TO CONFIRM
15.2 | Firm should give breakup prices of all major items and activities. |  |  | VENDER TO CONFIRM
16 | QUALIFYING CONDITIONS
16.1 | Only those vender, who have supplied and commissioned at least two numbers M.G.Set of 500 KVA or higher capacity in past ten years and such M./G.Sets are presently working satisfactorily for more than one year (more than six month if supplied to BHEL) after commissioning should quote. The following information is to be submitted by the vender about the companies where similar M.G.Sets have been supplied. This is required from venders for qualifications of their offers. |  |  | VENDER TO CONFIRM
| 1 . Name of the customer / company where similar M.G.Set is installed. (copy of purchase order to be furnised) |  |  | VENDER TO SPECIFY
| 2 . Complete postal address of the customer. |  |  | VENDER TO SPECIFY
| 3. Year of suppling / commissioning. |  |  | VENDER TO SPECIFY
| 4 . Application for which M.G.Set is supplied with details of accuracies achived on the job. |  |  | VENDER TO SPECIFY
| 5 . Name and designation of the contact person of the customer. |  |  | VENDER TO SPECIFY
| 6 . Phone. FAX, no andE-mail address of the contact person of fhe customer. |  |  | VENDER TO SPECIFY
| 7 . Performance certificate from the customer regarding satisfactory performance of M.G.Set supplied to them |  |  | VENDER TO SPECIFY
| 8. BHEL reserves the right to verify information submited by vender. In case the information is found to be false/ incorrect, the offer shall be rejected. |  |  | VENDER TO SPECIFY
Prepared by |  |  | Checked by |  | Approved by
Kaushik Dey |  | Inder Mathur | B. Bhadra | SJC | AKS | PKJ
Dy. Mgr. (Test) |  | Mgr. (WE&S) | DGM (Test) | DGM (WE&S) | AGM (FW) | AGM (CQX)