## Sheet1
BHARAT HEAVY ELECTRICAL LIMITED, JHANSI
|  |  | Specification No. | 10574
|  |  | Item No. | LE-1/7/6280, 6281, 6282, 6283, 6284, 6285,6286, 6287
|  |  | Location | Transformer block
|  |  | Quantity | 8 Nos.
SPECIFICATION CUM COMPLIANCE CERTIFICATE OF MOTORISED SLIDING DOOR
NOTE :
1 | VENDOR must submit complete information against clause No. 13 ( Qualifying condition). The offer meeting this clause would only be processed.
2 | The " offered" Column and where applicable, the " Deviations" Column of this format shall be filled in by the Vender and submitted along with the offer.Technical details also submitted with the offer. Inadequate / incomplete, ambiguous, or unsustainable information against any of the clauses of the specification / requirements shall be treated as non - compliance.
3 | The offer and all documents enclosed with offer should be in English language only.
SCOPE :
SUPPLY , ERECTION & COMMISSIONING OF MOTORISED SLIDING DOORS AS PER SPECIFICATION BELOW
S.NO. | DESCRIPTION FOR BHEL REQUIREMENT |  | SPECIFIED / TO BE CONFIRMED BY | OFFERED | DEVIATIONS
1 | PURPOSE & WORK PIECE MATERIAL:
1.1 | Electrically operated motorised Sliding doors are required for opening and closing of shop entrance. |  | VENDER TO CONFIRM
2 | SPECIFICATION
2.1 | Size of door - Width - 6000 mm x Height - 6250 mm |  | VENDER TO CONFIRM
2.2 | No. of segments - Two |  | VENDER TO CONFIRM
2.3 | Segment size - Width 3000 mm x 6250 mm Height |  | VENDER TO CONFIRM
2.4 | Service door size- Width - 750 mm x 2000 mm Height |  | VENDER TO CONFIRM
2.5 | Motor rating in KW : Minimum 1 KW |  | VENDER TO CONFIRM
3 | CONSTRUCTION
3.1 | Electrically operated motorised Sliding doors shall made in two segment of App. 3000 mm width x 6250 mm height. |  | VENDER TO CONFIRM
3.2 | Each segment shall slide side -wise on a set of roolers provided at the top of the doors. |  | VENDER TO CONFIRM
3.3 | At the booto side of the door a guide shall be provided for the smooth movement |  | VENDER TO CONFIRM
3.4 | The movement of the doors at top will be done in a specially designed beam capable of bearing the load of the doors. This beam will be mounted on two fabricated pillars provide with the system. |  | VENDER TO CONFIRM
3.5 | The main gate shall be fabricated form M.S Sq. pipe and M.S sheets specially bend in ‘U’ shape to give extra strength to the gate and withstand wind pressure. |  | VENDER TO CONFIRM
3.6 | A service door of size 750 mm x 2000 mm shall be provided in one segment of the door per set. |  | VENDER TO CONFIRM
4 | DOOR MOVEMENT
4.1 | The door movement system shall consist of an A.C.motor coupled to the gear box. |  | VENDER TO CONFIRM
4.2 | The sliding movement of the gate shall be effected by suitable capacity of motor coupled to the gearbox. (Minimum 1 KW motor) |  | VENDER TO CONFIRM
4.3 | Make of the motor shall be NGEF/ABB/Crompton/Alstom only. Other make is not acceptable. |  | VENDER TO CONFIRM
4.4 | Make of the gear box shall be Greaves / Shanti/ Elecon only. Other make gear boxes are not acceptable. |  | VENDER TO CONFIRM
4.5 | Fail safe electro magnetic / Electro hydraulic thruster brake shall be provided on the gear box shaft. |  | VENDER TO CONFIRM
4.6 | Provision shall be made for manual release of brake , if needed. |  | VENDER TO CONFIRM
4.7 | For the movement of door motorised winch should be mounted on ground or at the accessible height. |  | VENDER TO CONFIRM
5 | ELECTRICAL SYSTEM
5.1 | The electrical system shall consists of control panel, cable, cable movement system etc. |  | VENDER TO CONFIRM
5.2 | The system shall includes protection against over current, short circuit, earth fault, phase failure protection etc. |  | VENDER TO CONFIRM
5.3 | Doors shall be operated with start/stop (ON/OFF), forward / reverse push buttons. An emergency push buuton shall also be provided for stopping the doors in emergency. |  | VENDER TO CONFIRM
6 | LIMIT SWITCH
6.1 | Lever type limit switches shall be provided to on both side of door to stop the over travel. |  | VENDER TO CONFIRM
7 | ELECTRICAL SYSTEM :-
7.1 | 415+10%-10%,50HZ+/-3%,3 phase AC (4 wire system with earthed) power Suppply Source will be provided by BHEL at a singal point. |  | VENDER TO CONFIRM
7.2 | Tropicalisation : All electrical / electronic equipement shall be tropicalized. |  | VENDER TO CONFIRM
7.3 | All elecrical & electronic control cabinets & panels should be dust and vermin proof. |  | VENDER TO CONFIRM
7.5 | All electrical components in the cabinets should be mounted on DIN rail. |  | VENDER TO CONFIRM
8 | DOCUMENTATION : Three sets of following document (Hard copies) in English language should be supplied along with the system. |  | VENDER TO CONFIRM
8.1 | Operating and maintenance manuals |  | VENDER TO CONFIRM
8.2 | Detailed Maintenance manual of the system with all drawing of assemblies/sub-assemblies/parts including Electrical / diagrams. All Assembly /sub Assembly Drawing shall be supplied with the part list also. |  | VENDER TO CONFIRM
8.3 | Catalogues, O& M Manual of all bought out items including drawing. Wherever applicable. |  | VENDER TO CONFIRM
9 | ERECTION & COMMISSIONING
9.1 | Vender to take full responsibility for carring out the erection, start up,.testing of system, its control system & all type of other supplied equipement. Power, air & water shall be provided by BHEL at only one point to be indicated by supplior. Other reqirment like crane, Trolley shall also be provide by BHEL if available at site. Details of the requirements should be informed by VENDOR in advance. |  | VENDER TO CONFIRM
9.2 | Successful proving of BHEL specified service requirements by supplier shall be considered as part of commissioning. |  | VENDER TO CONFIRM
9.3 | Tools, Tackles, instruments and other necessary equipments, required to carry out all above activties should be brought by the vender. |  | VENDER TO CONFIRM
9.4 | Commissioning spares required for commissoning of the system within stipulated time shall be brought by the vender on returnable basis. |  | VENDER TO CONFIRM
9.5 | Portion, if any of the system, accessories and other supplied item where paints has rubbed off or peeled during transit or erection should be repainted and merged with the original surrounding paints by the VENDOR for this purpose the VENDOR should supply sufficient quantity of touch -up paint. |  | VENDER TO CONFIRM
9.6 | Schedule of Erecion and commissioning shall be submitted with the offer. |  | VENDER TO CONFIRM
9.7 | No manpower shall be provided by BHEL, Vendor shall make his own arrangement. |  | VENDER TO CONFIRM
10 | AMBIENT CONDITIONS & THERMAL STABILITY:
10.1 | Total system including all supplied items should work trouble free and efficiently under following operating conditions to achive specified accuracies, power supply: voltage -- 415 v- 10% + 10% Frequency -- 50 HZ +1.5HZ. -1.5 hz No .of phases -- 3 Ambient conditions -- Temperature = 5 to 50 degree celsius |  | VENDER TO CONFIRM
10.2 | Weather conditions are tropical. Atmosphere may be dust laden during some part of the year . System shall be kept in the normal shop floor conditions. Max temperature variation is 25 deg celsius in 24 hours. (VENDOR to confirm that system is suitable for above and details of provision on the system for the same are to be furnished by VENDOR) |  | VENDER TO CONFIRM
11 | GUARANTEE:
11.1 | 24 months from the date of acceptance of the door. |  | VENDER TO CONFIRM
12 | GENERAL :The VENDOR should submit the following information:
12.1 | Total connected load (KVA) |  | VENDER TO SPECIFY
12.2 | Floor area requred (Langth, width,HEIGHT) for complete system & accessories. |  | VENDER TO SPECIFY
12.3 | Total Weight of the system |  | VENDER TO SPECIFY
12.4 | First fill of hydraulic oil/gear oil /etc to be supplied by vender |  | VENDER TO CONFIRM
13 | QUALIFYING CONDITION
13.1 | Only those venders, who have supplied and commissioned at least Two motorised doors of similar or higher size in the past ten year and such door is presently working satisfactrily for more than one year (more then six months if supplied to BHEL) after commissioning should quote. Documentary support pertaining to following points shall submitted with the offer to justify the claim of qualification: |  | VENDER TO CONFIRM
| 1 . Name of the customer / company where similar door is installed. (copy of purchase order to be furnised) |  | VENDER TO SPECIFY
| 2 . Complete postal address of the customer. |  | VENDER TO SPECIFY
| 3. Year of suppling / commissioning. |  | VENDER TO SPECIFY
| 4 . Name and designation of the contact person of the customer. |  | VENDER TO SPECIFY
| 5. Phone. FAX, no and E-mail address of the contact person of fhe customer. |  | VENDER TO SPECIFY
| 7. Performance certificate (if posible) from the customer regarding satisfactory performance of door supplied to them. |  | VENDER TO SPECIFY
Prepared by |  | Checked by | Approved by
Inder Mathur |  | S.J.Chakraborty | A.K.Srivastava |  | V.K.Agarwal
Manager (WE&S) |  | DGM (WE&S) | AGM (FW) |  | AGM (TRM/TRP)