## Sheet1
BHARAT HEAVY ELECTRICAL LIMITED, JHANSI
|  |  | Specification No. | SP/9984
|  |  | Item No. | SP/MISC/9984
|  |  | Location | NEW WINDING SHOP
|  |  | Quantity | 1 SET
SCOPE :
Design, Supply, Erection & Commissioning of Air Conditioning system for New Transformer winding shop Complying with Specifications as Below
NOTE :
1 | VENDOR must submit complete information against clause No. 8.0 ( Qualifying condition). The offer meeting this clause would only be processed.
2 | The " offered" Column and where applicable, the " Deviations" Column of this format shall be filled in by the Vender and submitted along with the offer.Technical details also submitted with the offer. Inadequate / incomplete, ambiguous, or unsustainable information against any of the clauses of the specification / requirements shall be treated as non - compliance.
3 | The offer and all documents enclosed with offer should be in English language only.
Specification Cum Compliance Certificate of Air Conditioning system for New Transformer winding shop
S.NO. | DESCRIPTION FOR BHEL REQUIREMENT |  |  | SPECIFIED / TO BE CONFIRMED BY | OFFERED | DEVIATIONS
1 | GENERAL
1.1 | These special requirements are intended to amplify the General Conditions of Contract and shall be read in conjunction with them. In case of any discrepancy between the General Conditions of Contract and these special requirements, the most stringent shall apply. |  |  | VENDER TO CONFIRM
2 | SCOPE OF WORK
2.1 | The Scope of Work shall include supplying, installing, testing and commissioning of air conditioning system as described in the Technical Specifications. The vender shall carry out and complete in every respect all work under this contract in conformity with the contract documents and to the entire satisfaction of the Owner. |  |  | VENDER TO CONFIRM
2.2 | All items of work shall be executed strictly to fulfill the requirements laid down under the Basis of Design. The type of equipment, material specifications, method of installation and testing and type of controls shall be in accordance with the Technical Specifications, the approved shop drawings and the relevant Indian Standards. |  |  | VENDER TO CONFIRM
2.3 | The Scope of Work shall include all materials, labour, equipment, appliances and incidental work, whether specifically mentioned or not, but are necessary and customary to make a complete installation. It shall include all fittings, accessories, hardware, foundation bolts, terminal lugs, cable glands, junction boxes and other items, whether specifically mentioned or not, but are useful and necessary for proper and efficient working of the equipment. |  |  | VENDER TO CONFIRM
2.4 | The Scope of Work shall broadly include the following:
2.4.1 | Air Cooled Screw Type Water Chilling Units |  |  | VENDER TO CONFIRM
2.4.2 | Water Circulation Pumps |  |  | VENDER TO CONFIRM
2.4.3 | Air Handling Units |  |  | VENDER TO CONFIRM
2.4.4 | Air Cooling Units or alternatively, Floor-mounted Vertical Split AC Units |  |  | VENDER TO CONFIRM
2.4.5 | Exhaust Fans |  |  | VENDER TO CONFIRM
2.4.6 | Automatic Controls |  |  | VENDER TO CONFIRM
2.4.7 | Sheet Metal Work |  |  | VENDER TO CONFIRM
2.4.8 | Pipe Work |  |  | VENDER TO CONFIRM
2.4.9 | Thermal and Acoustic Insulation Work |  |  | VENDER TO CONFIRM
2.4.10 | False cealing work |  |  | VENDER TO CONFIRM
2.4.11 | Electrical Work |  |  | VENDER TO CONFIRM
2.4.12 | Vibration Isolation and Sound Attenuation. |  |  | VENDER TO CONFIRM
2.4.13 | Surface Painting. |  |  | VENDER TO CONFIRM
2.4.14 | Commissioning, Balancing and Performance Testing. |  |  | VENDER TO CONFIRM
2.4.15 | Shop Drawings Before Installation and As Built Drawings After Installation. |  |  | VENDER TO CONFIRM
2.4.16 | Test Reports, Lists of Spares and Operation and Maintenance Manuals. |  |  | VENDER TO CONFIRM
2.4.17 | On Site Training of Owner’s Personnel. |  |  | VENDER TO CONFIRM
2.4.18 | Maintenance During Defects Liability Period. |  |  | VENDER TO CONFIRM
2.5 | Site Visit Before Bidding
2.5.1 | The bidder shall visit site to study the site conditions and availability of resources at site before submitting the bid.
2.6 | Performance Guarantee
2.6.1 | The contractor shall guarantee the performance of all equipment and the efficiency of the air conditioning and pressurization systems as a whole to achieve the desired results. |  |  | VENDER TO CONFIRM
2.7 | Vibration Isolation and Sound Attenuation
2.7.1 | The equipment shall operate under all conditions of load without any objectionable vibration and noise. The contractor shall take the necessary precautions for vibration isolation and sound attenuation. |  |  | VENDER TO CONFIRM
2.7.2 | The noise inside the conditioned spaces with all equipment operating shall not exceed the following levels: |  |  | VENDER TO CONFIRM
2.7.3 | 65 dBA in external areas at a distance of 5 m from building line. |  |  | VENDER TO CONFIRM
2.8 | Shop Drawings Before Installation and As-Built Drawings After Installation
2.8.1 | The contractor shall prepare and submit for approval his shop drawings based on actual measurement at site. The shop drawings shall broadly cover the following drawings: |  |  | VENDER TO CONFIRM
2.8.2 | Equipment Layout giving complete details of all equipment. |  |  | VENDER TO CONFIRM
2.8.3 | Duct Layout showing all sizes, air quantities, air outlet/ intake details, damper locations and fabrication and support details. |  |  | VENDER TO CONFIRM
2.8.4 | Pipe Layout showing all sizes, water quantities, valve sizes, locations and fabrication and support details. |  |  | VENDER TO CONFIRM
2.8.5 | Electrical drawings showing schematic control and power wiring diagrams, cable sizes, switch details, fuse sizes, control components and wiring details. |  |  | VENDER TO CONFIRM
2.8.6 | Civil foundation details for all equipment. |  |  | VENDER TO CONFIRM
2.8.7 | The contractor shall verify adequacy of sizes of shafts, openings, clearances, etc. and shall co-ordinate with other contractors. Anomaly, if any, may be brought to the notice of the Engineer – in – Charge. He shall also co-ordinate his layouts with other disciplines of work. |  |  | VENDER TO CONFIRM
2.8.8 | After the completion of installation, the contractor shall prepare as-built drawings incorporating all the changes made in locations, routing, dimensions, levels, etc. during execution of the project. |  |  | VENDER TO CONFIRM
2.9 | Surface Painting
2.9.1 | All equipment shall be factory finished with epoxy paint before dispatch. If the shop paint gets damaged or marred during shipment and installation, the affected surface shall be cleaned with mineral spirit, wire brushed, spot primed and then coated with epoxy paint to match the finish over the adjoining shop painted surfaces. |  |  | VENDER TO CONFIRM
2.1 | Commissioning, Balancing and Performance Testing
2.10.1 | The commissioning of the air conditioning systems shall be carried out under the supervision of an experienced commissioning engineer. |  |  | VENDER TO CONFIRM
2.10.2 | The air conditioning systems shall be tested for their performance during peak summer and monsoon. The performance test shall be for ten hours on seven consecutive days in each season. All tests shall be carried out in the presence of the Owner’s representative. |  |  | VENDER TO CONFIRM
2.10.3 | The contractor shall rectify at his cost any defects in materials and/ or workmanship detected in the course of performance testing. The installation shall be tested again after the defects are rectified. |  |  | VENDER TO CONFIRM
2.10.4 | The contractor shall arrange at his cost all equipment, materials, instruments, appliances, tools, consumables and labour necessary for commissioning, balancing and testing. |  |  | VENDER TO CONFIRM
2.11 | Test Reports
2.11.1 | The results of the performance tests during summer and monsoon shall be submitted for scrutiny and approval. The test reports shall include record of all safety and automatic control settings for the entire installation. |  |  | VENDER TO CONFIRM
2.11.2 | The contractor shall also submit along with the test reports, the manufacturers’ certified performance data/ curves for all equipment highlighting the operational parameters for the project. |  |  | VENDER TO CONFIRM
2.12 | Operation and Maintenance Manuals
2.12.1 | On completion of the work but before handing over the air conditioning and pressurization to the Owner, the contractor shall submit three ring-bound copies of operation and maintenance manual. The manual shall include following: |  |  | VENDER TO CONFIRM
2.12.2 | A list of all equipment giving full details such as model numbers, part numbers, serial numbers, names and addresses of the manufacturers, etc. |  |  | VENDER TO CONFIRM
2.12.3 | Start up operation and maintenance instructions for the entire installation. |  |  | VENDER TO CONFIRM
2.12.4 | Step-by-step routine, periodical and breakdown maintenance procedure for all equipment. |  |  | VENDER TO CONFIRM
2.12.5 | Exploded view of all equipment detailing spare parts. |  |  | VENDER TO CONFIRM
2.13 | Availability of Spares and Services During the Life of the Machines
2.13.1 | The contractor shall furnish an undertaking that he shall make available all spares, consumables and services required for proper operation and maintenance of the air conditioning and pressurization systems for a minimum period of 10 years. |  |  | VENDER TO CONFIRM
2.14 | On Site Training of Owner’s Personnel
2.14.1 | On completion of the work but before handing over the air conditioning and pressurization systems to the Owner, the contractor shall train the Owner’s operation and maintenance staff to operate, adjust and maintain all equipment installed. |  |  | VENDER TO CONFIRM
2.15 | Completion Period
2.15.1 | The entire work covered under this contract shall be completed within four months from the date of the Letter of Award. If the work is delayed due to any cause over which the contractor has no control, then the Owner may, at the request of the contractor can extend the completion period by a reasonable time. |  |  | VENDER TO CONFIRM
2.16 | Warranty
2.16.1 | The air conditioning shall carry a warranty forTwenty Four months from the date of handing them over to the Owner against any defective materials, unsuitable product design and bad workmanship. Any shortcomings found during this warranty period shall be made good and defective materials shall be repaired/ replaced at site free of cost. |  |  | VENDER TO CONFIRM
2.17 | Maintenance Due to Defects During Liability Period
2.17.1 | The contractor shall receive service calls for any and all problems experienced in the operation of the air conditioning during defects liability period, which shall extend to twelve months from the date of handing over the installation to the Owner. |  |  | VENDER TO CONFIRM
2.17.2 | The contractor shall attend to these calls within 24 hours of receiving the complaints and take immediate steps to correct any deficiencies that may exist. |  |  | VENDER TO CONFIRM
2.17.3 | All equipment requiring repairs shall be immediately serviced and repaired. The contractor shall supply all replacement parts and labour at his cost. |  |  | VENDER TO CONFIRM
2.18 | Price
2.18.1 | The rates quoted shall remain firm and shall not be subjected to escalation. |  |  | VENDER TO SPECIFY
2.18.2 | The supply rate for each item of work in the Schedule of Quantities shall, unless otherwise expressly stated, include cost of all materials, packing, forwarding, loading, transporting to site, transit insurance and unloading at site. |  |  | VENDER TO SPECIFY
2.18.3 | The labour rate for each item of work in the Schedule of Quantities shall, unless otherwise expressly stated, include cost of fixing materials, appliances, tools and tackles including crane and scaffolding, handling, hoisting, setting, fitting, fixing in position and protecting plant and equipment, disposal of debris and all labour and other incidental items required in preparation for and in full and entire execution of the work called for in each item in accordance with these documents, general trade practices and recognized principles. |  |  | VENDER TO SPECIFY
2.18.4 | All statutory rates, taxes and duties of whatever nature including but not limited to excise duty, customs duty, value added tax, sales tax, turn over tax, octroi, works contract tax, service tax, etc. shall be indicated separately. |  |  | VENDER TO SPECIFY
2.18.5 | For price evaluation, total supply and labour value of the complete project, on TURNKEY basis will be considered. For any alternatives proposed by the firms will be analyzed and finalized after technical scrutiny, on technical case-to-case basis. |  |  | VENDER TO SPECIFY
3 | SYSTEM DESCRIPTION
3.1 | General
3.1.1 | Bharat Heavy Electricals Limited is creating additional capacity for transformer manufacturing in the form of New Winding shop at Jhansi. The new production winding shop will be of size 150 m x 24 m, which shall be air conditioned. the desired temperature and humidity conditions are to be maintained up to shop height. |  |  | VENDER TO CONFIRM
3.2 | Air Conditioning System
3.2.1 | The air conditioning system for New winding shop shall comprise suitable air cooled screw type water chilling units to air-condition space. These water chilling units along with their chilled water circulation pumps shall be located on the terrace of the air handling unit room or shall be given by the vender. |  |  | VENDER TO CONFIRM
3.2.2 | The air conditioned shop shall have two suitable capacity air handling units of sufficient capacity, housed in required located AHU rooms. |  |  | VENDER TO CONFIRM
3.2.3 | The conditioned air from the air handling units shall be carried through suitable supply air ducts and supply air grills discharged between the height from 4 m to 5 m. The return air shall be carried back to the air handling units through suitable return air ducts and return air grills located below 3 m from the floor-level. |  |  | VENDER TO CONFIRM
3.2.4 | The condensed water from the air handling units shall be discharged into the floor drains nearby. |  |  | VENDER TO CONFIRM
3.2.5 | The supply and return air sheet metal duct work shall have thermal insulation to reduce heat gain. The initial portions of the supply air ducts shall have acoustic insulation to reduce noise carry over. All chilled water pipe work shall have thermal insulation to reduce heat gain. All insulation exposed to atmosphere shall have weatherproof covering to prevent water ingress. |  |  | VENDER TO CONFIRM
3.2.6 | All rotating equipment shall be mounted on vibration isolation pads and all pipe and duct connections to the rotating equipment shall be through flexible connectors to prevent vibrations from being transmitted through the building structure. |  |  | VENDER TO CONFIRM
3.3 | Effect of Increased Areas
3.3.1 | Vender have to explicitly indicate the effect of lower capacity AC plant in winding shop for performance evaluation. |  |  | VENDER TO SPECIFY
3.4 | BASIS OF DESIGN
3.4.1 | The air conditioning system for New winding shop shall be designed on the basis of following parameters:
3.4.2 | Ambient conditions: 43.5O to 48°C DBT/ 24.4O C WBT |  |  | VENDER TO CONFIRM
3.4.3 | Inside conditions: 24O + 1O C DBT & RH below 60% |  |  | VENDER TO CONFIRM
3.4.4 | Chilled water return temperature: 12O C |  |  | VENDER TO CONFIRM
3.4.5 | Chilled water supply temperature: 7O C |  |  | VENDER TO CONFIRM
3.4.6 | Floor area: 150M x 24M (3600 M2) |  |  | VENDER TO CONFIRM
3.4.7 | Total false ceiling height: 11 Meter App. |  |  | VENDER TO CONFIRM
3.4.8 | Total effective height : 8 Meter |  |  | VENDER TO CONFIRM
3.4.9 | Equipment load 350 KW & Effective equipment load: 60 kW |  |  | VENDER TO CONFIRM
3.4.10 | Lighting load: 1 watt per Sq. ft. |  |  | VENDER TO CONFIRM
3.4.11 | Occupancy load: 60 persons |  |  | VENDER TO CONFIRM
4 | TECHNICAL SPECIFICATIONS
4.1 | Water Chilling Units
4.1.1 | General
4.1.1.1 | The water chilling unit shall be air cooled rotary screw type with refrigerant R– 404A/ 134a/ 407C/ 410A/ 22. It shall be suitable for outdoor installation and designed for maximum corrosion protection with all panels being of heavy gauge galvanized steel construction. |  |  | VENDER TO SPECIFY
4.1.1.2 | It shall be compact, lightweight design completely factory assembled and tested under load conditions before dispatch and shipped with full operating charge of refrigerant and oil. |  |  | VENDER TO SPECIFY
4.1.1.3 | It shall be complete with energy efficient multiple rotary screw compressors, semi-hermetic/ hermetic motors, flooded liquid cooler, air cooled condenser, all interconnecting refrigerant piping, microprocessor based control panel containing all necessary operating and safety controls, indicating lights, starter, internal wiring, etc. as described below. |  |  | VENDER TO SPECIFY
4.2 | Compressor – motor assembly
4.2.1 | The efficient compressor shall be semi-hermetic/ hermetic rotary screw type driven by a two-pole motor. The motor rating shall exceed break horsepower by at least 10%. It shall be suitable for reduced inrush current starting. Each compressor shall have a suction check valve, suction filter, suction service valve and discharge check valve. |  |  | VENDER TO SPECIFY
4.2.2 | The lubrication system shall be force-fed and shall include an integral oil separation system, oil sump and oil filter. The temperature shall be controlled during operation to maintain proper oil temperatures throughout the lubrication system. An electric oil heater shall be supplied with each compressor to maintain oil temperature during shutdown period. |  |  | VENDER TO SPECIFY
4.2.3 | The step-less capacity control system shall modulate compressor capacity automatically by using an electrically initiated, hydraulically actuated slide valve within each compressor housing. |  |  | VENDER TO SPECIFY
4.2.4 | The compressor – efficient motor assembly shall be installed on a common base frame with anti-vibration mounts. |  |  | VENDER TO SPECIFY
4.3 | Condenser
4.3.1 | The condenser shall be air cooled type. |  |  | VENDER TO SPECIFY
4.3.2 | The condenser coil shall be constructed of copper tubes and die formed aluminum fins having self-spacing collars. Fins are to be mechanically bonded to the tubes. |  |  | VENDER TO SPECIFY
4.3.3 | Refrigerant sub-cooling shall be incorporated into the coil. Baffles shall separate each condenser fan. |  |  | VENDER TO SPECIFY
4.3.4 | The condenser shall have direct driven, heavy duty, aluminium bladed fans. The fan motors shall be 6 pole, slow speed type with internal overloads and shall be permanently lubricated. |  |  | VENDER TO SPECIFY
4.4 | Cooler / Chiller
4.4.1 | The cooler shall be shell and tube type with seamless carbon steel shell, carbon steel dished ends and integrally finned copper tubes. |  |  | VENDER TO SPECIFY
4.4.2 | The shell shall be rolled from 8 mm thick tested quality carbon steel plates as per IS 226. It shall have galvanised steel baffles to provide zigzag passage over bank of tubes for efficient heat transfer. |  |  | VENDER TO SPECIFY
4.4.3 | The flooded evaporator shall have a built-in distributor for feeding refrigerant evenly under the tube bundle to produce a uniform boiling action and baffle plates shall ensure vapour separation. |  |  | VENDER TO SPECIFY
4.4.4 | The flooded evaporator shall be fitted with an oil recovery system. The oil recovery system shall ensure that the cooler is operating at peak efficiency at all times and provides optimal energy efficiency during extended periods of part load. |  |  | VENDER TO SPECIFY
4.4.5 | The water heads shall be of carbon steel and designed for easy removal for mechanical tube cleaning and/ or tube removal. They shall be designed for multiple pass arrangement for optimum water velocity through tubes for efficient heat transfer and lower pressure drop. |  |  | VENDER TO SPECIFY
4.4.6 | The tubes shall be at least 16 mm outside diameter seamless copper tubes plain from outside and integrally fine finned from inside. The fin spacing shall be at least 748 fins per meter. The tubes shall be roller expanded into tube sheets made of high grade carbon steel plates. The tubes shall be removable without affecting strength and durability of tube sheets or causing any leakage in adjacent tubes. The tubes shall be adequately supported to prevent tube vibrations. |  |  | VENDER TO SPECIFY
4.4.7 | The cooler shall be complete with standard accessories such as pressure relief valve, purge valve, angle relief valve at liquid refrigerant outlet and drain connection. |  |  | VENDER TO SPECIFY
4.4.8 | The cooler shall be designed for minimum 20 kg/ cm2 pneumatic pressure on shell side and minimum 10 kg/ cm2 hydraulic pressure on tube side. |  |  | VENDER TO SPECIFY
4.5 | Refrigerant piping
4.5.1 | The refrigerant lines shall be of copper/ seamless carbon steel pipes. The liquid refrigerant line shall include shut off valve with charging port, liquid sight glass with moisture indicator, solenoid valve, filter-drier, flash economizer and modulating refrigerant expansion devices. |  |  | VENDER TO SPECIFY
4.5.2 | The refrigerant vapour from the flash economizer shall be fed back into an intermediate compressor stage, thereby reducing the enthalpy of the refrigerant, increasing the net refrigeration effect of the evaporator and maximizing energy efficiency. |  |  | VENDER TO SPECIFY
4.5.3 | The modulating refrigerant control system shall optimize efficiency by restricting the flow of refrigerant vapour in the condenser from entering the evaporator at reduced load, by directly modulating a motorized refrigerant valve in the liquid line entering the evaporator. In addition, the refrigerant control system shall measure the level of liquid refrigerant in the flooded evaporator and restrict refrigerant flow entering the evaporator upon a rise in the level protecting the compressor from slugging liquid refrigerant. |  |  | VENDER TO SPECIFY
4.5.4 | The refrigerant piping shall be designed for minimum 20 kg/ cm2 nitrogen pressure. |  |  | VENDER TO SPECIFY
4.6 | Power and control panel
4.6.1 | The power and control panel shall be pre assembled, wired and cushion mounted on the unit for utmost reliability and long life. It shall be fabricated from steel and shall have lockable door. It shall have separate compartments for electrical power control and refrigeration control. |  |  | VENDER TO SPECIFY
4.6.2 | The power panel shall contain reduced inrush current starter and moulded case circuit breaker for each compressor – motor, factory wired with terminal block power connection, primary and secondary fused control power transformer. |  |  | VENDER TO SPECIFY
4.6.3 | The control panel shall include high and low pressure cut-outs, suction, discharge and oil pressure gauges, oil safety control, antifreeze protection, indicating lights to locate cause of shutdown, interlocks for inherent motor protection, marked terminal strip and interconnecting control wiring. |  |  | VENDER TO SPECIFY
4.6.4 | The equipment manufacturer shall provide all indicating instruments necessary for proper operational control of individual equipment. They shall be mounted on the equipment itself and shall not be measured separately. |  |  | VENDER TO SPECIFY
4.6.5 | It shall be possible to start or stop the water chilling unit manually or through an external signal. |  |  | VENDER TO SPECIFY
4.7 | Following operating controls shall be provided:
| a) Leaving chilled water temperature controller based on rate of change of return chilled water temperature. |  |  | VENDER TO SPECIFY
| b) Auto lead-lag functions that constantly even out running hours and machine start automatically. If this function is not provided then cycle counter and hour meter shall be provided for each machine to facilitate manual changing of lead-lag on machines and evening out of machine starts and running hours. |  |  | VENDER TO SPECIFY
4.8 | Following system protection controls with indicating lights or diagnostic readouts shall be provided to automatically act to insure system reliability:
| a) Low suction pressure. |  |  | VENDER TO SPECIFY
| b) High discharge pressure. |  |  | VENDER TO SPECIFY
| c) Freeze protection. |  |  | VENDER TO SPECIFY
| d) Low differential pressure. |  |  | VENDER TO SPECIFY
| e) Low oil level. |  |  | VENDER TO SPECIFY
| f) Compressor run error. |  |  | VENDER TO SPECIFY
| g) Loss of power. |  |  | VENDER TO SPECIFY
| h) Loss of chilled water flow. |  |  | VENDER TO SPECIFY
| i) Sensor error. |  |  | VENDER TO SPECIFY
| j) Compressor over current. |  |  | VENDER TO SPECIFY
| k) Over/ under voltage. |  |  | VENDER TO SPECIFY
| l) Anti recycle. |  |  | VENDER TO SPECIFY
4.8.1 | The electrical control shall be separate from refrigeration control to allow safer, ready adjustment, while the system is in operation. |  |  | VENDER TO SPECIFY
4.8.2 | The electrical system shall be self sufficient and shall need only a single three-phase external power supply to be provided to the power panel. |  |  | VENDER TO SPECIFY
4.8.3 | The water chilling unit shall be electrically interlocked with the chilled water pump. |  |  | VENDER TO SPECIFY
4.8.4 | The electrical control panel shall be wired to permit fully automatic operation during initial start-up, normal operation, and shutdown conditions. |  |  | VENDER TO SPECIFY
4.9 | Insulation
4.9.1 | The cooler and suction line shall be factory insulated with adequate thickness of foam rubber or equivalent insulating material to prevent condensation. The entire suction line and liquid line between the expansion valve and the cooler shall be insulated with flexible closed cell insulation. Insulation thickness and skin temperature to be identified. |  |  | VENDER TO SPECIFY
4.1 | Installation
4.10.1 | The water chilling unit shall be installed over concrete platform and shall be adequately isolated by vibration isolation pads to prevent vibrations being carried over to the building structure. |  |  | VENDER TO SPECIFY
4.11 | Testing and commissioning
4.11.1 | The water chilling unit shall be factory tested and charged in the presence of the Owner’s representative. The manufacturer shall provide factory test certificate for the complete load range. After the unit is properly installed, it shall be field tested to ensure that the unit meets the tender requirements. The necessary quantities of refrigerant, oil and other consumables shall be provided during initial testing and commissioning. The manufacturer’s factory representative shall be present during initial testing and commissioning at site. |  |  | VENDER TO SPECIFY
4.11.2 | The noise and vibration levels shall also be checked to establish that both are within acceptable limits. |  |  | VENDER TO SPECIFY
4.12 | Water Circulation Pumps
4.12.1 | General
4.12.1.1 | The water circulation pump shall be in line centrifugal back pull out type. It shall be direct driven by a highly efficient totally enclosed fan cooled motor. |  |  | VENDER TO SPECIFY
4.12.2 | Construction
4.12.2.1 | The pump casing shall be of close grained cast iron heavy section. It shall be back pull out type to facilitate servicing of rotating parts without major dismantling. |  |  | VENDER TO SPECIFY
4.12.2.2 | The impeller shall be of bronze or gun metal. It shall have smooth passage for minimum friction and maximum efficiency. It shall be statically balanced. The shaft shall be of stainless steel and protected by gun metal sleeves. The bearings shall be of ball/ journal type, grease lubricated and contained in easily removable housing. |  |  | VENDER TO SPECIFY
4.12.2.3 | The pump shall be provided with mechanical seals, air vent valve, grease lubricators, drain plug and water seal connections. |  |  | VENDER TO SPECIFY
4.12.2.4 | The motor rating shall be non overloading type throughout the pump capacity range. It shall have class F insulation. It shall be designed for quiet operation and its speed shall not exceed 2900 rpm. |  |  | VENDER TO SPECIFY
4.12.2.5 | The pump shall be coupled to the motor through a flexible coupling. The pump – motor assembly shall be dynamically balanced. It shall be mounted on common cast iron base or fabricated galvanized steel rails. |  |  | VENDER TO SPECIFY
4.12.3 | Controls
4.12.3.1 | The discharge side of chilled water pump shall have flow switch to conclusively establish water flow through cooler and provide electrical interlock with the water chilling unit. The flow switch is separately identified in the Schedule of Quantities. A variable frequency drive arrangement shall be provided as optional extra. |  |  | VENDER TO SPECIFY
4.12.4 | Installation
4.12.4.1 | The water circulation pump shall be installed in line at least 300 mm above floor level and the pipe connections shall be through flexible pipe connectors. |  |  | VENDER TO SPECIFY
4.12.5 | Testing and commissioning
4.12.5.1 | After the water circulation pump is properly installed, acceptance test shall be carried out during commissioning to establish capacity at design conditions. The capacity shall be computed from the standard performance curves provided by the manufacturer. |  |  | VENDER TO SPECIFY
4.12.5.2 | The noise and vibration levels shall also be checked to establish that both are within acceptable limits. |  |  | VENDER TO SPECIFY
4.13 | Air Handling Units
4.13.1 | General
4.13.1.1 | The air handling unit shall be floor mounted horizontal draw through type of sectionalized construction. Basic assembly shall consist of mixing plenum, filter section, coil section, fan section and filter plenum. |  |  | VENDER TO SPECIFY
4.13.1.2 | All sections shall be joined together with soft rubber gasket pressed between the two to make the joints airtight. Suitable airtight access doors/ panels with aluminum hinges and handles shall be provided to allow access to internal parts for maintenance. |  |  | VENDER TO SPECIFY
4.13.1.3 | The complete unit shall be mounted on a galvanized sheet steel base frame for ease of shipment and handling. The unit shall have painted lifting assembly lugs located to suit optimum hoisting stability. |  |  | VENDER TO SPECIFY
4.13.2 | Casing |  |  | VENDER TO SPECIFY
4.13.2.1 | The casing shall have a perimeter frame with a modular system based on standardized panels and reinforced vertical sections. Removal of side panels shall not affect the structural integrity of the unit. |  |  | VENDER TO SPECIFY
4.13.2.2 | The frame work shall be made from non corrosive extruded aluminum channels fitted together with pressure die cast aluminum/ nylon plastic/ polyamide corner pieces. |  |  | VENDER TO SPECIFY
4.13.2.3 | The panels shall be 40 mm thick with polyurethane foam insulation of 38 kg/ m3 density injected between two 0.6 mm galvanized steel sheets. The panels shall be fixed to the perimeter frame from inside the unit. The panels shall be flush mounted. There shall be no sharp edges or corners on the unit, which might cause accident or injury. A non hygroscopic seal shall be compressed between the panel and the aluminum frame channels to prevent cold cracking and air leakage. |  |  | VENDER TO SPECIFY
4.13.2.4 | All external surfaces of panels and frames shall be chemically treated, pre-coated with primer and then coated with a highly durable, factory applied, heat hardened epoxy based powder paint. |  |  | VENDER TO SPECIFY
4.13.3 | Fan section
4.13.3.1 | The fan section shall be suitable for horizontal/ vertical air delivery as per site conditions. Only one fan discharge shall be provided. The fan discharge velocity shall not exceed 11 m/ s. The fan discharge shall be isolated from the casing by a flexible connector of fire retardant fabric. |  |  | VENDER TO SPECIFY
4.13.3.2 | The cooling coil shall be at least six rows deep and shall be for chilled water duty. The cooling coil shall be made of copper tubes and aluminium plate fins. The copper tubes of 27 gauge and 16 mm or 13 mm outside diameter shall be mechanically expanded into 0.15 mm aluminium plate fins spaced 472 fins per metre and assembled in 1.5 mm thick galvanised steel sheet end plates. Soldering or tinning shall not be used in the bonding process. |  |  | VENDER TO SPECIFY
4.13.3.3 | The cooling coil shall be designed to utilise the full available cross section area of the unit. The air velocity across the coil face shall not exceed 2.5 m/ s. It shall have full face active with intertwined circuits for equal loading on each circuit. |  |  | VENDER TO SPECIFY
4.13.3.4 | The cooling coil circuit shall be adequately sized and water velocity shall not exceed 2.4 m/ s. The tubes shall be staggered in the direction of the air flow and shall have counter flow arrangement. The water headers shall be of C class electric resistance welded mild steel pipes. The headers shall have inlet/ outlet connections, drain at the bottom and vent plugs at the highest point. The inlet and outlet connections shall be on the same side. |  |  | VENDER TO SPECIFY
4.13.3.5 | A four pass eliminator of poly-vinyl-chloride shall be provided in front of the cooling coil. |  |  | VENDER TO SPECIFY
4.13.3.6 | The cooling coil shall be factory tested under water at 20 kg/ cm2 pneumatic pressure. |  |  | VENDER TO SPECIFY
4.13.4 | Drain pan
4.13.4.1 | The condensed water drain pan shall be provided under the cooling coil. It shall be of double skin sandwich insulated type with inner skin of 1.1 mm stainless steel sheet of 304 quality grade, outer skin of 0.6 mm galvanized steel sheet and polyurethane foam insulation of 38 kg/ m3 density injected between two. |  |  | VENDER TO SPECIFY
4.13.4.2 | The drain pan shall have two 40 mm or 50 mm female pipe threaded heavy gauge drain couplings on both sides to facilitate drain connection from either side. The drain pan shall slope towards drain water outlet for effective drainage. |  |  | VENDER TO SPECIFY
4.13.5 | Filter section/ plenum
4.13.5.1 | The filter section/ plenum shall have the same casing construction as the unit. It shall be designed to house maximum area of filters to ensure low air velocity and compact construction. It shall facilitate removal and refitting of filters from the side. The filter section shall contain pre-filters before the cooling coil. The filter plenum shall contain fine filters after the fan. |  |  | VENDER TO SPECIFY
4.13.5.2 | The pre-filter shall be washable type having 50 mm thick aluminum frame with folded synthetic fiber media sandwiched between high-density polyethylene mesh on one side and aluminum expanded mesh on the other side. It shall be capable of operating up to 2.5 m/ s face velocity without loss of filter efficiency and holding capacity. It shall filter out dust particles larger than 10 micron size with 90% filtration efficiency based on ASHRAE Test Standard 52-76. The initial air pressure drop shall not exceed 4 mm water gauge when clean. The final air pressure drop shall not exceed 10 mm water gauge when dirty. |  |  | VENDER TO SPECIFY
4.13.5.3 | Each filter of size 600 x 600 mm and above shall be mounted with eight numbers galvanised steel bolts and wing nuts having built in washers and 3 mm thick 20 mm wide neoprene gaskets. |  |  | VENDER TO SPECIFY
4.13.6 | Volume control dampers
4.13.6.1 | Each air inlet and air outlet of the air handling unit shall have volume control damper designed to control airflow. |  |  | VENDER TO SPECIFY
4.13.6.2 | The volume control damper shall be fabricated out of 1.6 mm bright galvanised steel sheets. It shall have opposed acting damper blades, mechanically secured to 13 mm outside diameter polished steel spindles, rotating in bronze or nylon bushings to provide smooth operation even without extra lubrication. |  |  | VENDER TO SPECIFY
4.13.7 | Controls
4.13.7.1 | The air capacity of the air handling unit shall be manually controlled by volume control dampers to be provided on air inlets and air outlets as part of the air handling unit. A variable frequency drive arrangement shall be provided as optional extra. |  |  | VENDER TO SPECIFY
| The cooling capacity of the air handling unit shall be controlled by a three-way motorised valve and a proportional thermostat. The thermostat shall sense the return air temperature and control the cooling capacity by varying the chilled water flow. The sensitivity of the thermostat shall be + 1O C. The three-way motorised valve and proportional thermostat are separately identified in the Schedule of Quantities. |  |  | VENDER TO SPECIFY
| Installation |  |  | VENDER TO SPECIFY
| The air handling unit shall be installed on cement concrete pedestals projecting at least 200 mm above the finished floor level of the air handling unit room. This is required to ensure air circulation and avoid entrapment of moisture below the unit. |  |  | VENDER TO SPECIFY
| The fan motor alignment shall be rechecked during installation to ensure vibration free operation. The pipe and duct connections shall be through suitable flexible connections to prevent vibrations from being transmitted through ductwork and pipe work. |  |  | VENDER TO SPECIFY
4.13.8 | Testing and commissioning
4.13.8.1 | After the air handling unit is properly installed, acceptance test shall be carried out during commissioning to establish both air capacity and cooling capacity at design conditions in accordance with the procedure specified under Performance Tests. |  |  | VENDER TO SPECIFY
4.13.8.2 | The air capacity shall be computed by measuring air velocity across filters. The cooling capacity shall be computed from air flow and dry and wet bulb temperatures of air entering and leaving the cooling coil. |  |  | VENDER TO SPECIFY
4.13.8.3 | The noise and vibration levels shall also be checked to establish that both are within acceptable limits. |  |  | VENDER TO SPECIFY
4.14 | Air Cooling Units
4.14.1 | General
4.14.1.1 | The air cooling unit shall be floor mounted horizontal draw through type of sectionalized construction. Basic assembly shall consist of filter section, humidifying section and fan section. |  |  | VENDER TO SPECIFY
4.14.1.2 | All sections shall be joined together with soft rubber gasket pressed between the two to make the joints airtight. Suitable airtight access doors/ panels with aluminum hinges and handles shall be provided to allow access to internal parts for maintenance. |  |  | VENDER TO SPECIFY
4.14.1.3 | The complete unit shall be mounted on a galvanized sheet steel base frame for ease of shipment and handling. The unit shall have painted lifting assembly lugs located to suit optimum hoisting stability. |  |  | VENDER TO SPECIFY
4.14.2 | Casing
4.14.2.1 | The casing shall have a perimeter frame with a modular system based on standardized panels and reinforced vertical sections. Removal of side panels shall not affect the structural integrity of the unit. |  |  | VENDER TO SPECIFY
4.14.2.2 | The frame work shall be made from non corrosive extruded aluminum channels fitted together with pressure die cast aluminum/ nylon plastic/ polyamide corner pieces. |  |  | VENDER TO SPECIFY
4.14.2.3 | The panels shall be 25 mm thick with polyurethane foam insulation of 38 kg/ m3 density injected between two 0.6 mm galvanized steel sheets. The panels shall be fixed to the perimeter frame from inside the unit. The panels shall be flush mounted. There shall be no sharp edges or corners on the unit, which might cause accident or injury. A non hygroscopic seal shall be compressed between the panel and the aluminum frame channels to prevent cold cracking and air leakage. |  |  | VENDER TO SPECIFY
4.14.2.4 | All external surfaces of panels and frames shall be chemically treated, pre-coated with primer and then coated with a highly durable, factory applied, heat hardened epoxy based powder paint. |  |  | VENDER TO SPECIFY
4.14.3 | Fan section
4.14.3.1 | The fan section shall be suitable for horizontal/ vertical air delivery as per site conditions. Only one fan discharge shall be provided. The fan discharge velocity shall not exceed 11 m/ s. The fan discharge shall be isolated from the casing by a flexible connector of fire retardant fabric. |  |  | VENDER TO SPECIFY
4.14.3.2 | The fan wheels shall be backward inclined/ forward curved, multiple blade, double inlet double width type, fabricated from 1.6 mm thick heavy gauge galvanized steel and enclosed in housing mounted on common shaft. |  |  | VENDER TO SPECIFY
4.14.3.3 | The fan housing shall be made of die formed 1.6 mm thick heavy gauge galvanized steel sheets with streamlined inlets and guide vanes to ensure smooth air intake. |  |  | VENDER TO SPECIFY
4.14.3.4 | The fan shaft shall be EN-8 or C-40 carbon steel with precisely machined ends. The fan shaft shall not pass through its first critical speed. |  |  | VENDER TO SPECIFY
4.14.3.5 | The fan and shaft assembly shall rest on self aligning pillow block sealed ball bearings mounted on suitable supports and easily accessible for lubrication and maintenance. |  |  | VENDER TO SPECIFY
4.14.3.6 | Each fan wheel shall be individually balanced to allow interchange and entire fan and shaft assembly shall be dynamically trim balanced to ISO 1940 quality grade. |  |  | VENDER TO SPECIFY
4.14.4 | Fan drive
4.14.4.1 | The fan shall be direct/ belt driven by a totally enclosed fan cooled squirrel cage four pole induction motor with IP 55 protection and class F insulation. The motor rating shall be at least 15% more than the fan shaft load. The motor shall be mounted inside the fan section. |  |  | VENDER TO SPECIFY
4.14.4.2 | The water circulation pump shall be direct driven by three/ single phase motor and the assembly shall be supported on a galvanized steel base frame. |  |  | VENDER TO SPECIFY
4.14.5 | Filter section/ plenum
4.14.5.1 | The filter section/ plenum shall have the same casing construction as the unit. It shall be designed to house maximum area of filters to ensure low air velocity and compact construction. It shall facilitate removal and refitting of filters from the side. |  |  | VENDER TO SPECIFY
4.14.5.2 | The filter section shall contain two banks of filters – one bank of 20 micron rough filters and the other of 10 micron pre-filters before the wet deck humidifier pads. |  |  | VENDER TO SPECIFY
4.14.5.3 | The filter shall be washable type having 50 mm thick aluminum frame with folded synthetic fiber media sandwiched between high-density polyethylene mesh on one side and aluminum expanded mesh on the other side. It shall be capable of operating up to 2.5 m/ s face velocity without loss of filter efficiency and holding capacity. It shall filter out dust particles larger than 20/ 10 micron size with 90% filtration efficiency based on ASHRAE Test Standard 52-76. The initial air pressure drop shall not exceed 4 mm water gauge when clean. The final air pressure drop shall not exceed 10 mm water gauge when dirty. |  |  | VENDER TO SPECIFY
4.15 | Automatic Controls
4.15.1 | General
4.15.1.1 | All automatic controls shall be electrically operated. The equipment manufacturer shall provide all operating and safety controls necessary for proper operation of individual equipment as described in respective specification. They shall be mounted on the equipment itself and shall not be measured separately. |  |  | VENDER TO SPECIFY
4.15.2 | Proportional thermostats
4.15.2.1 | The proportional thermostat shall sense the return air temperature and actuate the three – way modulating valve of the air handling unit. |  |  | VENDER TO SPECIFY
4.15.2.2 | The proportional thermostat shall have a range of 10 OC – 30 OC and a differential of 1 OC. |  |  | VENDER TO SPECIFY
4.15.2.3 | The proportional thermostat shall be suitable for working on line voltage. |  |  | VENDER TO SPECIFY
4.15.3 | Flow switches |  |  | VENDER TO SPECIFY
4.15.3.1 | The flow switch shall be vane operated type. The motion of the vane shall actuate switch by the action of a magnet, which controls the switch. |  |  | VENDER TO SPECIFY
4.15.4 | Installation |  |  | VENDER TO SPECIFY
4.15.4.1 | All automatic controls specifically mentioned and/ or necessary shall be installed in the locations appropriate for the proper functioning of the equipment they control. |  |  | VENDER TO SPECIFY
4.16.5 | Testing and commissioning |  |  | VENDER TO SPECIFY
4.15.5.1 | All automatic controls and instruments shall be tested for their proper functioning during commissioning and performance testing. |  |  | VENDER TO SPECIFY
4.15.6 | Sheet Metal Work |  |  | VENDER TO SPECIFY
4.15.6.1 | Ducts |  |  | VENDER TO SPECIFY
4.15.6.1.1 | All rectangular ducts shall be fabricated out of bright galvanized steel sheets with no watermarks. The galvanized steel sheets shall conform to IS 277. The zinc coating shall not be less than 125 gm/ m2 of surface area. |  |  | VENDER TO SPECIFY
4.15.6.1.2 | The thickness of sheets shall be as under: |  |  | VENDER TO SPECIFY
| Duct longer side | Sheet thickness |  | VENDER TO SPECIFY
| Up to 750 mm | 0.63 mm (24 gauge) |  | VENDER TO SPECIFY
| 751 mm to 1500 mm | 0.80 mm (22 gauge) |  | VENDER TO SPECIFY
| 1501 mm to 2250 mm | 1.00 mm (20 gauge) |  | VENDER TO SPECIFY
| 2251 mm and above | 1.25 mm (18 gauge) |  | VENDER TO SPECIFY
4.15.6.2 | Duct dampers |  |  | VENDER TO SPECIFY
4.15.6.2.1 | The duct dampers shall be of robust construction having opposed acting damper blades, mechanically secured to 13 mm outside diameter polished steel spindles, rotating in bronze or nylon bushings to provide smooth operation even without extra lubrication. |  |  | VENDER TO SPECIFY
4.15.6.2.2 | The duct dampers shall be fabricated out of 1.6 mm thick bright galvanised steel sheets. They shall be provided with suitable linkages, index levers and quadrants as required for their proper operation, control and setting in any desired position. |  |  | VENDER TO SPECIFY
4.15.6.2.3 | The duct dampers and their operating devices shall be robust, easily operable and accessible through suitable access doors. Each duct damper shall have an indicating device clearly showing its open/ close position and a locking device to keep it in fixed position at all times after air balancing of the entire system. |  |  | VENDER TO SPECIFY
4.15.6.2.4 | The duct dampers shall be provided in duct branches having multiple outlets for proper volume control and air balancing of the system. |  |  | VENDER TO SPECIFY
4.15.6.3 | Grills |  |  | VENDER TO SPECIFY
4.15.6.3.1 | All grills shall be of powder coated aluminum construction in rectangular shape. They shall be designed according to the location and the service required. |  |  | VENDER TO SPECIFY
4.15.6.3.2 | All grills shall have flange frame with the outside edge returned or curved 5 – 7 mm. The outer frames shall be fabricated from minimum 1.6 mm thick aluminum sheets and the internal louvers shall be fabricated from minimum 0.8 mm thick aluminum sheets. The louvers shall be spaced less than 18 mm. |  |  | VENDER TO SPECIFY
4.15.6.3.3 | The core of the supply air grill shall have adjustable front louvers parallel to the longer dimension to give 0 – 30O vertical deflection and adjustable back louvers parallel to the shorter dimension to achieve a horizontal spread air pattern to at least 45O. The return air grills shall have only front louvers. |  |  | VENDER TO SPECIFY
4.15.6.3.4 | All supply air grills shall be provided with volume control dampers operated from front face by removable keys. All volume control dampers shall be of aluminum anodized in matt black finish. |  |  | VENDER TO SPECIFY
4.15.6.3.5 | All return/ exhaust air grills shall be without volume control dampers. The gravity louver type grills shall have louvers mechanically secured to polished steel spindles, rotating in bronze or nylon bushings to provide smooth operation even without extra lubrication. |  |  | VENDER TO SPECIFY
4.15.6.3.6 | The effective area of grills shall not be less than 75% of the gross face area. All grills shall be fitted with a suitable flexible gasket between the concealed face of the flange and the finished surface. |  |  | VENDER TO SPECIFY
4.15.6.3.7 | Since different spaces may require different types or patterns, all grills shall be selected in consultation with the Architects and the Consultants. |  |  | VENDER TO SPECIFY
4.15.6.4 | Installation |  |  | VENDER TO SPECIFY
4.15.6.4.1 | The duct fabrication and installation shall generally conform to IS 655 – 1963 and specifically conform to the approved shop drawings to be prepared by the contractor. The contractor shall machine fabricate the ducts in his workshop or install a lock former machine at site to fabricate the ducts. |  |  | VENDER TO SPECIFY
4.15.6.4.2 | The contractor shall provide for necessary allowances for beams, pipes or other obstructions in the building, whether or not they are shown on the drawings. Where necessary to avoid beams, pipes or other obstructions, the duct shall be transformed, divided or turned to one side as per site conditions without changing the cross sectional area. |  |  | VENDER TO SPECIFY
4.15.6.4.3 | If the duct cannot be run as shown on the drawing, the contractor shall install the duct between the required points by any route available as per site conditions and in co-ordination with other services. |  |  | VENDER TO SPECIFY
4.15.6.4.4 | The ducts shall be rigid and shall be adequately supported and braced with standing seams, galvanized angles, etc. as required to keep the duct true to shape and prevent it from bucking, vibrating or breaching. |  |  | VENDER TO SPECIFY
4.15.6.4.5 | The duct fabrication shall conform to the following: |  |  | VENDER TO SPECIFY
| Longer side & thickness | Transverse joints | Reinforcement | VENDER TO SPECIFY
| Up to 400 mm , 24 gauge | 25 mm pocket slip | Cross bracing | VENDER TO SPECIFY
| 401 to 750 mm, 24 gauge | 25 mm pocket slip | 25 x 25 x 3 mm angle at 1200 mm | VENDER TO SPECIFY
| 751 to 1000 mm, 22 gauge | Sheet metal flange | 25 x 25 x 3 mm angle at 1200 mm | VENDER TO SPECIFY
| 1001 to 1500 mm, 22 gauge | 40 x 40 x 3 mm angle flange | 40 x 40 x 3 mm angle at 1200 mm | VENDER TO SPECIFY
| 1501 to 2250 mm, 20 gauge | 50 x 50 x 3 mm angle flange | 50 x 50 x 3 mm angle at 1200 mm | VENDER TO SPECIFY
| 2251 mm and more, 18 gauge | 50 x 50 x 6 mm angle flange | 50 x 50 x 6 mm angle at 1200 mm | VENDER TO SPECIFY
4.15.6.4.6 | The ducts shall be straight and smooth on the inside with neatly finished joints. All joints shall be made air tight by using 3 mm thick rubber gaskets. The internal ends of slip joints shall be in the direction of air flow. |  |  | VENDER TO SPECIFY
4.15.6.4.7 | The changes in dimensions and shape of the ducts shall be gradual. All sharp elbows shall have guide vanes to allow the air to take the turn without any appreciable turbulence. |  |  | VENDER TO SPECIFY
4.15.6.4.8 | All sheet metal connections, partitions and plenums required to confine the air flow to and through filters and fans shall be of 18 gauge galvanized steel sheets thoroughly stiffened with 25 x 25 x 3 mm galvanized steel angle braces. |  |  | VENDER TO SPECIFY
4.15.6.4.9 | The plenums shall have inspection doors of not less than 450 x 450 mm size to give access to internal parts. The galvanized angle flanges shall be fixed with rivet head inside and riveting from outside. |  |  | VENDER TO SPECIFY
4.15.6.4.10 | All sheet metal work shall be independently supported from structural members such as slab, beams, etc. by drilling holes in concrete and inserting anchor fasteners and bolts. Under no circumstances the duct shall rest on false ceiling or be supported from false ceiling hangers. |  |  | VENDER TO SPECIFY
4.15.6.4.11 | All horizontal ducts shall be transversely supported with trapeze hangers formed of galvanized steel rods and galvanized steel angles under the ducts as under: |  |  | VENDER TO SPECIFY
| Below 1800 mm perimeter | 40 x 40 x 3 mm angle with 10 mm rod |  | VENDER TO SPECIFY
| 1801 to 2500 mm perimeter | 40 x 40 x 6 mm angle with 10 mm rod |  | VENDER TO SPECIFY
| Over 2500 mm perimeter | 50 x 50 x 6 mm angle with 10 mm rod |  | VENDER TO SPECIFY
4.15.6.4.12 | All vertical ducts shall be supported by structural members at each floor. |  |  | VENDER TO SPECIFY
4.15.6.4.13 | Wherever ducts pass through concrete or brickwork, galvanised steel sheet skirting and bitumen applied curb shall be provided around it. |  |  | VENDER TO SPECIFY
4.15.6.4.14 | The sheet metal work shall be totally vibration free under all operational conditions. Wherever ducts are connected to rotating equipment suitable flexible connectors shall be provided. The connecting ducts shall be rigidly held by independent supports on both sides. |  |  | VENDER TO SPECIFY
4.15.6.4.15 | The flexible connector shall made of fire retardant heavy canvas sleeve at least 100 mm long securely bonded and bolted on both sides. It shall be suitable for air pressure at the point of installation. |  |  | VENDER TO SPECIFY
4.15.6.4.16 | The surfaces of all galvanised sheet metal work including all joints and supports devoid of zinc coating due to cutting, welding or threading shall be painted with two coats of red oxide and finished with two coats of zinc rich paint. |  |  | VENDER TO SPECIFY
4.15.6.4.17 | All sheet metal work shall be measured on the external surface and shall include all fittings and supports. |  |  | VENDER TO SPECIFY
4.15.6.5 | Testing and commissioning |  |  | VENDER TO SPECIFY
4.15.6.5.1 | After the sheet metal work is properly installed, all ducts shall be tested for air leakage at joints and connections before application of insulation. |  |  | VENDER TO SPECIFY
4.15.6.5.2 | The entire air distribution system shall be balanced to supply the required air quantities in different rooms and areas to maintain the specified design conditions. |  |  | VENDER TO SPECIFY
4.15.6.5.3 | The total of air quantities measured at various diffusers and grills shall tally with the air quantity measured at the related fan discharge. |  |  | VENDER TO SPECIFY
4.15.6.5.4 | The duct damper adjustments in the duct branches shall be permanently marked after the air balancing so that their settings can be restored to their correct position if disturbed at any time. |  |  | VENDER TO SPECIFY
4.15.6.5.5 | The final balance of air quantities through various diffusers and grills shall be recorded and submitted to the Consultants for approval. |  |  | VENDER TO SPECIFY
4.15.6.5.6 | The contractor shall provide at his expense all materials, tools, equipment, instruments, services and labour required to perform testing and balancing. |  |  | VENDER TO SPECIFY
4.15.7 | Pipe Work |  |  | VENDER TO SPECIFY
4.15.7.1 | Pipes and fittings |  |  | VENDER TO SPECIFY
4.15.7.1.1 | All pipes carrying cooling water shall be galvanised steel heavy class construction as per IS 1239. The fittings shall be galvanised steel heavy class. They shall be of screwed and/ or welded type. |  |  | VENDER TO SPECIFY
4.15.7.1.2 | All pipes carrying chilled water shall be mild steel heavy class construction as per IS 1239 for pipes of diameter 150 mm and below and as per IS 3589 for pipes of diameter 200 mm and above. The fittings shall be malleable steel heavy class. They shall be of welded type. |  |  | VENDER TO SPECIFY
4.15.7.1.3 | All pipes carrying condensed water drain shall be of heavy-duty polyvinyl chloride construction. The fittings shall be of the same material and of heat grip type. |  |  | VENDER TO SPECIFY
4.15.7.1.4 | All pipes and fittings shall be suitable for working pressure of 10 kg/ cm2. |  |  | VENDER TO SPECIFY
4.15.7.2 | Valves |  |  | VENDER TO SPECIFY
4.15.7.2.1 | The valves shall be gate, globe, check, butterfly or balancing type as indicated on the drawings and specified in the Schedule of Quantities. They shall include necessary flanges, counter flanges and nuts, bolts and gaskets. |  |  | VENDER TO SPECIFY
4.15.7.2.2 | All valves having sizes 50 mm and below shall be of gun metal construction with screwed female ends. All valves having sizes 65 mm and above shall have cast iron body with gun metal working parts, non-rising spindles and flanged ends with matching flanges. All valves shall have air release and clean out plugs. |  |  | VENDER TO SPECIFY
4.15.7.2.3 | All valves shall conform to IS 778 and IS 780 as applicable. All flanges shall conform to IS 6392. |  |  | VENDER TO SPECIFY
4.15.7.2.4 | The check valves shall be dual plate type with stainless steel springs and hinge/ stop pins. |  |  | VENDER TO SPECIFY
4.15.7.2.5 | The butterfly valves shall have heavy duty cast iron body conforming to IS 210 Gr. FG 220 with resilient black nitrile rubber seat moulded on to the body, nylon coated disk conforming to IS 865, stainless steel shaft treated for permanent lubrication and shaft seals having nitrile O rings and rubber seals. They shall have flow control lever and a locking device. |  |  | VENDER TO SPECIFY
4.15.7.2.6 | The balancing valves shall be similar to the butterfly valves and shall have built in facility to measure pressure drop across the valve for computing water flow rate. |  |  | VENDER TO SPECIFY
4.15.7.2.7 | All valves shall be suitable for working pressure of 10 kg/ cm2. |  |  | VENDER TO SPECIFY
4.15.7.3 | Strainers |  |  | VENDER TO SPECIFY
4.15.7.3.1 | All strainers shall preferably be of Y type with cast iron or fabricated steel body. They shall have removable bronze screens with 3 mm perforations and permanent magnets. They shall be provided with flanges or threaded sockets as required. |  |  | VENDER TO SPECIFY
4.15.7.3.2 | The strainers shall be so designed as to enable blowing off accumulated dirt and facilitate removal and replacement of the screens without disconnecting them from the main pipes. |  |  | VENDER TO SPECIFY
4.15.7.3.3 | All strainers shall be suitable for working pressure of 10 kg/ cm2. |  |  | VENDER TO SPECIFY
4.15.7.4 | Centrifugal air separator |  |  | VENDER TO SPECIFY
4.15.7.4.1 | The centrifugal air separator shall be fabricated from 5 mm thick mild steel shell and 6 mm thick dished ends. Its outside surface shall be coated with epoxy paint and all hardware shall be of stainless steel. |  |  | VENDER TO SPECIFY
4.15.7.4.2 | The centrifugal air separator shall be complete with air vent valve and drain plug. |  |  | VENDER TO SPECIFY
4.15.7.4.3 | The centrifugal air separator shall be so designed as to ensure tangential entry and exit at low velocity resulting in separation of air by centrifugal force. |  |  | VENDER TO SPECIFY
4.15.7.4.4 | The centrifugal air separator shall be suitable for working pressure of 10 kg/ cm2. |  |  | VENDER TO SPECIFY
4.15.7.5 | Flexible pipe connectors |  |  | VENDER TO SPECIFY
4.15.7.5.1 | The flexible pipe connector shall be leak proof tube lined with abrasion resistant seamless lining of rubber, full faced flanges integral with the tube, metal retaining rings and control rods. |  |  | VENDER TO SPECIFY
4.15.7.5.2 | The flexible pipe connector shall be suitable for working pressure of 10 kg/ cm2. |  |  | VENDER TO SPECIFY
4.15.7.6 | Test points |  |  | VENDER TO SPECIFY
4.15.7.6.1 | The test point shall have sealing bushes to allow passage of a fine needle like probes and to seal the passage on withdrawal of probes to prevent water leakage. |  |  | VENDER TO SPECIFY
4.15.7.6.2 | The test point shall be of brass construction with 6 mm threaded connection, neoprene sealing bushes and screwed cover. |  |  | VENDER TO SPECIFY
4.15.7.7 | Pressure gauges
4.15.7.7.1 | The pressure gauge shall have 100 mm dial and 10 mm gun metal gate valve for isolation. It shall be connected to pipes by copper tubing. |  |  | VENDER TO SPECIFY
4.15.7.7.2 | The pressure gauge shall be graduated in kg/ cm2 and its range shall be so selected that the pressure readings under normal duty conditions fall approximately in the middle of the range. The pressure gauge shall be accurately calibrated. |  |  | VENDER TO SPECIFY
4.15.7.8 | Thermometers
4.15.7.8.1 | The thermometer shall be alcohol in glass type with metallic protective casings. It shall be fitted in thermometer well having 12 mm threaded connection and sized for penetration to 75% of pipe diameter. |  |  | VENDER TO SPECIFY
4.15.7.8.2 | It shall be graduated in 0.1O C and its range shall be so selected that the temperature readings under normal duty conditions fall approximately in the middle of the range. The thermometer shall be accurately calibrated. |  |  | VENDER TO SPECIFY
4.15.7.9 | Installation
4.15.7.9.1 | All pipe work shall be installed in work man like manner and shall include all necessary fittings, accessories and supports. It shall specifically conform to the approved shop drawings to be prepared by the contractor. |  |  | VENDER TO SPECIFY
4.15.7.9.2 | The pipes shall be connected to one another with welded fittings, unless otherwise stated or directed at site. All tee off connections shall be through equal or reducing tees. Otherwise, ferrules shall be welded to the main pipe. Drilling and tapping of main pipe shall not be permitted. |  |  | VENDER TO SPECIFY
4.15.7.9.3 | The pipes shall be accurately cut to the required size and the burrs shall be removed before laying the pipes. The open ends of pipes shall be closed to prevent entry of foreign matter. The fittings used in the horizontal pipe runs shall be eccentric to facilitate free flow of water. In other locations, concentric fittings may be used. |  |  | VENDER TO SPECIFY
4.15.7.9.4 | All equipment and valve connections shall be through flanges. All flanges shall be drilled to BS 10 Table E. All flanged connections shall have minimum 3 mm thick ring type asbestos gaskets. |  |  | VENDER TO SPECIFY
4.15.7.9.5 | The welding of pipes shall be done by qualified welders and shall strictly conform to IS 9595 specifying code of practice for manual metal arc welding. The butt weld of each welder shall be subject to radiography test. After approval of this weld, the concerned welder shall be allowed to work further. The rest of the welds shall be subject to visual inspection only. |  |  | VENDER TO SPECIFY
4.15.7.9.6 | The inlets and the outlets of the coolers and water circulating pumps shall have butterfly valves. The high and low positions in the pipe work shall have air vent valves and drain valves. |  |  | VENDER TO SPECIFY
4.15.7.9.7 | The suction side of the water circulating pumps shall have strainers. |  |  | VENDER TO SPECIFY
4.15.7.9.8 | The closed pressurized expansion tank and centrifugal air separator shall be installed in the chilled water pipe line at a suitable location. |  |  | VENDER TO SPECIFY
4.15.7.9.9 | All pipe connections to the coolers, water circulating pumps and cooling coils shall be through flexible pipe connectors of equal size. |  |  | VENDER TO SPECIFY
4.15.7.9.10 | All inlets and outlets of the coolers, water circulating pumps, cooling coils and balancing valves shall have test points. |  |  | VENDER TO SPECIFY
4.15.7.9.11 | The suction side of the coolers shall have water flow switches installed in the chilled water return line. |  |  | VENDER TO SPECIFY
4.15.7.9.12 | All inlets and outlets of the coolers, water circulating pumps and cooling coils shall have pressure gauges. |  |  | VENDER TO SPECIFY
4.15.7.9.13 | All inlets and outlets of the coolers and cooling coils shall have thermometers. |  |  | VENDER TO SPECIFY
4.15.7.9.14 | The pipe work shall be properly supported by hangers, clamps, wall brackets, floor supports etc. as applicable. The contractor shall adequately design all hangers, clamps, wall brackets, floor supports etc. and will be responsible for their structural sufficiency. |  |  | VENDER TO SPECIFY
4.15.7.9.15 | All pipe supports inside the air conditioning plant room shall be of galvanized steel channels only. Elsewhere they shall be of galvanized steel angles and rods adjustable for height. All hardware used shall be hot dipped galvanized. |  |  | VENDER TO SPECIFY
4.15.7.9.16 | The spacing between two supports shall not exceed following: |  |  | VENDER TO SPECIFY
| 1200 mm for pipes of diameter 12 mm and below |  |  | VENDER TO SPECIFY
| 1800 mm for pipes of diameter 16 mm and 25 mm |  |  | VENDER TO SPECIFY
| 2400 mm for pipes of diameter 32 mm and above |  |  | VENDER TO SPECIFY
4.15.7.9.17 | The vertical pipe risers shall be parallel to wall and column lines and shall be straight and plumb. The pipe risers passing from floor to floor shall be supported at each slab by clamps or collars attached to the pipes and with 15 mm thick rubber pads or any other resilient material. Where pipes pass through the terrace floor, suitable flashing shall be provided to prevent water leakage. The pipe risers shall have suitable clean outs at the lowest points and air vents at the highest points. |  |  | VENDER TO SPECIFY
4.15.7.9.18 | Wherever pipes pass through wall and slabs, 3 mm thick pipe sleeves shall be provided. The diameter of the sleeves shall be 50 mm/ 100 mm larger than the diameter of respective cooling water/ chilled water pipes. The annular space shall be filled with fiber glass and finished with retainer rings. |  |  | VENDER TO SPECIFY
4.15.7.9.19 | The insulated pipes shall be supported in such a manner as not to put undue pressure on insulation. The clamps, saddles and rollers shall be separated from insulation by 20 gauge galvanized steel sheet extending at least 150 mm on both sides. |  |  | VENDER TO SPECIFY
4.15.7.9.20 | The pipe layout shall take due care of expansion and contraction of pipes. The contractor shall provide necessary expansion joints where required. |  |  | VENDER TO SPECIFY
4.15.7.9.21 | All non galvanized pipe work including all welded joints and supports shall be painted with two coats of red oxide primer and all external surfaces after insulation shall be painted with two coats of enamel. |  |  | VENDER TO SPECIFY
4.15.7.9.22 | The surfaces of all galvanized pipe work including all joints and supports devoid of zinc coating due to cutting, welding or threading shall be painted with two coats of red oxide and finished with two coats of zinc rich paint. |  |  | VENDER TO SPECIFY
4.15.7.9.23 | All pipe work shall be measured along the centre line of the installed pipes before application of insulation. The unit rates for pipes shall include all fittings and accessories such as bends, elbows, tees, reducers, unions, expansion loops, flanges with gaskets, nuts, bolts, etc. these fittings and accessories shall be measured as part of pipe length along the centre line of the installed pipes. |  |  | VENDER TO SPECIFY
4.15.7.9.24 | The unit rates shall also include all wastage, pipe supports including hangers, channels, wooden haunches, nuts, bolts, vibration isolation suspenders where specified or required and any other item required to fully complete the pipe work in accordance with these specifications, general trade practices and recognized principles. None of these items shall be separately measured nor paid for. |  |  | VENDER TO SPECIFY
4.15.7.9.25 | However all valves, strainers, closed pressurized expansion tank, centrifugal air separator, flexible pipe connectors, test points, flow switches, pressure gauges and thermometers shall be separately measured and paid for as per the unit rates. |  |  | VENDER TO SPECIFY
4.15.7.10 | Flushing, chemical cleaning and dosing
4.15.7.10.1 | After the pipe work installation is completed in all respects, the entire system shall be flushed and chemically cleaned to ensure that all suspended particles, rust and welding flux are completely removed. After the chemical cleaning the entire system shall be flushed with clean water and then dosed with anti rust chemicals and biocides. The entire treatment shall be carried out under the supervision of specialists. |  |  | VENDER TO SPECIFY
4.15.7.11 | Testing, balancing and commissioning
4.15.7.11.1 | After the pipe work is properly installed, but before application of insulation, it shall be tested for water leakage at joints and connections by applying hydrostatic pressure. |  |  | VENDER TO SPECIFY
4.15.7.11.2 | The hydrostatic test pressure shall be twice the maximum operating pressure but not less than 10 kg/ cm2. The pressure should hold for a period of at least 24 hours. |  |  | VENDER TO SPECIFY
4.15.7.11.3 | The system may be tested in sections and such sections shall be securely capped. The defects detected during the hydrostatic test shall be rectified and the pipe work again tested in the same manner. The entire pipe work shall be again tested at the end. |  |  | VENDER TO SPECIFY
4.15.7.11.4 | The contractor shall make sure that the required water flow through all coils and other heat exchangers is achieved properly and noiselessly without any air locks. |  |  | VENDER TO SPECIFY
4.15.7.11.5 | The entire water distribution system shall be balanced to supply the required water quantities to different equipment to maintain the specified design conditions. |  |  | VENDER TO SPECIFY
4.15.7.11.6 | The total of water quantities measured at different equipment shall tally with the water quantity measured at the related water circulating pump discharge. |  |  | VENDER TO SPECIFY
4.15.7.11.7 | All control valves shall be set for full flow condition during water balancing. The water flow shall be adjusted by the balancing cocks provided for the purpose. The valve adjustments shall be permanently marked after the water balancing so that their settings can be restored to their correct position if disturbed at any time. |  |  | VENDER TO SPECIFY
4.15.7.11.8 | The final balance of water quantities through different equipment shall be recorded and submitted to the Consultants for approval. |  |  | VENDER TO SPECIFY
4.15.7.11.9 | The contractor shall provide at his expense all materials, tools, equipment, instruments, services and labour required to perform testing and balancing and to remove water resulting from cleaning and after testing. |  |  | VENDER TO SPECIFY
4.15.8 | Thermal and Acoustic Insulation Work
4.15.8.1 | Material
4.15.8.1.1 | The insulation material for sheet metal work shall be resin bonded rigid fibre glass with thermal conductivity not exceeding 0.029 kcal/ h – cm – OK at 20O C mean temperature and for chilled water pipe work shall be rigid polyurethane foam with thermal conductivity not exceeding 0.023 kcal/ h – cm – OK at 10O C mean temperature. |  |  | VENDER TO SPECIFY
4.15.8.1.2 | The insulation material density shall not be less than 24 kg/ m2 for duct thermal insulation in slabs, 48 kg/ m2 for duct acoustic insulation in slabs and 32 kg/ m2 for pipe insulation in pre-formed sections. |  |  | VENDER TO SPECIFY
4.15.8.1.3 | 50 mm for all duct work running in unconditioned spaces, |  |  | VENDER TO SPECIFY
4.15.8.1.4 | 25 mm for all duct work running in conditioned spaces, |  |  | VENDER TO SPECIFY
4.15.8.1.5 | 25 mm for duct acoustic insulation, |  |  | VENDER TO SPECIFY
4.15.8.1.6 | 50 mm for chilled water pipe work of diameter 150 mm and above and |  |  | VENDER TO SPECIFY
4.15.8.1.7 | 30 mm for chilled water pipe work of diameter below 150 mm. |  |  | VENDER TO SPECIFY
4.15.8.2 | Duct thermal insulation
4.15.8.2.1 | The outside duct surface shall be first cleaned and then 85/40 or 85/25 industrial grade bitumen or any other approved adhesive shall be applied on the clean surface. |  |  | VENDER TO SPECIFY
4.15.8.2.2 | Then resin bonded fibre glass insulation of appropriate thickness and density shall be uniformly stuck on the outside duct surfaces. All longitudinal and transverse joints shall be filled with insulation material and sealed with aluminum tape. |  |  | VENDER TO SPECIFY
4.15.8.2.3 | Then galvanised iron angles shall be fixed along the four edges of the insulated duct to give it proper rectangular shape. The outer surface shall be wrapped with heavy canvas cloth dipped in cold setting compound with vapour barrier property and all joints overlapped. The insulation material shall be held in position by tightly drawn poly vinyl chloride straps. |  |  | VENDER TO SPECIFY
4.15.8.2.4 | If the duct is long, then fire breaks shall be provided in the duct insulation at 15 m centres by providing discontinuity in the insulating material using a fire stop in the form of 50 mm x 50 mm x 3 mm galvanised steel angle. The finish material of the insulation shall be tucked within this fire stop. |  |  | VENDER TO SPECIFY
4.15.8.2.5 | The insulated duct shall be finally clad with minimum 24 gauge polished aluminium sheets. |  |  | VENDER TO SPECIFY
4.15.8.3 | Duct acoustic insulation
4.15.8.3.1 | The inside duct surface shall be first cleaned and then 85/40 or 85/25 industrial grade bitumen or any other approved adhesive shall be applied on the clean surface. |  |  | VENDER TO SPECIFY
4.15.8.3.2 | Wooden batons, 25 mm wide and 25 mm thick, treated with preservative and fire retardant solution shall be fixed inside the duct at 600 mm centres. The space between the batons shall then be filled acoustic with of appropriate thickness and density in cut slabs of 600 mm x 600 mm. These slabs shall be uniformly stuck to the inside duct surface using cold setting adhesives. |  |  | VENDER TO SPECIFY
4.15.8.3.3 | The insulation surface shall be covered with fibre reinforced tissue paper and finally clad with minimum 28 gauge perforated aluminium sheets having at least 10% perforations. The aluminium sheets shall be fixed to the wooden batons using galvanised iron screws with washers and neatly finished. |  |  | VENDER TO SPECIFY
4.15.8.4 | Chilled water pipe insulation
4.15.8.4.1 | The outside pipe surface shall be first cleaned and then two coats of red oxide primer/ zinc chromate paint applied on the clean surface, especially the welded portion, allowing the paint to dry for at least 24 hours. Then 85/40 or 85/25 industrial grade bitumen or any other approved adhesive shall be applied on the painted surface. |  |  | VENDER TO SPECIFY
4.15.8.4.2 | Then pre moulded pipe sections of rigid polyurethane foam insulation of appropriate thickness and density shall be uniformly stuck on the pipe surfaces. All longitudinal and transverse joints shall be filled with insulation material and sealed with aluminium tape. |  |  | VENDER TO SPECIFY
4.15.8.4.3 | The outer surface shall be wrapped with heavy canvas cloth dipped in cold setting compound with vapour barrier property and all joints overlapped. The insulation material shall be held in position by tightly drawn poly vinyl chloride straps. |  |  | VENDER TO SPECIFY
4.15.8.4.4 | The insulated pipe shall be finally clad with minimum 24 gauge polished aluminium sheets. |  |  | VENDER TO SPECIFY
4.15.8.5 | Chilled water pump insulation
4.15.8.5.1 | The outside pump surface shall be first cleaned and then 85/40 or 85/25 industrial grade bitumen or any other approved adhesive shall be applied on the clean surface. |  |  | VENDER TO SPECIFY
4.15.8.5.2 | Then rigid polyurethane foam insulation of appropriate thickness and density shall be uniformly stuck on the pump surface. In general, the material and thickness of insulation shall be same as that used for the connected pipe work. The insulation shall be set and sealed in hot air blown grade bitumen to follow the pump contour. |  |  | VENDER TO SPECIFY
4.15.8.5.3 | The insulated pump shall be finally clad with minimum 24 gauge polished aluminium sheets. |  |  | VENDER TO SPECIFY
4.15.8.5.4 | The insulation material shall be applied in such a way that it can be easily removed for pump maintenance. |  |  | VENDER TO SPECIFY
4.15.8.6 | Insulation of other accessories |  |  | VENDER TO SPECIFY
4.15.8.6.1 | The insulation of other accessories like pressurised expansion tank and centrifugal air separator shall be applied similar to that specified under chilled water pump insulation. |  |  | VENDER TO SPECIFY
4.15.8.6.2 | All pipe fittings and specials like valves, strainers, etc. shall be insulated in the similar to that specified under chilled water pipe insulation. The valve bonnets, yokes and spindles shall be insulated in such a manner that insulation is not damaged while the valve is being used or serviced. |  |  | VENDER TO SPECIFY
4.15.8.7 | Application |  |  | VENDER TO SPECIFY
4.15.8.7.1 | The insulation shall be applied only after the pipe work is pressure tested for water leakage at joints and connections by applying hydrostatic pressure and all leaks are rectified. |  |  | VENDER TO SPECIFY
4.15.8.7.2 | Testing and commissioning |  |  | VENDER TO SPECIFY
4.15.8.7.2.1 | The effectiveness of the duct thermal insulation shall be tested by measuring the temperature rise in the supply air between each air handling unit and the farthest grill. This temperature rise shall not be more than 1O C. |  |  | VENDER TO SPECIFY
4.15.8.7.2.2 | The effectiveness of the acoustic insulation shall be tested by measuring sound intensity levels outside the air handling unit rooms. These levels shall be within the permissible norms. |  |  | VENDER TO SPECIFY
4.15.8.7.2.3 | The effectiveness of the chilled water pipe insulation shall be tested by measuring the temperature rise in the chilled water between the outlet of water chilling unit and the inlet to the cooling coil of the farthest air handling unit/ fan coil unit. This temperature rise shall not be more than 1O C. |  |  | VENDER TO SPECIFY
4.15.9 | Electrical Work
4.15.9.1 | General
4.15.9.1.1 | The BHEL shall only provide adequate 3 phase, 50 + 5% Hz, 415 + 10% V, 4 wire electric supply at single point. The scope of work under this contract shall include the distribution boards and the power and control cabling and earthing from the distribution boards to the various equipment of the air conditioning and pressurisation systems. It shall also include provision of remote push button stations for the pumps, air handling units, air cooling units and exhaust fans. |  |  | VENDER TO SPECIFY
4.15.9.2 | Distribution Board and Other Panels
4.15.9.2.1 | The distribution board shall be 60 micron powder coated sheet metal enclosed cubicle type, fully compartmentalized construction, indoor wall mounted or free floor standing with mild steel channels, dust tight, vermin proof and having IP 52 degree of protection as per IS 2147. |  |  | VENDER TO SPECIFY
4.15.9.2.2 | The sheet metal shall be minimum 1.6 mm thick cold rolled cold annealed steel. It shall undergo a process of degreasing, pickling in acid, cold rinsing, phosphatising, passivating and then sprayed with a higher corrosion resistant primer. The primer shall be baked in oven. The finishing shall be by application of epoxy powder coating of Siemens grey shade. |  |  | VENDER TO SPECIFY
4.15.9.2.3 | All doors, removable covers, gland plates and joints between adjacent sections shall have neoprene gaskets all round. The gland plates shall have at least 10% extra space for future use. The location of various components shall be such that there shall be ease of operation and their maintenance. The panel board shall be extendable on either side. Each feeder switch/ circuit breaker door shall have engraved metallic or acrylic nameplate. The main nameplate shall also be provided. |  |  | VENDER TO SPECIFY
4.15.9.2.4 | There shall be separate cable alley covering the entire height adjacent to feeder modules. The bus bar supports shall be hylam or epoxy insulators. All power switches shall be AC 23 duty and provided with door interlocks. The ON and OFF positions of the switch/ circuit breaker handle shall be clearly indicated. The current rating of the circuit breaker/ switch fuse shall be not less than that stated in the Schedule of Equipment. The fuse gear shall be HRC link type only, unless otherwise stated. |  |  | VENDER TO SPECIFY
4.15.9.2.5 | The bus bars shall be made from electrolytic grade copper of cross section suitable for the specified current rating and environment conditions. The neutral bus bar shall have cross sectional area not less that half that of phase bus bar. The spacing between the bus bars shall not be less than 25 mm. The bus bar system shall have 50 kA short circuit withstand capacity. The interconnections between the bus bars and various components shall be made using PVC insulated copper conductors made to IS 694 for feeders up to and including 63 A and with solid copper links for feeders of rating higher than 63 A and colour coded – red, yellow, blue and black. |  |  | VENDER TO SPECIFY
4.15.9.2.6 | A continuous copper earth bus shall be provided throughout the length of the distribution board and brought out into two suitable studs on each detachable section of the distribution board. Each power switch and circuit breaker shall be earthed by interconnecting it with the earth bus of the distribution board. |  |  | VENDER TO SPECIFY
4.15.9.2.7 | The distribution board shall incorporate 10 kA breaking capacity moulded case circuit breakers. It shall have a three phase three wire moulded case circuit breaker and a four pole earth leakage circuit breaker as incomer, 1000 A copper bus bars, neutral bars, starters, miniature circuit breakers, etc. Each earth leakage circuit breaker shall have 30 mA sensitivity, unless otherwise stated. |  |  | VENDER TO SPECIFY
4.15.9.2.8 | The design, manufacturing process and performance of the distribution board and all the components and instruments incorporated in them shall comply with the latest standards set by Bureau of Indian Standards and tariff Advisory Committee and particularly to the following: |  |  | VENDER TO SPECIFY
| BS 159 | Bus bars and bus bar connections |  | VENDER TO SPECIFY
| IS 1248 | Direct acting electrical indicating instruments |  | VENDER TO SPECIFY
| IS 2147 | Degree of protection provided by enclosures for low voltage switch gear and control gear |  | VENDER TO SPECIFY
| IS 2208 | HRC cartridge link fuse up to 600 V AC circuit breakers |  | VENDER TO SPECIFY
| IS 2516 | AC circuit breakers |  | VENDER TO SPECIFY
| IS 2705 | Current transformers |  | VENDER TO SPECIFY
| IS 3156 | Voltage transformers |  | VENDER TO SPECIFY
| IS 3043 | Code of practice for earthing |  | VENDER TO SPECIFY
| IS 4237 | Minimum clearance in air for bus bars |  | VENDER TO SPECIFY
| The contractor/ manufacturer of distribution board shall prepare the shop drawings showing full internal and external details such as: |  |  | VENDER TO SPECIFY
| a) Physical dimensions of all compartments |  |  | VENDER TO SPECIFY
| b) Physical dimensions and layout of all bus bars |  |  | VENDER TO SPECIFY
| c) Positioning of meters relays, indicating lamps, etc. |  |  | VENDER TO SPECIFY
| d) Front and side elevations |  |  | VENDER TO SPECIFY
| e) Single line diagram |  |  | VENDER TO SPECIFY
| f) Other relevant details. |  |  | VENDER TO SPECIFY
4.15.9.2.9 | The manufacture of distribution board shall not commence until the Consultants approve the shop drawings. |  |  | VENDER TO SPECIFY
4.15.9.2.10 | The manufacturer of the distribution board shall have in his possession a certificate from C. P. R. I. (or approved equivalent agency) certifying his capability to manufacture 50 kA short circuit withstand capacity bus bar system. If this certificate is not furnished to the Consultants, the distribution board cannot be taken up for manufacture. |  |  | VENDER TO SPECIFY
4.15.9.2.11 | At reasonable times during production and prior to dispatch of distribution board, the contractor/ manufacturer shall provide and arrange for Owner’s representative reasonable access and all facilities at the place of production, for inspection. |  |  | VENDER TO SPECIFY
4.15.9.2.12 | The following tests shall be carried out in the presence of the Owner’s representative: |  |  | VENDER TO SPECIFY
| a) 500 V Meggar – insulation test |  |  | VENDER TO SPECIFY
| b) High voltage test at 2 kV for one minute. |  |  | VENDER TO SPECIFY
4.15.9.2.13 | Six copies of the test certificates bearing the manufacturer’s as well as contractor’s stamps and signatures shall be furnished to the Consultants before dispatch. |  |  | VENDER TO SPECIFY
4.15.9.3 | Power Cabling and Wiring
4.15.9.3.1 | The power cabling and wiring shall include cables, wires, cable trays, conduits, glands, sockets and other ancillary materials like lockable nylon cable ties, galvanized iron hardware, spacers and saddles, cable identification tags, end termination, etc. as may be necessary. |  |  | VENDER TO SPECIFY
4.15.9.3.2 | All cables shall be XLPE insulated 1.1 kV grade armoured overall sheathed copper conductors conforming to IS 7098 (Part I) 1988. The cables shall be laid on walls/ columns/ ceilings or on cable trays as the case may be. The spacers, saddles and clamps shall be of galvanised iron. The lockable cable ties shall be of nylon. The cable identification tags shall be provided at not more than 10 m interval. Each cable identification tag shall mention the size of the cable and the name of the panel on both ends. |  |  | VENDER TO SPECIFY
4.15.9.3.3 | All wires shall be PVC insulated 1.1 kV grade multi stranded copper conductors conforming to IS 694. The cross sectional area of phase and neutral wires shall not be less than 2.5 mm2. The cross sectional area of the earth wire running inside the PVC conduits shall not be less than 2.5 mm2. The cross sectional area of control wires shall be 1.5 mm2. All wires shall have PVC protective sheathing. For ease of identification, wires with different colours shall be used for phase and neutral. For example, red, yellow and blue for phases, black for neutral and green for earth. |  |  | VENDER TO SPECIFY
4.15.9.3.4 | The cable trays shall be ladder type and made from minimum 2 mm thick cold rolled mild steel and hot dip galvanised after fabrication. The side channels shall be at least 70 mm. The rungs shall be 35 mm wide and 10 mm in height. They shall be at 250 mm interval. The cable trays shall be complete with galvanised iron coupler plates, hardware, cable bends in all directions, as required. The supports shall be at 1 m interval on the horizontal run and at 0.6 m interval on the vertical run. |  |  | VENDER TO SPECIFY
4.15.9.3.5 | All conduits shall be hot dip galvanised steel. All conduit accessories shall be compatible with the conduits installed. All conduits shall be provided with couplers for straight joints. |  |  | VENDER TO SPECIFY
4.15.9.3.6 | The end termination to the XLPE insulated 1.1 kV grade armoured overall sheathed copper conductors shall be made using nickel plated double compression brass cable glands, copper compression type cable sockets, PVC insulating tapes, etc. For cables below 10 mm2, the sockets are not necessary. |  |  | VENDER TO SPECIFY
4.15.9.3.7 | The contractor shall prepare his shop drawings showing the proposed cable tray and cable layouts, method of laying and supporting, etc. These shop drawings shall be submitted to the Consultants for approval before starting the work. |  |  | VENDER TO SPECIFY
4.15.10 | False ceiling
4.15.10.1 | General
4.15.10.1.1 | The false ceiling shall be provided at the height of App. 11.00 meter from the ground floor. |  |  | VENDER TO CONFIRM
4.15.10.1.2 | Providing and fixing of false ceiling in plaster of paris shaeet with G.I.section with bottoms putty and runners in proper line level with proper finishing including all material and labour etc. complete. |  |  | VENDER TO CONFIRM
4.15.11 | Insulation on side wall
4.15.11.1 | Providing and fixing insulation for side wall and top above the ceiling in glass wool with all material and labour etc. complete. |  |  | VENDER TO CONFIRM
5 | PERFORMANCE TESTS
5.1 | General
5.1.1 | After installation, initial testing and successful commissioning of all equipment as per the Technical Specifications, the performance tests shall be carried out to establish the equipment ratings. |  |  | VENDER TO CONFIRM
5.1.2 | All equipment capacities shall be computed from temperature/ pressure readings and water flow measurements, whereas power consumption shall be computed from voltage, current and power factor measurements. |  |  | VENDER TO CONFIRM
5.1.3 | The contractor shall arrange at his cost all instruments required for the performance tests. They shall be properly calibrated and the calibration certificates shall be furnished to the HVAC Consultants for approval before starting the performance tests. |  |  | VENDER TO CONFIRM
5.1.4 | The computed results shall tally with the capacity and power consumption figures furnished in the tender. All equipment shall be guaranteed for specified ratings with + 3% tolerance. |  |  | VENDER TO CONFIRM
5.1.5 | The performance tests shall be carried out during peak summer and monsoon. The performance test shall be for ten hours on seven consecutive days in each season. All tests shall be carried out in the presence of the Owner’s representative. |  |  | VENDER TO CONFIRM
5.1.6 | All safety and control instruments shall be checked for proper operation. At least four sets of readings shall be taken on each day and for each item. The test readings shall be acceptable only if steady conditions of temperature/ pressure, water flow rates and voltage, current and power factor prevail for at least 15 minutes before taking each set of readings. |  |  | VENDER TO CONFIRM
5.1.7 | The test readings and the computed test results shall be properly recorded and furnished to the Consultants for approval. |  |  | VENDER TO CONFIRM
5.2 | Performance Test Readings
5.2.1 | The following readings for each equipment or area shall be recorded during the performance tests and shall be used to check the compliance with the specified conditions. The date, time and ambient conditions shall also be recorded. |  |  | VENDER TO CONFIRM
5.3 | Water chilling unit
| Ambient air temperature (OC) |  |  | VENDER TO CONFIRM
| Cooler entering water temperature (OC) |  |  | VENDER TO CONFIRM
| Cooler leaving water temperature (OC) |  |  | VENDER TO CONFIRM
| Cooler entering water pressure (kg/ cm2) |  |  | VENDER TO CONFIRM
| Cooler leaving water pressure (kg/ cm2) |  |  | VENDER TO CONFIRM
| Input current (A) |  |  | VENDER TO CONFIRM
| Supply voltage (V) |  |  | VENDER TO CONFIRM
| Power factor |  |  | VENDER TO CONFIRM
5.4 | Water circulating pumps |  |  | VENDER TO CONFIRM
| Pump discharge pressure (kg/ cm2) |  |  | VENDER TO CONFIRM
| Pump water flow rate (l/ m) |  |  | VENDER TO CONFIRM
| Pump motor current (A) |  |  | VENDER TO CONFIRM
| Supply voltage (V) |  |  | VENDER TO CONFIRM
5.5 | Air handling units
| Coil face area (m2) |  |  | VENDER TO CONFIRM
| Coil face velocity (m/ s) |  |  | VENDER TO CONFIRM
| Coil entering air dry bulb temperature (OC) |  |  | VENDER TO CONFIRM
| Coil entering air wet bulb temperature (OC) |  |  | VENDER TO CONFIRM
| Coil leaving air dry bulb temperature (OC) |  |  | VENDER TO CONFIRM
| Coil leaving air wet bulb temperature (OC) |  |  | VENDER TO CONFIRM
| Motor current (A) |  |  | VENDER TO CONFIRM
| Supply voltage (V) |  |  | VENDER TO CONFIRM
5.6 | Air cooling units
| Filter face area (m2) |  |  | VENDER TO CONFIRM
| Filter face velocity (m/ s) |  |  | VENDER TO CONFIRM
| Humidifier entering air dry bulb temperature (OC) |  |  | VENDER TO CONFIRM
| Humidifier leaving air dry bulb temperature (OC) |  |  | VENDER TO CONFIRM
| Motor current (A) |  |  | VENDER TO CONFIRM
| Supply voltage (V) |  |  | VENDER TO CONFIRM
5.7 | Automatic controls
| Check the working of automatic controls and instruments. |  |  | VENDER TO CONFIRM
5.8 | Sheet metal work
| Check for air leakage. |  |  | VENDER TO CONFIRM
| Check the working of dampers. |  |  | VENDER TO CONFIRM
5.9 | Pipe work
| Check for water leakage. |  |  | VENDER TO CONFIRM
| Check the working of valves. |  |  | VENDER TO CONFIRM
| Check the working of strainers. |  |  | VENDER TO CONFIRM
| Check the working of centrifugal sediment separators. |  |  | VENDER TO CONFIRM
| Check the working of closed pressurized expansion tank. |  |  | VENDER TO CONFIRM
| Check the working of centrifugal air separator. |  |  | VENDER TO CONFIRM
| Check the working of all instruments. |  |  | VENDER TO CONFIRM
5.1 | Insulation
| Water temperature at the outlet of the cooler (OC) |  |  | VENDER TO CONFIRM
| Water temperature at the inlet to the farthest air handling unit (OC) |  |  | VENDER TO CONFIRM
| Air temperature at the outlet of each air handling unit (OC) |  |  | VENDER TO CONFIRM
| Air temperature at the corresponding farthest grill (OC) |  |  | VENDER TO CONFIRM
| Sound level outside the air handling unit room (dBA) |  |  | VENDER TO CONFIRM
| Check for sweating. |  |  | VENDER TO CONFIRM
6 | TECHNICAL DATA TO BE SUBMITTED WITH TENDER
6.1 | General
6.1.1 | The bidder shall furnish complete information about all equipment and materials offered. |  |  | VENDER TO SPECIFY
6.1.2 | The tender shall be accompanied by two sets of technical literature giving full description of equipment and materials offered. |  |  | VENDER TO SPECIFY
6.1.3 | The model numbers, if any, of the equipment offered shall be clearly marked on the technical literature. |  |  | VENDER TO SPECIFY
6.2 | Technical Data
6.2.1 | In addition to the technical literature, the following technical details of the equipment and materials offered shall be furnished with the tender. |  |  | VENDER TO SPECIFY
6.3 | Water chilling unit
6.3.1 | Water chilling unit make and model number |  |  | VENDER TO SPECIFY
6.3.2 | Compressor make and model number |  |  | VENDER TO SPECIFY
6.3.3 | Compressor type |  |  | VENDER TO SPECIFY
6.3.4 | Number of compressors per unit |  |  | VENDER TO SPECIFY
6.3.5 | Type of lubrication |  |  | VENDER TO SPECIFY
6.3.6 | Operating speed (rpm) |  |  | VENDER TO SPECIFY
6.3.7 | Type of drive |  |  | VENDER TO SPECIFY
6.3.8 | Compressor motor make, type and rating (kW) |  |  | VENDER TO SPECIFY
6.3.9 | Type of starter |  |  | VENDER TO SPECIFY
6.3.10 | Condenser make and model number |  |  | VENDER TO SPECIFY
6.3.11 | Condenser coil tube material, diameter and thickness (mm) |  |  | VENDER TO SPECIFY
6.3.12 | Condenser coil fin material and spacing (fins/ m) |  |  | VENDER TO SPECIFY
6.3.13 | Condenser fan type and diameter (mm) |  |  | VENDER TO SPECIFY
6.3.14 | Condenser fan motor make, type and rating (kW) |  |  | VENDER TO SPECIFY
6.3.15 | Condenser air flow rate (m3/ h) |  |  | VENDER TO SPECIFY
6.3.16 | Cooler make and model number |  |  | VENDER TO SPECIFY
6.3.17 | Cooler shell material, diameter, length and thickness (mm) |  |  | VENDER TO SPECIFY
6.3.18 | Cooler tube material and fin spacing (fins/ m) |  |  | VENDER TO SPECIFY
6.3.19 | Cooler tube diameter, length and thickness (mm) |  |  | VENDER TO SPECIFY
6.3.20 | Number of tubes in each cooler |  |  | VENDER TO SPECIFY
6.3.21 | Inside and outside tube surface of each cooler (m2) |  |  | VENDER TO SPECIFY
6.3.22 | Cooler water flow rate (m3/ h) |  |  | VENDER TO SPECIFY
6.3.23 | Cooler water pressure drop (m) |  |  | VENDER TO SPECIFY
6.3.24 | Cooler entering water temperature (OC) |  |  | VENDER TO SPECIFY
6.3.25 | Cooler leaving water temperature (OC) |  |  | VENDER TO SPECIFY
6.3.26 | Oil to be used and quantity (kg) |  |  | VENDER TO SPECIFY
6.3.27 | Refrigerant to be used and quantity (kg) |  |  | VENDER TO SPECIFY
6.3.28 | Cooling capacity at operating conditions (kcal/ h) |  |  | VENDER TO SPECIFY
6.3.29 | Power consumption at operating conditions (kW) |  |  | VENDER TO SPECIFY
6.3.30 | Overall length, width and height (m) |  |  | VENDER TO SPECIFY
6.3.31 | Service clearance required on all sides (m) |  |  | VENDER TO SPECIFY
6.3.32 | Operating weight (kg) |  |  | VENDER TO SPECIFY
6.3.33 | Type of foundation required |  |  | VENDER TO SPECIFY
6.4 | Water circulating pumps
6.4.1 | Make and model number |  |  | VENDER TO SPECIFY
6.4.2 | Material of construction |  |  | VENDER TO SPECIFY
6.4.3 | Pump speed (rpm) |  |  | VENDER TO SPECIFY
6.4.4 | Pump motor make, type and rating (kW) |  |  | VENDER TO SPECIFY
6.4.5 | Water flow rate (l/ m) |  |  | VENDER TO SPECIFY
6.4.6 | Total head (m) |  |  | VENDER TO SPECIFY
6.4.7 | Pump efficiency (%) |  |  | VENDER TO SPECIFY
6.4.8 | Power consumption at operating conditions (kW) |  |  | VENDER TO SPECIFY
6.4.9 | Overall length, width and height and operating weight (m, kg) |  |  | VENDER TO SPECIFY
6.4.10 | Service clearance required on all sides (m) |  |  | VENDER TO SPECIFY
6.5 | Air handling units
6.5.1 | Make and model number |  |  | VENDER TO SPECIFY
6.5.2 | Material of construction |  |  | VENDER TO SPECIFY
6.5.3 | Number of fan wheels, fan wheel type, diameter and width (mm) |  |  | VENDER TO SPECIFY
6.5.4 | Fan speed (rpm) |  |  | VENDER TO SPECIFY
6.5.5 | Motor make, type and rating (kW) |  |  | VENDER TO SPECIFY
6.5.6 | Total air flow rate and total static pressure (m3/ h, mm of water gauge) |  |  | VENDER TO SPECIFY
6.5.7 | Power consumption at operating conditions (kW) |  |  | VENDER TO SPECIFY
6.5.8 | Coil length and height (mm) |  |  | VENDER TO SPECIFY
6.5.9 | Number of rows in coil depth and number of tubes in coil face |  |  | VENDER TO SPECIFY
6.5.10 | Coil tube material, diameter and thickness (mm) |  |  | VENDER TO SPECIFY
6.5.11 | Coil fin material, thickness and fin spacing (mm, fins/ m) |  |  | VENDER TO SPECIFY
6.5.12 | Coil face velocity and air pressure drop across coil (m/ s, mm of water gauge) |  |  | VENDER TO SPECIFY
6.5.13 | Coil entering water temperature (OC) |  |  | VENDER TO SPECIFY
6.5.14 | Coil leaving water temperature (OC) |  |  | VENDER TO SPECIFY
6.5.15 | Water flow rate (l/ m) |  |  | VENDER TO SPECIFY
6.5.16 | Water pressure drop in coil (m of water column) |  |  | VENDER TO SPECIFY
6.5.17 | Total cooling capacity at operating conditions (kcal/ h) |  |  | VENDER TO SPECIFY
6.5.18 | Number and length, width and thickness of air filters (mm) |  |  | VENDER TO SPECIFY
6.5.19 | Filter media and filtration efficiency (%) |  |  | VENDER TO SPECIFY
6.5.20 | Filter face velocity and pressure drop across filters (m/ s, mm of water gauge) |  |  | VENDER TO SPECIFY
6.5.21 | Overall length, width and height and operating weight (m, kg) |  |  | VENDER TO SPECIFY
6.5.22 | Service clearance required on all sides (m) |  |  | VENDER TO SPECIFY
6.6 | Air cooling units
6.6.1 | Make and model number |  |  | VENDER TO SPECIFY
6.6.2 | Material of construction |  |  | VENDER TO SPECIFY
6.6.3 | Number of fan wheels, fan wheel type, diameter and width (mm) |  |  | VENDER TO SPECIFY
6.6.4 | Fan speed (rpm) |  |  | VENDER TO SPECIFY
6.6.5 | Motor make, type and rating (kW) |  |  | VENDER TO SPECIFY
6.6.6 | Total air flow rate and total static pressure (m3/ h, mm of water gauge) |  |  | VENDER TO SPECIFY
6.6.7 | Power consumption at operating conditions (kW) |  |  | VENDER TO SPECIFY
6.6.8 | Material and make of humidifier pads |  |  | VENDER TO SPECIFY
6.6.9 | Make and model number of water circulation pump |  |  | VENDER TO SPECIFY
6.6.10 | Water flow rate and head (m3/ h, m of water column) |  |  | VENDER TO SPECIFY
6.6.11 | Number and length, width and thickness of air filters (mm) |  |  | VENDER TO SPECIFY
6.6.12 | Filter media and filtration efficiency (%) |  |  | VENDER TO SPECIFY
6.6.13 | Filter face velocity and pressure drop across filters (m/ s, mm of water gauge) |  |  | VENDER TO SPECIFY
6.6.14 | Overall length, width and height and operating weight of complete unit (m, kg) |  |  | VENDER TO SPECIFY
6.6.15 | Service clearance required on all sides (m) |  |  | VENDER TO SPECIFY
6.7 | Automatic Controls
6.7.1 | Make and model number of three – way modulating valves |  |  | VENDER TO SPECIFY
6.7.2 | Make and model number of thermostats |  |  | VENDER TO SPECIFY
6.7.3 | Make and model number of flow switches |  |  | VENDER TO SPECIFY
6.7.4 | Sheet metal work
6.7.5 | Make of galvanised steel sheets |  |  | VENDER TO SPECIFY
6.7.6 | Make of duct dampers |  |  | VENDER TO SPECIFY
6.7.7 | Make of grills |  |  | VENDER TO SPECIFY
6.8 | Pipe Work
6.8.1 | Make of pipes |  |  | VENDER TO SPECIFY
6.8.2 | Make of valves |  |  | VENDER TO SPECIFY
6.8.3 | Make of strainers |  |  | VENDER TO SPECIFY
6.8.4 | Make of closed pressurised expansion tank |  |  | VENDER TO SPECIFY
6.8.5 | Make of centrifugal air separator |  |  | VENDER TO SPECIFY
6.8.6 | Make of flexible connectors |  |  | VENDER TO SPECIFY
6.8.7 | Make and model number of pressure gauges |  |  | VENDER TO SPECIFY
6.8.8 | Make and model number of thermometers |  |  | VENDER TO SPECIFY
6.9 | Insulation |  |  | VENDER TO SPECIFY
6.9.1 | Make and type of material
6.9.2 | Material density and thickness (kg/ m3, mm) |  |  | VENDER TO SPECIFY
6.9.3 | Thermal conductivity (kcal/ h – cm – 0 K) |  |  | VENDER TO SPECIFY
6.1 | Electrical Work
6.10.1 | Make of main distribution board |  |  | VENDER TO SPECIFY
6.10.2 | Make of copper cables and wires |  |  | VENDER TO SPECIFY
6.10.3 | Make of moulded case breakers |  |  | VENDER TO SPECIFY
6.10.4 | Make of miniature circuit breakers |  |  | VENDER TO SPECIFY
6.10.5 | Make of starter components |  |  | VENDER TO SPECIFY
6.10.6 | Make of earth leakage circuit breakers |  |  | VENDER TO SPECIFY
6.10.7 | Make of indicating lamps |  |  | VENDER TO SPECIFY
6.10.8 | Make of voltmeters/ ammeters |  |  | VENDER TO SPECIFY
7 | Provisions to be given by BHEL
7.1 | Bidder have to give preliminary civil drawing for civil work to be carried out by BHEL. This include AHU room size for air-conditioning of New winding shop. |  |  | VENDER TO CONFIRM
7.1 | Bidder have to explicitly mark in the preliminary drawing to be submitted in the technical-bid, for SA & RA Duct opening in PUF Wall, Duct Hangers, Supports, Foundation, etc. Also, provide condensate Drain Pipe sizes & its removal in the Main Drain. |  |  | VENDER TO CONFIRM
7.1 | Bidder have to give total requirement of electrical point, water, air, etc. at one point. |  |  | VENDER TO CONFIRM
7.1 | Bidder have to clearly indicate any other requirement from BHEL in the technical offer, otherwise it will be assumed that any future requirement to complete the work on TURNKEY basis will be in the scope of the contractor. |  |  | VENDER TO CONFIRM
8 | QUALIFYING CONDITION
8.1 | Only those venders, who have supplied and commissioned at least Two numbers Air conditioning system of 150 TR capacity or higher rating for block or similar application in the past ten year and such systems are presently working satifactorily for more then one year (more then six months if supplied to BHEL) after commmssioning, should quote. The following information is to be submitted by the Vender about the companies where Air conditioning systems have been supplied. This is required from all the venders for qualification of their offer. Documentary support pertaining to following points shall submitted with the offer to justify the claim of qualification: |  |  | VENDER TO SPECIFY
| 1 . Name of the customer / company where similar system is installed. (copy of purchase order to be furnised) |  |  | VENDER TO SPECIFY
| 2 . Complete postal address of the customer. |  |  | VENDER TO SPECIFY
| 3. Year of suppling / commissioning. |  |  | VENDER TO SPECIFY
| 4 . Application for which system is supplied with details of accuracies achived on the job. |  |  | VENDER TO SPECIFY
| 5 . Name and designation of the contact person of the customer. |  |  | VENDER TO SPECIFY
| 6 . Phone. FAX, no and E-mail address of the contact person of fhe customer. |  |  | VENDER TO SPECIFY
| 7 . Performance certificate from the customer regarding satisfactory performance of system supplied to them. If performance certificate is not available, commissioning reports of such plants to be submitted. |  |  | VENDER TO SPECIFY
| 8. BHEL reserves the right to verify information submited by vender. In case the information is found to be false/ incorrect, the offer shall be rejected. |  |  | VENDER TO CONFIRM
Prepared by |  |  | Checked by | Approved by
Inder Mathur |  | S.C.Srivastava | S.J.Chakraborty | A.K.Srivastava
Manager (WE&S) |  | Sr. Manager (WE&S) | DGM (WE&S) | AGM (FW)