## Sheet1
BHARAT HEAVY ELECTRICAL LIMITED, JHANSI
|  |  | Specification No. | 9230 R2
|  |  | Item No. | SP/ELEC/9230
|  |  | Location | Bay-9 ( Power Testing )
|  |  | Quantity | 1 No.
SCOPE :
SUPPLY , ERECTION & COMMISSIONING OF 2 MVA MOTOR GENERATOR SET, COMPLYING AS PER SPECIFICATION BELOW
NOTE :
1 | VENDOR must submit complete information against clause No. 18.0 ( Qualifying condition). The offer meeting this clause would only be processed.
2 | The " offered" Column and where applicable, the " Deviations" Column of this format shall be filled in by the Vender and submitted along with the offer.Technical details also submitted with the offer. Inadequate / incomplete, ambiguous, or unsustainable information against any of the clauses of the specification / requirements shall be treated as non - compliance.
3 | The offer and all documents enclosed with offer should be in English language only.
SPECIFICATION CUM COMPLIANCE CERTIFICATE OF 2 MVA MOTOR GENERATOR SET
S.NO. | DESCRIPTION FOR BHEL REQUIREMENT |  |  | SPECIFIED / TO BE CONFIRMED BY VENDER | OFFERED | DEVIATIONS
1 | PURPOSE & WORK PIECE MATERIAL:
1.1 | Design, Engineering, Manufacturing, supply , installation, testing and commissioning of 2 MVA Motor Generator set. The set is required for the testing of various tranformers. |  |  | VENDER TO CONFIRM
1.2 | 2 MVA MG SET is required for testing of 250 MVA 220kV class 3 phase Power Transformers & 105 MVA 220 /11 kV single Phase Power Transformers. Details of following various tests are required to be performed with the above Set. |  |  | VENDER TO CONFIRM
1.2.1 | No Load Loss measurement up to 200 KW for 3 phases Power Transformers at 50 /60 Hz. |  |  | VENDER TO CONFIRM
1.2.2 | No load Loss measurement up to 40 KW for single phase Power Transformers at 50 /60 Hz. |  |  | VENDER TO CONFIRM
1.2.3 | Induced Over Voltage Test & Partial Discharge Measurement at the frequency from 100 Hz to 160 Hz for all Power Transformers up to 250 MVA, 220 kV class for 30 minutes. |  |  | VENDER TO CONFIRM
1.2.4 | Over Excitation and Partial Discharge measurements at 100 to 125% of rated voltage of Power Transformers feeding from LV side at 70 Hz to 80 Hz for 12 hours . |  |  | VENDER TO CONFIRM
1.3 | During testing of No Load Loss , Load Loss Test, the frequency and the voltage of the alternator should not drop at any load. |  |  | VENDER TO CONFIRM
1.4 | The same Power Output i.e. 2 MVA shall be available at all four combinations of excitation winding( Series – Star:11kV/105 Amp, series – Parallel : 5.5kV/210 Amp, delta – Series: 6.35 kV/182 Amp & Delta Parallel :3.175kV/364Amp) of winding Change Over. |  |  | VENDER TO CONFIRM
1.5 | Once the frequency is fixed/ selected at particular voltage for a particular test then frequency should not drop at load. |  |  | VENDER TO CONFIRM
1.6 | The noise level of the MG Set is to be as per IS 12065 and its vibration level should also be as per IS 12075. |  |  | VENDER TO CONFIRM
1.7 | The winding of alternator should be suitable to achieve the minimum possible PD level so as not to affect the Test of Power Transformers, during testing of Transformers. |  |  | VENDER TO CONFIRM
1.8 | Harmonic level shall not exceed 1.5 % THF at rated output. |  |  | VENDER TO CONFIRM
1.9 | Max stator winding Temp Rise at rated load, voltage frequency 90°C. |  |  | VENDER TO CONFIRM
1.1 | Max Rotor winding Temp Rise at rated load, voltage frequency 100°C. |  |  | VENDER TO CONFIRM
1.11 | Suitable rating plate indicating detailed specification on each items. |  |  | VENDER TO CONFIRM
1.12 | Supplier has to furnish tentative OGA drawings for civil work. |  |  | VENDER TO CONFIRM
1.13 | Block diagram and general arrangement drawings shall be submitted. |  |  | VENDER TO CONFIRM
1.14 | All items shall be capable for indoor operation. |  |  | VENDER TO CONFIRM
1.15 | Total weight of total assembly to be submitted along with offer. |  |  | VENDER TO CONFIRM
1.16 | Supplier to conduct Routine / Type Test in presence of BHEL representative. Supplier has to submit results of test conducted. |  |  | VENDER TO CONFIRM
1.17 | Type test can be waived off if supplier submits similar test report. |  |  | VENDER TO CONFIRM
1.18 | Supplier will give all fastening hardware for necessary foundation. IS 4722. |  |  | VENDER TO SPECIFY
1.19 | Power supply requ9rement for Generator Excitation & A.C Variable speed drive for motor shall be clearly indicated in the offer. |  |  | VENDER TO SPECIFY
1.2 | Temp Sensors shall be provided at suitable locations of the Generator & Motor for safety and protection. Location of these sensors shall be clearly indicated in the offer |  |  | VENDER TO SPECIFY
1.21 | General Term & Condition will be as per IS 4722. |  |  | VENDER TO CONFIRM
1.22 | Supplier to furnish switchgear details and make for 2MVA. along with the equipment list seperately. |  |  | VENDER TO SPECIFY
1.23 | Details of accessories are also to be furnished. |  |  | VENDER TO SPECIFY
2 | EQUIPMENT CONFIGURATION :- 2 MVA MG SET consist of suitable A.C. drive Motor & A.C. Generator mounted on a common torsion free bed plate fully aligned together and having following 4 winding combination from generator. All the coupling should be properly covered. Suitable holes for anchoring the same in concrete to be provided. M.G.Set shall complete with Control panels,motor, & generator breakers, winding change over panel, power and control cables and other accecessaries. Complete set shall be of an " State of art" latest design & technology. |  |  | VENDER TO CONFIRM
2.1 | MOTOR
2.1.1 | The motor shall be suitable for generator operation. Motor shall be A.C. drive motor |  |  | VENDER TO CONFIRM
2.1.2 | Following details to be submitted:
2.1.2.1 | Motor rating 550 KW Minimum |  |  | VENDER TO CONFIRM
2.1.2.2 | Supply voltage (available) 1KV ±6% 3Phase 50HZ AC
2.1.2.3 | Rated voltage of Motor |  |  | VENDER TO SPECIFY
2.1.2.4 | Rated speed - 0 - 1500 RPM |  |  | VENDER TO CONFIRM
2.1.2.5 | Class of insulation - F |  |  | VENDER TO SPECIFY
2.1.2.6 | Duty - Continious |  |  | VENDER TO SPECIFY
2.1.2.7 | Cooling - Forced air cooled |  |  | VENDER TO CONFIRM
2.1.2.8 | Noise level - As per IS 12065 |  |  | VENDER TO CONFIRM
2.1.2.9 | Accessories |  |  | VENDER TO SPECIFY
2.1.2.10 | Details of motor, make with technical literature to be submitted with the offer |  |  | VENDER TO SPECIFY
2.1.2.11 | Over voltage - 1.1 Times of rated voltage |  |  | VENDER TO CONFIRM
2.1.2.12 | Under voltage - 0.9 Times of rated voltage |  |  | VENDER TO CONFIRM
2.1.2.13 | Over speed - 1.2 Times of Max. speed |  |  | VENDER TO CONFIRM
2.1.2.14 | Occasional excess current- 1.5 Times rated current for 15 sec. |  |  | VENDER TO CONFIRM
2.1.2.15 | Momentary excess torque - 1.5 Times the rated torque |  |  | VENDER TO CONFIRM
2.1.2.16 | Temperature rise - As per IS 12802 |  |  | VENDER TO CONFIRM
2.1.2.17 | Pull up torque - 0.3 Times the rated torque & 0.5 times he locked rotor torque |  |  | VENDER TO CONFIRM
2.1.2.18 | Ambient temp. - 45 ºC |  |  | VENDER TO CONFIRM
2.1.2.19 | Altitude - >1000 mtr MSL |  |  | VENDER TO CONFIRM
2.1.2.20 | Vibration measurement - As per IS 12075 |  |  | VENDER TO CONFIRM
2.1.2.21 | Protection - IP 23 |  |  | VENDER TO CONFIRM
2.2 | MOTOR BREAKER PANEL
2.2.1 | Motor breaker panel shall be suitable for the incoming supply to drive motor. |  |  | VENDER TO CONFIRM
2.2.2 | Following details to be submitted:
2.2.2.1 | Rating |  |  | VENDER TO SPECIFY
2.2.2.2 | Breaking capacity |  |  | VENDER TO SPECIFY
2.2.2.3 | No. of Phases - 3 |  |  | VENDER TO SPECIFY
2.2.2.4 | Voltage - 11KV, 50 ±3% HZ, 3 Pahse (Availbale) |  |  | VENDER TO SPECIFY
2.2.2.5 | Protection- Over current and earth fault |  |  | VENDER TO SPECIFY
2.2.2.6 | Metering - Voltage and current |  |  | VENDER TO SPECIFY
2.2.2.7 | Accessories - CT's and PT's |  |  | VENDER TO SPECIFY
2.2.2.8 | Cable entry - Bottom |  |  | VENDER TO SPECIFY
2.2.2.9 | Auxilary contacts- 8 NO + 8 NC |  |  | VENDER TO SPECIFY
2.2.2.10 | Shunt trip |  |  | VENDER TO SPECIFY
2.3 | TRANSFORMER
2.3.1 | Suitable transformer shall be provided for the operation of A.C. Drive motor |  |  | VENDER TO CONFIRM
2.3.2 | Following details to be submitted:
2.3.2.1 | Rating of transformer |  |  | VENDER TO SPECIFY
2.3.2.2 | Primary voltage - 11KV, 50 ±3%Hz, 3 Phase (Available) |  |  | VENDER TO SPECIFY
2.3.2.3 | Secondary voltage |  |  | VENDER TO SPECIFY
2.3.2.4 | Duty of transformer - continuous |  |  | VENDER TO SPECIFY
2.3.2.5 | Vector group |  |  | VENDER TO SPECIFY
2.3.2.6 | Installation - Out door |  |  | VENDER TO SPECIFY
2.3.2.7 | Accessories |  |  | VENDER TO SPECIFY
2.3.2.8 | Tappings |  |  | VENDER TO SPECIFY
2.3.2.9 | Cooling of transformer |  |  | VENDER TO SPECIFY
2.3.2.10 | Termination boxes - both for HT and LT |  |  | VENDER TO SPECIFY
2.4 | D.C.DRIVE
2.4.1 | Suitable drive shall be provided for A.C.Drive motor |  |  | VENDER TO CONFIRM
2.4.2 | Following details to be submitted:
2.4.2.1 | Rated current |  |  | VENDER TO SPECIFY
2.4.2.2 | Rated in put voltage |  |  | VENDER TO SPECIFY
2.4.2.3 | Rated output voltage |  |  | VENDER TO SPECIFY
2.4.2.4 | Range of speed control |  |  | VENDER TO SPECIFY
2.4.2.5 | Direction of rotation |  |  | VENDER TO SPECIFY
2.4.2.6 | Bridge configuration |  |  | VENDER TO SPECIFY
2.4.2.7 | Control system |  |  | VENDER TO SPECIFY
2.4.2.8 | Field control |  |  | VENDER TO SPECIFY
2.4.2.9 | Cooling of converters |  |  | VENDER TO CONFIRM
2.4.2.10 | Provision for local and remote control |  |  | VENDER TO CONFIRM
3 | A.C. GENERATOR
3.1 | 2 MVA rating 3 phase, 50 Hz A.C. generator shall be provided (standard to be used IS- 4722 -2001) |  |  | VENDER TO CONFIRM
3.1.1 | Following details to be submitted:
3.1.1.1 | Rating of A.C.Generator - 2MVA 3 Phase at all frequencies |  |  | VENDER TO CONFIRM
3.1.1.2 | Rated voltage - 0- 11 KV (variable) |  |  | VENDER TO CONFIRM
3.1.1.3 | Frequency - 0- 200 HZ (Variable frequency) |  |  | VENDER TO CONFIRM
3.1.1.4 | Rated speed - 0- 1500 RPM |  |  | VENDER TO CONFIRM
3.1.1.5 | Out put current at 11KV - 105 Amp. |  |  | VENDER TO CONFIRM
3.1.1.6 | Power factor - 0.15 Max. at al load |  |  | VENDER TO CONFIRM
3.1.1.7 | No. of poles - 8/16 |  |  | VENDER TO SPECIFY
3.1.1.8 | Excitor |  |  | VENDER TO SPECIFY
3.1.1.9 | Excitation - Brushless |  |  | VENDER TO CONFIRM
3.1.1.10 | Insulation - F |  |  | VENDER TO CONFIRM
3.1.1.11 | Duty - Continuous |  |  | VENDER TO CONFIRM
3.1.1.12 | Cooling - Forced air cooled / water cooled |  |  | VENDER TO SPECIFY
3.1.1.13 | Bearing -Sleeve type |  |  | VENDER TO SPECIFY
3.1.1.14 | Accessories |  |  | VENDER TO SPECIFY
3.1.1.15 | Over voltage - 1.1 times of rated voltage |  |  | VENDER TO CONFIRM
3.1.1.16 | Over speed - 1.2 Times of Max. speed |  |  | VENDER TO CONFIRM
3.1.1.17 | Temperature rise - As per IS 12802 |  |  | VENDER TO CONFIRM
3.1.1.18 | Breakdown torque - As per IS - 4722 |  |  | VENDER TO CONFIRM
3.1.1.19 | Ambient temperature - 45 ºC |  |  | VENDER TO CONFIRM
3.1.1.20 | Altitude - >1000 mtr MSL |  |  | VENDER TO CONFIRM
3.1.1.21 | Harmonic Content - as per IS 4722 |  |  | VENDER TO CONFIRM
3.1.1.22 | Vibration measurement - As per IS 12075 |  |  | VENDER TO CONFIRM
3.1.1.23 | Occasional excess current - 1.5 Times current for 15 sec. as per IS 4722 |  |  | VENDER TO CONFIRM
3.1.1.24 | Type of encloser - IP 44 |  |  | VENDER TO CONFIRM
3.1.1.25 | Partial discharge |  |  | VENDER TO CONFIRM
3.2 | EXCITATION CONTROL PANEL
3.2.1 | Suitable excitation panel for A.C. generator shall be provided to obtain variable out put from Generator (0-11 KV) |  |  | VENDER TO CONFIRM
3.2.2 | Following details to be submitted:
3.2.2.1 | Mounting of panel- on Floor |  |  | VENDER TO SPECIFY
3.2.2.2 | Control provide in the panel (brief description to be submitted) |  |  | VENDER TO SPECIFY
3.2.2.3 | Input supply - 240 Volt A.C. single phase or 415 Volt 3 Phase 50 HZ available |  |  | VENDER TO CONFIRM
3.2.2.4 | Rating of excitation controller |  |  | VENDER TO SPECIFY
3.2.2.5 | Protection |  |  | VENDER TO SPECIFY
3.2.2.6 | Local and remote control - Required |  |  | VENDER TO SPECIFY
3.2.2.7 | Accessories |  |  | VENDER TO SPECIFY
3.3 | GENERATOR BREAKER PANEL
3.3.1 | Generator breaker panel shall be provided suitable for the outgoing supply |  |  | VENDER TO CONFIRM
3.3.2 | Following details to be submitted:
3.3.2.1 | Rating |  |  | VENDER TO SPECIFY
3.3.2.2 | Breaking capacity |  |  | VENDER TO SPECIFY
3.3.2.3 | No. of poles - 3 |  |  | VENDER TO CONFIRM
3.3.2.4 | Voltage rating- 11 KV |  |  | VENDER TO SPECIFY
3.3.2.5 | Protection- Over current and earth fault |  |  | VENDER TO SPECIFY
3.3.2.6 | Metering - Voltage and current |  |  | VENDER TO SPECIFY
3.3.2.7 | Accessories - CT's and PT's |  |  | VENDER TO SPECIFY
3.3.2.8 | Cable entry - Bottom |  |  | VENDER TO CONFIRM
3.3.2.9 | Auxilary contacts- 8 NO + 8 NC |  |  | VENDER TO CONFIRM
3.3.2.10 | Shunt trip - 110 Volt DC |  |  | VENDER TO CONFIRM
4 | WINDING CHANGE OVER PANEL
4.1 | Suitable winding change over panel is required to select the winding of A.C.Generator |  |  | VENDER TO CONFIRM
4.2 | Winding selection shall be star- series, star- parallel, Delta - Parallel, Delta - series connection |  |  | VENDER TO CONFIRM
4.3 | Details of change over panel to be submitted |  |  | VENDER TO SPECIFY
4.4 | Details of out put voltage and current in each selection are as below
| Selection | Voltage | Current/ MVA
4.4.1 | Star - Series | 11 KV | 105 Amp. / 2MVA | VENDER TO CONFIRM
4.4.2 | Star - Parallel | 5.5 KV | 210 Amp. / 2MVA | VENDER TO CONFIRM
4.4.3 | Delta - Series | 6.35 KV | 182 Amp. / 2MVA | VENDER TO CONFIRM
4.4.4 | Delta - Parallel | 3.175 KV | 364 Amp. / 2MVA | VENDER TO CONFIRM
4.5 | In all selection/ combination of winding out power will be -2MVA |  |  | VENDER TO CONFIRM
5 | CABLES
5.1 | All veriety of power and control cable shall be provided for the suitable length of minimum 250 meter, |  |  | VENDER TO SPECIFY
5.2 | Following cables required with the Generator set : Cable sizes and length to be specified by the vender |  |  | VENDER TO SPECIFY
5.2.1 | Cable from Motor breaker to Transformer (11 KV grade of suitable rating), |  |  | VENDER TO SPECIFY
5.2.2 | Cable from Transformer to D.C.Drive panel (Suitable grade & rating) |  |  | VENDER TO SPECIFY
5.2.3 | Cable from D.C.Drive panel to drive motor (suitable grade and rating) |  |  | VENDER TO SPECIFY
5.2.4 | Cable from A.C.Generator to Winding changeover panel (11 KV grade of suitable rating) |  |  | VENDER TO SPECIFY
5.2.5 | Cable from Exitation panel to generator (1.1 KV grade of suitable rating) |  |  | VENDER TO SPECIFY
5.2.6 | Cable form winding change over panel to Generator breaker (11 KV grade of suitable rating) |  |  | VENDER TO SPECIFY
5.2.7 | Control cable ( 1.1 KV grade) |  |  | VENDER TO SPECIFY
6 | SAFETY ARRANGEMENTS:
6.1 | Following safety features in addition to other standard safety features should be provided on the generator |  |  | VENDER TO CONFIRM
6.2 | Generator should have adequate and reliable safety interlocks/ devices to avoid damage to the generator, work piece and the operator due to the malfunctioning or mistakes. Generator functions should be continuously monitored and alarm/warning indications through lights/ alarm number with messages ( on panels ) should be available . |  |  | VENDER TO CONFIRM
6.3 | All the pipes. Cables etc . On the generator should be well supported and protected . |  |  | VENDER TO CONFIRM
6.4 | All the rotating parts used on generator should be statically & dynamically balanced to avoid undue vibrations . |  |  | VENDER TO CONFIRM
6.5 | ELCB/ Earth foult relay to be provided in the the circuit to protect the equipment for Earth fault. |  |  | VENDER TO CONFIRM
6.6 | Emergency Switches at suitable locations as per International Norms are to be provided. |  |  | VENDER TO CONFIRM
7 | ENVIRONMENTAL PERFORMANCE TO THE MACHINE
7.1 | The Generator shall conform to following factors related to environment : |  |  | VENDER TO CONFIRM
7.2 | Total supplied items should work trouble free and efficiently under following operating conditions and should give specified accuracies. Ambient conditions : Temperature = 5 to 45 degree Celsius Relative Humidity = 95% max . (Vendor to confirm that machine is suitable for above and details of provisions on the machine for the same are to be furnished by Vendor ) |  |  | VENDER TO CONFIRM
7.3 | Weather conditions are tropical, Atmosphere may be dust laden during some part of the year. Machine shall be kept in the normal shop floor condition. Max.Temperature variation is up to 25 deg Celsius in 24 hours.( Vendor to confirm that machine is suitable for above and details of provisions on the machine for the same are to be furnished by Vendor |  |  | VENDER TO CONFIRM
7.4 | The generator, including attachments and accessories, should be suitable for 24 Hrs. Continuous operation to its full capacity for 24 Hrs. a day and 7 days a week throughout. Vendor to ensure and confirm the same . |  |  | VENDER TO CONFIRM
7.5 | If any safety / environmental protection enclosure is required it should be built in the machine/ generator by the vendor
7.6 | Paint of the machine/ generator should be oil / coolant resistant and should not peel off. |  |  | VENDER TO CONFIRM
8 | LEVELLING & ANCHORING SYSTEM
8.1 | Complete anchoring system including foundation bolts, anchoring materials, fixators, leveling shoes etc, shall be supplied for the Machine/ generator .
9 | TOOLS FOR ERECTION, OPERATION & MAINTENANCE : |  |  | VENDER TO CONFIRM
9.1 | Special tools and equipment required for erection of the machine/ generator shall be brought by the vendor. Necessary tools like Torque Wrench, Spanners, Keys, grease guns etc for operation and maintenance of the machine should be supplied. List of such tools should be submitted with offer . |  |  | VENDER TO CONFIRM
10 | SPARES : |  |  | VENDER TO CONFIRM
10.1 | Itemised break - up of mechanical, hydraulic, electrical and electronic spares used on the machine/generator in sufficient quantity as per recommendation of Vendor for 2 years of trouble free operation on three shifts continuous running basis should be offered by vender. The list to include following, in addition to other recommended spares :( Unit Price of each item of spare should be offered ) |  |  | VENDER TO CONFIRM
10.2 | Detailed maintenance manual of machine with all drawings of machine assemblies / sub assemblies / parts including electrical/ pneumatic / hydraulic circuit diagrams. All assemblies / sub- assemblies drawings shall be supplied with the part list also. |  |  | VENDER TO CONFIRM
10.3 | Catalogues , O&M manuals of all bought out items including drawings where ever applicable in english lenguage. |  |  | VENDER TO CONFIRM
11 | PROVE OUT OF BHEL COMPONENTS:
11.1 | Complete prove out of M.G.Set shall be done by Vendor at BHEL works to the specified design accuracy. Material for the prove out components shall be provided by BHEL. Vendor shall be fully responsible for prove out of MG set as per BHEL requirements to the full satisfaction of BHEL. |  |  | VENDER TO CONFIRM
12 | M.G.SET ACCEPTANCE: ( Tests / Activities to be performed by Vendor )
12.1 | Tests/Activities should be carried out at supplier's works on the M.G.Set before dispatch : |  |  | VENDER TO CONFIRM
12.1.1 | Geometrical Accuracy Tests
12.1.2 | The M.G.Set should be tested for continuous running of 24 hrs. If any break down occurs during this test, the test should be repeated for 24 hrs from that time. |  |  | VENDER TO CONFIRM
12.1.3 | Routine test as per IS |  |  | VENDER TO CONFIRM
12.1.4 | Type test as per IS
12.2 | Test to be carried out at BHEL works while commissioning the machine :
12.2.1 | Geometrical Accuracy Tests |  |  | VENDER TO CONFIRM
12.2.2 | Full load test to demonstrate |  |  | VENDER TO CONFIRM
12.2.3 | The M.G.set should be tested for continuous running of 24 hrs. If any break down occurs during this test, the test should be repeated for 24 hrs from that time .
12.2.4 | Demonstration of all features of the M.G.set & all accessories to the satisfaction of BHEL for their efficient and effective use. |  |  | VENDER TO CONFIRM
12.2.5 | Job prove out. Minimum three job trial will be taken as per BHEL specifications. |  |  | VENDER TO SPECIFY
12.2.6 | Two weeks supervision of independent operation of M.G.set by BHEL after job prove out . |  |  | VENDER TO SPECIFY
12.2.7 | Training of BHEL M.G.set operators in operation of complete set by the supplier's experts/ engineers during commissioning at BHEL works . |  |  | VENDER TO SPECIFY
12.2.8 | Commissioning of the M.G.Set |  |  | VENDER TO SPECIFY
13 | GENERAL : The vendor should submit the following information : |  |  | VENDER TO SPECIFY
13.1 | Floor area required ( Length, Width, Height ) for complete machine & accessories. |  |  | VENDER TO SPECIFY
13.2 | Painting of M.G.Set / Electrical panels: RAL 6011 Apple green ( Polyurethane paint) |  |  | VENDER TO SPECIFY
13.3 | Total weight of the set |  |  | VENDER TO SPECIFY
13.4 | Weight of heaviest part of the set |  |  | VENDER TO SPECIFY
13.5 | Weight of the heaviest assembly / sub assembly of the set |  |  | VENDER TO SPECIFY
13.6 | Dimensions of largest part / sub assembly / assembly of the set |  |  | VENDER TO SPECIFY
13.7 | Detailed catalogues, sketch/ photograph of the set and accessories/ attachments should be submitted with the offer. |  |  | VENDER TO SPECIFY
13.8 | Hydraulic, pneumatic, water and oil piping should be preferably metallic except places where flexible piping are essential. All the pipes required for the same shall be included in the standard scope of the set |  |  | VENDER TO CONFIRM
14 | TRAINING
14.1 | BHEL persons should be trained at supplier works for mutually agreed period in the area of a - Mechanical, Electrical and electronic maintenance for machine and other supplied equipments b- Operator for machine operation |  |  | VENDER TO CONFIRM
15 | FOUNDATION
15.1 | vendor shall submit the preliminary layout drawing for getting BHEL"s approval within one month from the date of Letter of Intent ( LOI)/P.O. , whichever is earlier . Soil condition data will be furnished by BHEL along with the approval. Complete foundation Design including details, like Static/Dynamic load details etc . and final layout Drawings shall be submitted by the supplier within one month after getting BHEL"s approval . The Layout should consist of all requirements pertaining to complete machine and all accessories including space requirement. BHEL shall construct complete foundation for machine & supplier shall check & approve the same before erection. Vendor should arrange equipment required for the testing of foundation, if required. The vendor shall also indicate detailed specifications of grouting compound and grouting procedure etc. for foundation bolts of the machine. |  |  | VENDER TO SPECIFY
16 | ERECTION & COMMISSIONING
16.1 | Supplier to take full responsibility for carrying out the erection, start up , testing of machine/generator, it's control system & all types of other supplied equipment, machining of test pieces etc. Service requirement like power, air & water shall be provided by BHEL at only one point to be indicated by supplier in their foundation/ layout drawings . Other requirements like crane, lifting tackles etc. shall also be provided by BHEL if availabe. Details of these requirements should be informed by vendor in advance. |  |  | VENDER TO CONFIRM
16.2 | The M.G.set is to be installed on our prepared foundation, details of which will be furnished by manufacturer. |  |  | VENDER TO SPECIFY
16.3 | The offer should include the charges for complete transportation, erection and commissioning of the M.G.Set and auxilary equipments with duration. Your commissioning engineer's services should also be available at site for setting all controls while demonstrating the working of the M.G.set. |  |  | VENDER TO CONFIRM
17 | MISCELLANEOUS
17.1 | The offer should be descriptive and complete. Details of all equipments and accessories with general arrangement drawings and catalogues to be enclosed with the offer. Offer with out complete details are liable to be rejected. |  |  | VENDER TO SPECIFY
17.2 | Firm should give breakup prices of all major items and activities. |  |  | VENDER TO SPECIFY
18 | QUALIFYING CONDITIONS
18.1 | Only those vender, who have supplied and commissioned at least two numbers M.G.Set of 500 KVA or higher capacity in past ten years and such M./G.Sets are presently working satisfactorily for more than one year (more than six month if supplied to BHEL) after commissioning should quote. The following information is to be submitted by the vender about the companies where similar M.G.Sets have been supplied. This is required from venders for qualifications of their offers. |  |  | VENDER TO SPECIFY
| 1 . Name of the customer / company where similar M.G.Set is installed. (copy of purchase order to be furnised) |  |  | VENDER TO SPECIFY
| 2 . Complete postal address of the customer. |  |  | VENDER TO SPECIFY
| 3. Year of suppling / commissioning. |  |  | VENDER TO SPECIFY
| 4 . Application for which M.G.Set is supplied with details of accuracies achived on the job. |  |  | VENDER TO SPECIFY
| 5 . Name and designation of the contact person of the customer. |  |  | VENDER TO SPECIFY
| 6 . Phone. FAX, no andE-mail address of the contact person of fhe customer. |  |  | VENDER TO SPECIFY
| 7 . Performance certificate from the customer regarding satisfactory performance of M.G.Set supplied to them |  |  | VENDER TO SPECIFY
| 8. BHEL reserves the right to verify information submited by vender. In case the information is found to be false/ incorrect, the offer shall be rejected. |  |  | VENDER TO CONFIRM
Prepared by |  |  | Checked by |  | Approved by
Pramod Nograiya |  | Inder Mathur | B. Bhadra | SJC | AKS | VKA
Mgr. (Test) |  | Mgr. (WE&S) | DGM (Test) | DGM (WE&S) | AGM (FW) | AGM (CQX)