SUB BOARD SPEC SHEET 01 OF 02

BHARAT HEAVY ELECTRICALS LIMITED

JHANSI

EQUIPMENT         	:    415 VOLT,3 PHASE 4 WIRE 50 HZ, L.T. SUB BOARD

SPECIFICATION NO. 	:    9233

LOCATION	 	:    BAY-10, BAY-11 & LOCO

QUANTITY	 	 :    NINE NOS.

SPECIFICATION:

Air insulated metal clad totally enclosed rigid floor mounting free standing cubicle type manually operated L.T. Board. The board shall comprise of suitable length of 1250 Amp. TPN Bus bar chamber with copper /aluminum Bus bar with rupturing capacity 31 MVA at 415 volt. Panel should be equipped with the following incoming and out going feeders:-

INCOMING:

- 1 No. 630 Amp. Triple pole neutral switch fuse unit. Make should be L&T / GE power control/C&S/ Siemens only. Model of switch to be confirmed by the supplier.

- 3 Nos. ring type CT with 15 VA burden and 15 T10 class of accuracy with ratio 600-400/5 for metering.

- 0-400-600 dual range 144 mm² with 1.5 class accuracy flush mounting type ammeter with ammeter selector switch.

- 0-500 volt range 144 mm² with 1 class accuracy flush mounting voltmeter with voltmeter selector switch.

- Set of cable termination suitable for 2 Nos. 3½ core 300 mm² AL.conductor PVC/ XLPE  cable with suitable cable gland.

- KWH meter for 3 phase 4 wire 415 volt 50 Hz System suitable for balance and unbalance load condition.

- Operating handle shall be supplied.

OUT GOING

- 3 Nos. 315 Amp. Rating 415 volt 50HZ triple pole 3 phase fuse switch unit with set of cable termination suitable for 1 No. 3½ core 300 mm² AL.conductor PVC/ XLPE  cable with suitable cable gland.

- 3 Nos. 200 Amp. Rating 415 volt 50HZ triple pole 3 phase fuse switch unit with set of cable termination suitable for 1 No. 3½ core 185 mm² AL.conductor PVC/ XLPE  cable with suitable cable gland.

- 3 Nos. 100 Amp. Rating 415 volt 50HZ triple pole 3 phase fuse switch unit with set of cable termination suitable for 1 No. 3½ core 95 mm² AL.conductor PVC/ XLPE  cable with suitable cable gland.

SUB BOARD SPEC SHEET 02 OF 02

- 3 Nos. 63 Amp. Rating 415 volt 50HZ triple pole 3 phase fuse switch unit with set of cable termination suitable for 1 No. 3½ core 50 mm² AL.conductor PVC/ XLPE  cable with suitable cable gland.

GENERAL REQUIREMENT

- The sub board shall be complete light, stream line dust and vermin proof.

- The equipment should be confirmed to relevant IS/BS.

- Aluminum anodized name plate for outgoing circuit shall be screwed in front and back of the panel.

- Barriers for protection against fire between bus sections should be provided.

- Copper earth bus bar of suitable capacity shall be provided inside the panel.

- All the drawing including outline general arrangement shall be submitted to us in

Triplicate for approval before commencement of work.

- At least 15 day advance information should be given to enable us to depute our

Representative for inspection / testing. Dispatch shall be affected only after inspection.

- The equipment shall be guaranteed in respect of material construction and operation against any manufacturing and design defect for a period of 24 months after supply.

- Offer shall be sent with complete literature and necessary details.

- The instruction and maintenance manual should be sent along with the equipments.

- The panel finish should be with Aircraft Grey to ISS shade-693.

- Notwithstanding the details in this specification if any thing else is required for its functioning the same should brought in the notice and included in the offer.

QUALIFYING CONDITION

Only those venders, who are in the line of panel manufacturing or authorized agents of panel manufacturer, shall quote. The following information’s are to be submitted with the offer. This is required from venders for qualifications of their offers.

Name of the panel manufacturer and company profile

Details of manufacturing facilities available at manufacturer works.

Details of test facilities available at manufacturer works.

BHEL reserves the right to verify information submitted by vender. In case the information is found to be false/ incorrect, the offer shall be rejected.

Sujeet Srivastava			Inder Mathur	 		S.J.Chakraborty

Sr. Engineer (WE&S)		Manager(WE&S)		DGM(WE&S)