LTPANEL SPEC SHEET 01 OF 03

BHARAT HEAVY ELECTRICALS LIMITED

JHANSI

EQUIPMENT         	:    415 VOLT,3 PHASE 4 WIRE 50 HZ,L.T. PANEL

SPECIFICATION NO. 	:    9232

INCOMER LT PANEL 	:    QTY. 	3 NOS.

OUTGOING LT PANEL	:    QTY.	10 NOS.

LOCATION		:    NEW SUB-STATION IN WINDING SHOP.

NEW SUB-STATION IN LOCO

1.0	SPECIFICATION:

1.1	Air insulated metal clad totally enclosed rigid floor mounting free standing cubicle type manually operated L.T. Panel for incoming/outgoing circuits. The panel shall comprise of suitable length of 2400 Amp. TPN Bus bar chamber with aluminum Bus bar with rupturing capacity 31 MVA at 415 volt. It should be similar and matched with existing panel installed in sub-station. Size of panel shall be 2140 MM Height, 1620MM Length and 530 MM width (approx.). Panel should be equipped with the following:-

2.0	INCOMER L.T.PANEL     QUANTITY – 3NOS.

  - 1 No. 1600 Amp. Triple pole trip free draw out type air circuit breaker. Make of breaker should be L&T / GE power control/ C&S/Siemens only.

  - Bolted type neutral link.

  - 1600 Amp. Rating fixed and insolating device complete with automatic safety shutters.

  - Shunt release trip coil suitable for 30 volt D.C.

  - 8 way auxiliary switch with 4 NO + 4NC contacts.

  - 3 Nos. ring type epoxy molded CT with 15 VA burden and 15 CM and 15 T10 class of accuracy with ratio 1200-800/5 for instrument and protection.

  - 3 Nos. ring type epoxy molded CT with 15 VA burden 15 T10 class of  accuracy and ratio 1200-800/5 mounted on outgoing bus bar just before cable termination.

  - 1.No. over load relay

  - 1 No. earth fault relay

  - Set of cable termination suitable for 4 NOS 3½ core 300 mm² AL.conductor PVC/ XLPE  cable with suitable cable gland.

  - 0-800-1200 dual range 144 mm² with 1.5 class accuracy flush mounting type ameter with ameter selector switch’s.

  - 0-500 volt range 144 mm² with 1 class accuracy flush mounting voltmeter with voltmeter selector switch.

  - Multifunction KWH meter for 3 phase 4 wire 415 volt 50 Hz System suitable for balance and unbalance load condition.

  - Red and green indication lamp for ON and OFF indication.

LTPANEL SPEC SHEET 02 OF 03

  - Independent manual spring closing mechanism complete with mechanical on and off indication.

  - The copper earth bus bar of suitable capacity shall be provided inside the panel and insulating barrier shall be supplied.

  - Extension Pieces Along with Hardware and Insulating Barrier shall be supplied.

  - Operating handle shall be supplied.

3.0	OUT GOING L.T.PANEL    QUANTITY – 10 NOS.:

  - 1 No. 800 Amp. Triple pole trip free draw out type air circuit breaker. Make of breaker should be L&T / GE power control/ C&S/Siemens only.

  - Bolted type neutral link.

  - 800 Amp. Rating fixed and insolating device complete with automatic safety shutters.

  - Shunt release trip coil suitable for 30 volt D.C.

  - 8 way auxiliary switch with 4 NO + 4NC contacts.

  - 3 Nos. ring type epoxy molded CT with 15 VA burden and 15 CM and 15 T10 class of accuracy with ratio 600-400/5 for instrument and protection.

  - 3 Nos. ring type epoxy molded CT with 15 VA burden 15 T10 class of  accuracy and ratio 600-400/5 mounted on outgoing bus bar just before cable termination.

  - 1.No. over load relay

  - 1 No. earth fault relay

  - Set of cable termination suitable for 2 NOS 3½ core 300 mm² AL.conductor PVC/ XLPE  cable with suitable cable gland.

  - 0-400-600 dual range 144 mm² with 1.5 class accuracy flush mounting type ameter with ameter selector switch’s.

  - 0-500 volt range 144 mm² with 1 class accuracy flush mounting voltmeter with voltmeter selector switch.

  - Multifunction KWH meter for 3 phase 4 wire 415 volt 50 Hz System suitable for balance and unbalance load condition.

  - Red and green indication lamp for ON and OFF indication.

  - Independent manual spring closing mechanism complete with mechanical on and off indication.

  - The copper earth bus bar of suitable capacity shall be provided inside the panel and insulating barrier shall be supplied.

  - Extension Pieces Along with Hardware and Insulating Barrier shall be supplied.

  - Operating handle shall be supplied.

4.0	GENERAL REQUIREMENT

  - The panel shall be complete light, stream line dust and vermin proof.

  - The equipment should be confirmed to relevant IS/BS.

LTPANEL SPEC SHEET 03 OF 03

  - All the drawing including outline general arrangement shall be submitted to us in Triplicate for approval before commencement of work.

  - At least 15 day advance information should be given to enable us to depute our representative for inspection / testing. Dispatch shall be affected only after inspection.

  - Aluminum anodized name plate for outgoing circuit shall be screwed in front and back of the panel.

  - The equipment shall be guaranteed in respect of material construction and operation against any manufacturing and design defect for a period of 24 months after supply.

  - Offer shall be sent with complete literature and necessary details.

  - Notwithstanding the details in this specification if any thing else is required for its functioning the same should brought in the notice and included in the offer.

  - The Offer should be in duplicate with complete technical details.

  - The instruction and maintenance manual should be sent along with the equipments.

  - The panel finish should be with Aircraft Grey to ISS shade-693.

- QUALIFYING CONDITION

  - Only those venders, who are in the line of panel manufacturing or authorized agents of panel manufacturer, shall quote. The following information’s are to be submitted with the offer. This is required from venders for qualifications of their offers.

  - Name of the panel manufacturer and company profile

  - Details of manufacturing facilities available at manufacturer works.

  - Details of test facilities available at manufacturer works.

  - BHEL reserves the right to verify information submitted by vender. In case the information is found to be false/ incorrect, the offer shall be rejected.

Sujeet Srivastava			Inder Mathur	 		S.J.Chakraborty

Sr. Engineer (WE&S)		Manager(WE&S)		DGM(WE&S)