## Sheet1
BHARAT HEAVY ELECTRICAL LIMITED, JHANSI
SPECIFICATION CUM COMPLIANCE CERTIFICATE OF EARTHING SYSTEM
NOTE :
1 | VENDOR must submit complete information against clause No. 8 ( Qualifying condition). The offer meeting this clause would only be processed.
2 | The " offered" Column and where applicable, the " Deviations" Column of this format shall be filled in by the Vender and submitted along with the offer.Technical details also submitted with the offer. Inadequate / incomplete, ambiguous, or unsustainable information against any of the clauses of the specification / requirements shall be treated as non - compliance.
3 | The offer and all documents enclosed with offer should be in English language only.
SCOPE :
SUPPLY , INSTALLATION & TESTING OF EARTHING SYSTEM AS PER SPECIFICATION BELOW
S.NO. | DESCRIPTION FOR BHEL REQUIREMENT |  | SPECIFIED / TO BE CONFIRMED BY | OFFERED | DEVIATIONS
1 | PURPOSE
1.1 | Earthing system required in new shops, sub-station and diesel generator room as per IS 3043 - 1987 with latest amendment. |  | VENDER TO CONFIRM
2 | REQUIREMENT
2.1 | NEW WINDING SHOP : 5 NOS. |  | VENDER TO QUOTE
2.2 | NEW CORE & TANKING SHOP : 5 NOS. |  | VENDER TO QUOTE
2.3 | NEW WINDING SHOP SUB-STATION : 5 NOS. |  | VENDER TO QUOTE
2.4 | NEW DIESEL GENERATOR ROOM : 8 NOS. |  | VENDER TO QUOTE
2.5 | NEW LOCO ASSEMBLY SHOP : 5 NOS |  | VENDER TO QUOTE
2.6 | NEW BOGIE SHOP : 5 NOS. |  | VENDER TO QUOTE
2.7 | NEW LOCO SUB-STATION : 5 NOS. |  | VENDER TO QUOTE
3 | CONSTRUCTION : Maintenance free earthing system to be installed for the protection as per IS 3043 - 1987. The earthing system shall consist of: |  | VENDER TO CONFIRM
3.1 | EARTH ELECTRODE : Earth elctrode shall be Copper bonded steel Electrode 3/4 dia (17.2 mm) length 6 feet of 2 numbers having copper coated with 254 micron. Earth electrode shall be connected with coupler (highly conductive copper silicon alloy compressed) at 6 feet depth below the ground level. |  | VENDER TO CONFIRM
3.2 | CONNECTION BETWEEN EARTH ELCTRODE: 12.5 mm x 3 mm pure copper strip and 40 x5 mm MS strip shall be connected with " UL listed Exothermic weld " to the top of each earth electrodes. The earth electrode shall interconnected by copper strip 25x3 mm as per IEEE 80 & 837, NEFA 780 & MIL-STD 188-124B. |  | VENDER TO CONFIRM
3.3 | EARTH ENHANCEMENT COMPOND : Resistivity of earth enhancement compond shall be less than 0.2 ohms-meter. The compond shall be highly conductive and contains homogenous mixture of chemicals, portland cement. It shall be envirinment frendly, non corrosive, not explosive, not couse burns and irritation to eye, skin etc. The compond shall not contain bentonite, salt and charcoal. |  | VENDER TO CONFIRM
3.4 | QUANTITY OF GROUND ENHANCEMENT MATERIAL: The quantity shall be minimum 30 Kg. for each earth pit |  | VENDER TO CONFIRM
3.5 | EARTH PIT CHAMBER: The earth pit chamber size shall be 300 mm x 300 mm concrete chamber with cast iron cover. |  | VENDER TO CONFIRM
3.6 | TESTING POINT: Earth pit testing point shall be provided at the suitable location inside the building above 900 mm from ground level. |  | VENDER TO CONFIRM
4 | INSTALLATION
4.1 | Installation of complete earthing system shall be in the vender scope. |  | VENDER TO CONFIRM
5 | TESTING |  | VENDER TO CONFIRM
5.1 | Testing shall be done after complition of installation. Final grid resistance of each area shall be measured and shall be with 1 ohm. |  | VENDER TO CONFIRM
6 | LIST OF ITEMS TO BE SUPPLIED IN EACH EARTH PIT |  | VENDER TO CONFIRM
| ITEM DESCRIPTION | QUANTITY | VENDER TO CONFIRM
6.1 | Earthing electrode 17.2 mm dia 6 feet long | 2 Nos. | VENDER TO CONFIRM
6.2 | 17.2 mm coupler | 1 No. | VENDER TO CONFIRM
6.3 | Earth enhancing compound (MEG) 30Kg. Bag | 1 No. | VENDER TO CONFIRM
6.4 | Copper busbar (MEEB) 25 mm x 6mm x 3mm | 1 No. | VENDER TO CONFIRM
6.5 | Copper busbar (SEEB) 25mm x 6 mm x 3 mm | 1 No. | VENDER TO CONFIRM
6.6 | Interconnection 35 sq. mm copper multi strand cable /3/16 inch cadmium cable from 25x6x150 mm (SEEB) to 25x6x300 mm (MEEB) | 1 Meter | VENDER TO CONFIRM
6.7 | Extothermic welding for interconnection
| (a) 17.2 mm Electrode - 25x6x150 mm | 1 No. | VENDER TO CONFIRM
| (b) Interconnection between 25x6x150 mm to 25x6x300 mm | 2 nos. | VENDER TO CONFIRM
6.8 | Inspection chember (1 feet x 1 feet) | 1 No. | VENDER TO CONFIRM
7 | GENERAL
7.1 | The system shall be guaranteed in respect of material construction and operation against any manufacturing and design defect for a period of 24 months after supply. |  | VENDER TO CONFIRM
7.2 | Offer shall be sent with complete literature and necessary details. |  | VENDER TO CONFIRM
7.3 | Price break up shall be given as per specification point No. 6.0 |  | VENDER TO CONFIRM
7.4 | Not withstanding the details in the specification, if anything else is required for its function the same shall be brought out in notice and include in the offer and it should fulfill the standard. |  | VENDER TO CONFIRM
8 | QUALIFYING CONDITION
8.1 | Only those vender, who are in the line of earthing system or authorised agents of company shall quote. |  | VENDER TO SUBMIT
Sujeet Srivastava |  | Inder Mathur | S.J.Chakraborty
Sr. Engineer (WE&S) |  | Manager (WE&S) | DGM (WE&S)