## Sheet1
Bharat Heavy Electricals Limited
Unit: Jhansi
(Works Engg. & Services Deptt.)
Equipment : OIL STORAGE VESSEL
Item No : ME-1/7/2578
Location : BAY-6
Quantity : 1 No
Specification No : 7027A
OIL STORAGE VESSEL: 30 KILO LITRES CAPACITY
1 | OIL STORAGE VESSEL
1.1 | Oil Storage vessel is required for the storing of Shell Diala dx oil for 3 phase fright locos. This vessel will be used for storage and distribution of transformer insulating oil
2 | SCOPE
2.1 | Design, manufacturing and supply of 30KL capacity oil storage vessel.
2.2 | This is to be fabricated from tested rolled steel , properly reinforced with steel sections and complying with the requirements of factory safety act as well as storage vessel safety rules and shall conform to relevant code of practice and BIS standards.
2.3 | The vessel is to be provided with a sump at the bottom for draining the residual oil. The vessel is to be mounted on a base / footing at such a height asto provide sufficient clearance between sump drain connection and ground.
2.4 | The vessel is to be provided with 2 numbers 500 m.m. diameter manholes, one each located on top and bottom and shall be effectively sealed by hinged covers designed to provent ingess of water / moisture is not possible.
2.5 | The vessel shall be provided with an access ladder permanently located inside and outside near the manholes to facilitate maintenance and cleaning. Six number "U" supports made out of circular M.S. bar of 20m.m. diameter (400mm in width & 200mm deep) is to be welded diametrically opposite to the in side ladder and equally spaced over the height.
2.6 | The vessel shall be provided with contents gauge, low and high level indicators.
3 | DETAILS OF OIL STORAGE VESSEL
3.1 | Storage capacity - 30 KL
3.2 | Mounting - Vertically
3.3 | Minimum diameter of the vessel - 2500 mm
3.4 | Shell Thickness - Minimum 8 mm (as per IS : 2062)
3.5 | Tangent length - To be furnished by vender
3.6 | Storage condition - Atmospheric pressure and ambient temperature (4ºC to 60ºC)
4 | FOLLOWING ITEMS TO BE PROVIDED
4.1 | One number 75mm drain pipe at the lowest depth of vessel with necessary ball valves
4.2 | Two 75mm dia oil inlet / out let pipes fixed to the vessel with necessary ball valves
4.3 | One number inspection port on top of the vessel
4.4 | One number 75mm dia over flow pipe
4.5 | Oil level indicator.
5 | PAINTING
5.1 | The internal and external surface to be painted shall be shot or sand blasting to remove all rust and scale or foreign adhering matter or grease.
5.2 | All steel surfaces exposed to weather to be given a primary coat of zinc chromate. Second coat of oil and weather resistant paint. Final two coats of glossy oil and weather resistant light gray paint in accordance with shade No. 631 ofIS:5.
5.3 | The internal surface to be painted with crank case yellow enamel paint. 5.4 All paints shall be carefully selected to withstand heat and extremes of weather.
5.4 | The paint shall not scale off or crinkle or be removed by abrasion due to normal handling.
5.5 | The minimum thickness of outside painting of vessel will be 20 microns per coat and the total thickness will be 40-60 microns.
6 | MISCELLANIOUS
6.1 | Suitable lifting lugs shall be provided for handling the vessel to facilitate erection at site.
6.2 | Drawing showing diameter / height with details of steel like wall thickness dished end thickness to be used shall be provided.
6.3 | Inspection will be carried out at supplier works.
7 | QUALIFYING CONDITION
7.1 | Only those venders, who have supplied and commissioned at least two Nos. storage vessel for similar application in the past ten years and such vessel is presently working satisfactorily for more than one year (more than six month if supplied to BHEL) after Commissioning should quote. The following information is to be submitted by the vender about the companies where similar machines/vessel have been supplied. This is required from venders for qualifications of their offers,
A | Name of the customer/ company where similar machine/plant/vessel is installed 2. Complete postal address of the customer
B | Year of commissioning
C | Name and designation of the contact person of the customer
D | Phone , Fax No. and e.mail address of the contact person of the customer
E | Performance certificate from the customer regarding satisfactory performance of the machine/ plant/ vessel supplied to them
Drafted By | Chacked By |  | Approved
Inder Mathur Mgr(WE&S) | S.J.Chakraborty Incharge Maint | Incharge Production | AGM(FW) | AGM(TRM NPT)