## MAIN SHEET
Price Format
NAME OF PROJECT: |  | 206 MW SHAHPURKANDI HEP
NAME OF PACKAGE: |  | HVAC SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-406-571-11000-A001
[5 empty] | Supply |  |  | Service |  | Taxes
S. No. | DESCRIPTION |  | UNIT | QTY | Total Ex-Works Price | Freight in % | Total Freight | Unit Price | Total Price | GST type | GST rate in % | GST amount | Total Price Including Freight & GST
1 | Total lump sum firm price for Supply part, Services part and Mandatory spares comprising of design (i.e.preparation and submission of drawing /documents including “As Built” drawings and O&M manuals), engineering, manufacture, fabrication, assembly, inspection / testing at vendor's & sub-vendor’s works, painting, maintenance tools & tackles (as applicable) fill of lubricants & consumables, spares alongwith spares for erection, startup and commissioning as required, forwarding, proper packing, shipment and unloading, handling, transportation to stores area & storage, transporation and delivery at site, (from stores area) & in-site transportation, assembly, erection & commissioning, final painting at site, minor civil work, trial run at site and carrying out Performance guarantee / Functional / Demonstration tests at site (As applicable), training of customer/client O&M staff and handover in flawless condition of the package to the end customer complete with all accessories for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. |  | Lot | 1 | [8 empty] | 0
2 | MAJOR BREAK-UP OF PRICES GIVEN IN 1.0 ABOVE.
2.1 | Total lumpsum firm price inclusive of all prevailing taxes, duties and other levies for Design (i.e. Preparation and submission of drawing /documents including “As Built” drawings and O&M manuals) and engineering as per tender technical specification above, amendment & agreements till placement of order. |  | Lot | 1 | NA |  |  |  | 0 |  |  | 0 | 0
2.2 | Total lump sum firm price for Supply part comprising of design (i.e.preparation and submission of drawing /documents including “As Built” drawings and O&M manuals), engineering, manufacture, fabrication, assembly, inspection / testing at vendor's & sub-vendor’s works, painting, maintenance tools & tackles (as applicable), fill of lubricants & consumables alongwith spares for erection as required, startup and commissioning spares as required, forwarding, proper packing, shipment and delivery at site for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. (Break-up as per Annexure-I) |  | Lot | 1 | 0 |  | 0 | NA |  |  |  | 0 | 0
2.3 | Total lumpsum firm prices for Services part comprising for unloading, handling, transportation to stores area & storage, transporation to site (from stores area) & in-site transportation, assembly, erection & commissioning, final painting at site, minor civil work, trial run at site and carrying out Performance guarantee / Functional / Demonstration tests at site (As applicable), training of customer/client O&M staff and handover in flawless condition of the package to the end customer complete with all accessories for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. (Break-up as per Annexure-I) |  | Lot | 1 | NA |  |  | 0 | 0 |  |  | 0 | 0
2.4 | Total lumpsum firm price for Mandatory Spares comprising of manufacture, fabrication, assembly, inspection / testing (as applicable) at vendor's & sub-vendor’s works, painting, forwarding, proper packing, shipment, delivery at site & guarantee as per tender technical specification above, amendment & agreements till placement of order. (Price break up of mandatory spares is to be furnished as per Annexure- II) |  | Lot | 1 | 0 |  | 0 | NA |  |  |  | 0 | 0
Note: 1) Please note that the complete engineering of the package is in the scope of bidder as per the tender requirement. However, for the payment purpose bidder to note that 50% of price as per sl. no. 2.1 shall be made against basic engineering (i.e. Preparation, submission & approval of basic drawing/ documents as indicated in tender specification) and the remaining payment shall be made for the balance engineering part on pro-rata basis.

## ANNEXURE-I
ANNEXURE - I PRICE BREAKUP (FOR MAIN PLANT AND OTHER AUX BUILDINGS)
NAME OF PROJECT: |  | 206 MW SHAHPURKANDI HEP
NAME OF PACKAGE: |  | HVAC SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-406-571-11000-A001
SL NO | DESCRIPTION | Qty |  |  | UNIT | SUPPLY |  | E&C
A | VENTILATION SYSTEM | Powerhouse I | Powerhouse II | Total |  | Unit Ex-Works Price (INR) | Total Ex-Works Price (INR) | Unit E&C Price (INR) | Total E&C Price (INR)
1 | Sheet metal containerized type air washer unit ( Evaporative AHU/AIR WASHER) with centrifugal fan (DIDW) with motor, pumps with motors (2X100%), air washer internals, inlet air louvers, filters, piping as per IS:1239, Part-I (medium class galvanised), valves, nozzles, level switch, temp indicators, back wash arrangement, strainer, galvanised drain piping., NRD, saturation efficiency of 90% for above AHU as per specification. AHU as per specification of capacity 85000 cmh . Each air handling has 1 no centrifugal fan ( 1 x 100% duty) of capacity 85000 CMH at min. 75 mm SP. | 2 | 2 | 4 | NO* |  | 0 |  | 0
2 | Heating Kit for above AHU comprising strip heaters, safety controls, air-stat, contactors, frame work, thermostat & humidistat/ sensors etc. for above AHU as per specification. | 2 | 2 | 4 | LOT* |  | 0 |  | 0
3 | Axial flow supply fans with pre and fine filter (wall mounted) complete with casing, TEFC sq cage induction motors & mounting frame, MS rain protection cowl, bird screen , structural support and all other accessories (suitable for 415V/3-phase supply). Following fan shall have 30 mmwc static pressure.
3.1* | Capacity 10,000 CMH with Motor rating 2.2 KW | 1 | 1 | 2 | NO* |  | 0 |  | 0
3.2* | Capacity 7,500 CMH with Motor rating 1.5 KW | 1 | 1 | 2 | NO* |  | 0 |  | 0
3.3* | Capacity 4,000 CMH with Motor rating 0.75 KW | 1 | 1 | 2 | NO* |  | 0 |  | 0
4 | Axial flow supply fans with pre filter (wall mounted) complete with casing, TEFC sq cage induction motors & mounting frame, MS rain protection cowl, bird screen,structural support and all other accessories (suitable for 415V/3-phase supply). Following fan shall have 20 mmwc static pressure.
4.1* | Capacity 7,500 CMH with Motor rating 1.1 KW | 1 | 1 | 2 | NO* |  | 0 |  | 0
4.2* | Capacity 4,000 CMH with Motor rating 0.75 KW | 1 | 1 | 2 | NO* |  | 0 |  | 0
5 | Axial flow exhaust fans (Bifurcated type, spark proof construction, wall mounted) complete with casing, flame proof motor & mounting frame, MS rain protection cowl, bird screen, structural support and all other accessories epoxy painted (suitable for 415V/3-phase supply). Following fan shall have 15 mmwc static pressure.
5.1* | Capacity 15,000 CMH withMotor rating 2.2 KW | 12 | 12 | 24 | NO* |  | 0 |  | 0
5.2* | Capacity 10,000 CMH withMotor rating 1.5 KW | 1 | 1 | 2 | NO* |  | 0 |  | 0
5.3* | Capacity 4,000 CMH with Motor rating 0.75 KW | 1 | 1 | 2 | NO* |  | 0 |  | 0
5.4* | Capacity 2,000 CMH with Motor rating 0.55 KW | 1 | 1 | 2 | NO* |  | 0 |  | 0
6 | Axial flow exhaust fans (Wall mounted) complete with casing,TEFC sq cage induction motor & mounting frame, MS rain protection cowl, bird screen,structural support and all other accessories epoxy painted (suitable for 415V/3-phase supply) as specified.Following fan shall have 10 mmwc static pressure.
6.1* | Capacity 7,500 CMH with Motor rating 0.55 KW | 1 | 1 | 2 | NO* |  | 0 |  | 0
6.2* | Capacity 4,000 CMH with Motor rating 0.55 KW | 1 | 1 | 2 | NO* |  | 0 |  | 0
6.3* | Capacity 2,000 CMH with Motor rating 0.37 KW | 2 | 2 | 4 | NO* |  | 0 |  | 0
7 | Exhaust fan (propeller type) completes with induction motor & mounting frame MS rain protection cowl, bird screen, structural support and all other accessories as specified (suitable for 240V/ 1 phase). Following fan shall have 10 mmwc static pressure.
7.1* | Capacity 1000 CMH with Motor rating 100 watts | 10 | 10 | 20 | NO* |  | 0 |  | 0
8 | Make up water pumps 2x 100% for pumping make up water to Evaporative AHU Make up tank | 2 | 2 | 4 | NO* |  | 0 |  | 0
9 | Piping with valves , strainers , fitting etc to complete the system from Make up water pumps to Make up tanks water tanks located above Evaporative AHU units | 1 | 1 | 2 | LOT |  | 0 |  | 0
10 | MS(epoxy painted) Make up water Tanks 4 m3 (min thickness 5mm) | 2 | 2 | 4 | NO* |  | 0 |  | 0
B | AIR CONDITIONING SYSTEM
11 | AIR COOLED SPLIT UNITS consisting of outdoor unit (having compressor condenser coils with fan and motor), indoor unit (having evaporator coil, filter,fan with motor), interconnecting refrigerant piping as per site requirement & fittings with insulation, cordless remote, electrical power cord upto the nearest available point along with isolator / MCB, fixing frame for indoor and outdoor unit, Stablizer,etc. (Maximum avaiable BEE star Rating)
11.1* | 2.0 TR capacity (non-ductable type, 240 V, 1 phase isolation switch) i.e MCB of suitable rating as specified. | 16 | 16 | 32 | NO* |  | 0 |  | 0
11.2* | Electric Room heater(Oil filled ) with fan 2000W | 5 | 5 | 10 | NO* |  | 0 |  | 0
C | COMMON ITEM FOR HVAC SYSTEM
12 | GSS zinc coating 180 gms/ m2 Finished Ducting complete with hangers, vanes, tie rods, gaskets, sealant, adhesive , nut, bolt, locknut, hilti, bracing ,Structural support and all other accessories as required for installation of ducting at site as per specifications and site requirement.
12.1* | 18G. | 500 | 500 | 1000 | SQM* |  | 0 |  | 0
12.2* | 20G. | 750 | 750 | 1500 | SQM* |  | 0 |  | 0
12.3* | 22G. | 1250 | 1250 | 2500 | SQM* |  | 0 |  | 0
12.4* | 24G. | 1500 | 1500 | 3000 | SQM* |  | 0 |  | 0
13* | Wall mounted dampers (gravity operated) for different areas. | 3 | 3 | 6 | SQM* |  | 0 |  | 0
14* | Inlet Louvres | 10 | 10 | 20 | SQM* |  | 0 |  | 0
15* | MS Duct With Epoxy paint ( grills etc) | 10 | 10 | 20 | SQM* |  | 0 |  | 0
16* | Thermal insulation of supply air duct & return air duct with finish as specified. | 50 | 50 | 100 | SQM* |  | 0 |  | 0
17 | Fire damper.
17.1* | Fire damper with auto resetting, limit switches, indication lamps etc. | 9 | 9 | 18 | SQM* |  | 0 |  | 0
17.2* | Motorized actuator with single phase power supply for the above fire damper | 10 | 10 | 20 | NO* |  | 0 |  | 0
18 | VOLUME CONTROL DAMPER
18.1* | VOLUME CONTROL DAMPERS in GI construction as per specifications for supply / return ducts/ Air Washer room complete with fixing arrangement. | 50 | 50 | 100 | SQM* |  | 0 |  | 0
18.1* | Motorized actuator with single phase power supply for the above VCD | 4 | 4 | 8 | NO* |  | 0 |  | 0
19 | Grills / Diffusers
19.1* | SUPPLY AIR DIFFUSERS / GRILLS with VCD (G.I ) complete with fixing frames, nuts, bolts, gaskets, washers etc | 25 | 25 | 50 | SQM* |  | 0 |  | 0
19.2* | RETURN AIR DIFFUSERS / GRILLS without VCD (G.I) complete with fixing frames, nuts, bolts, gaskets, washers etc | 25 | 25 | 50 | SQM* |  | 0 |  | 0
20 | PLC BASED CONTROL SYSTEM for HVAC system - with Hot redundant PLC consisting of PLC Panels for AWU room , RIO Panel etc, OWS, Key board, I/O modules, I/O adopter modules, Furniture for PLC ( as required), power supply, UPS, Battery and Battery Charger, printer, Connectivity to SCADA for monitoring purpose, etc as specified as per tender specification | 1 | 1 | 2 | LOT |  | 0 |  | 0
21 | FIELD INSTRUMENTS like gauges, transmitter, switces for measuring of flow, temperature, pressure, level, humidity,RH and other instrument required for local monitoring & control etc for HVAC System | 1 | 1 | 2 | LOT |  | 0 |  | 0
22 | ELECT LV SWITCHBOARDS, LPBS, LOCAL MOTOR STARTERS, AC FUSE DBs, CABLE TRAYS, TRAY SUPPORT, TERMINATION & JOINTING KIT, CABLING ITEMS, ABOVE GROUND EARTHING MATERIAL, LT POWER CABLES, LT CONTROL CABLES, SCREENED CONTROL CABLES ETC. FOR COMPLETENESS OF HVAC SYSTEM :
22.1 | LV SWITCHGEAR (PANELS, FEEDER MODULES, CABINET ETC.) WITH BASE FRAME AND ANGLE/CHANNEL FOR FLOOR MOUNTING/ WALL MOUNTING | 1 | 1 | 2 | LOT |  | 0 |  | 0
POWER HOUSE SWTCHBOARD (400A, 415V, 3PH-4 WIRE, INCOMER POWER CABLE SIZE - 1RUN-1C-400 SQMM/PHASE, 1RUN-1C-400 SQMM NEUTRAL, FLOOR MOUNTED) WITH INCOMER AS MCCB/ACB AND OUTGOING FEEDER WITH MCCB
22.2 | LOCAL PUSH BUTTON STATION (LPBS) FOR MOTOR DRIVES | 1 | 1 | 2 | LOT |  | 0 |  | 0
22.3 | LOCAL MOTOR STARTER FOR SUPPLY AND EXHAUST FANS OF SMALLER RATING FOR LOCAL CONTROL | 1 | 1 | 2 | LOT |  | 0 |  | 0
22.4 | AC FUSE DBs for SINGLE PHASE LOADS (AS REQUIRED FOR LIMITING LT SWITCHGEAR LENGTH TO 10.8 METRE) | 1 | 1 | 2 | LOT |  | 0 |  | 0
22.5 | CABLING ITEM (CABLE TRAY, TRAY SUPPORT, CLAMPS, TIE, CONNECTOR, CABLE GLANDS & LUGS, TERMINATION & JOINTING KIT AND CABLE JUNCTION BOX ETC.) | 1 | 1 | 2 | LOT |  | 0 |  | 0
22.6 | ABOVE GROUND EARTHING MATERIAL | 1 | 1 | 2 | LOT |  | 0 |  | 0
22.7 | LT POWER CABLE | 1 | 1 | 2 | LOT |  | 0 |  | 0
22.8 | LT CONTROL CABLE | 1 | 1 | 2 | LOT |  | 0 |  | 0
22.9 | SCREENED(INSTRUMENTATION) CONTROL CABLE | 1 | 1 | 2 | LOT |  | 0 |  | 0
22.1 | INSULATING MATS FOR LT BOARDS MENTIONED UNDER SL. NO. 1 ABOVE | 1 | 1 | 2 | LOT |  | 0 |  | 0
22.11 | COMMUNICABLE ETHERNET SWITCHES, CAT-6E AND OFC CABLE FOR NUMERICAL RELAYS INTEGRATION OF LT BOARDS(AS APPLICABLE) MENTIONED UNDER SL. NO. 1 ABOVE. ALL THE NUMERICAL RELAYS TO BE INTEGRATED AND ONE COMMON POINT TO BE MADE AVAILABLE FOR UPPER LEVEL DCS/SCADA COMMUNICATION. | 1 | 1 | 2 | LOT |  | 0 |  | 0
23* | 50NB MS medium class INSULATED DRAIN WATER PIPING from various equipment like AHUs (including equalising line) , Split ACs cooling water pumps etc upto nearest available drain point with necessary fittings like tees, reducers, expanders, elbows, flanges, valves with flanges, U trap etc as per specifications. | 50 | 50 | 100 | Rmt* |  | 0 |  | 0
24 | Complete Structural work (painted) for routing & supporting of ducts, pipes, Fan Fixing and other equiments etc (through duct racks, bracket support, channels, angles, hilti etc.) along with bolting for fixing / anchoring, conrete fastners, grouting etc. | 1 | 1 | 2 | LOT |  | 0 |  | 0
25 | Handling arrangement for HVAC equipments
25.1* | 1T Chain Pulley Block arrangment with tripod | 1 | 1 | 2 | NO* |  | 0 |  | 0
26 | Total lumpsum price for special tools & tackles for maintenance inclusive of packing forwarding, transportation up to site, etc. (Bidder shall submit item-wise price break-up). |  |  | 1 | LOT | 0 | 0 | NA
27 | Total lumpsum price for commissioning spares inclusive of packing forwarding, transportation up to site, etc. (Bidder shall submit item-wise price break-up). |  |  | 1 | LOT | 0 | 0
28 | Providing full support during FAT of DDCMIS, preparation of control scheme, and commissining of DDCMIS as per relevent specification. |  |  | 21 | Mandays* | NA |  |  | 0
TOTAL | [6 empty] | 0 |  | 0
NOTES
1 | The bidder shall furnish unit rates for variable item (marked *) for necessary adjustment (plus or minus) variation during detailed engg. stage. The unit rates quoted above shall be considered for adjustment and no separate unit rates shall be quoted. Unit rates shall be valid throughout the contract. Final qty. shall be paid as per actual measurment at site for erection for all the variable items.
2 | Any cell left blank in the unpriced schedule shall be treated as "Quoted" and included in total price
3 | Price format shall not be changed by the bidder as the bidder may get disqualified by doing so.
4 | The BOQ mentioned above shall be read in conjunction with technical specification requirement. Any item required as per technical specification but not specifically indicated in above BOQ, shall deemed to be inculded in total prices quoted by bidder. No additional price shall be payable against such items.

## APPENDIX-A
APPENDIX-A Special tools & tackles for maintenance
NAME OF PROJECT: |  | 206 MW SHAHPURKANDI HEP
NAME OF PACKAGE: |  | HVAC SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-406-571-11000-A001
SL NO | DESCRIPTION | UNIT | Qty | Unit Ex-Works Price (INR) | Total Ex-Works Price (INR)
1 | Measuring tape | NO | 1 |  | 0
2 | Tachometer | NO | 1 |  | 0
3 | Double ended spanner | SET | 1 |  | 0
4 | Ring spanners | SET | 1 |  | 0
5 | Gasket punch | NO. | 1 |  | 0
6 | Center punch | NO. | 1 |  | 0
7 | Hammer with wooden handles | NO. | 1 |  | 0
8 | Scissors for sheet metal cutting | NO. | 1 |  | 0
9 | Torch light (suitable for 2 cells) | NO. | 1 |  | 0
10 | Multimeter | NO. | 1 |  | 0
11 | Anemometer | NO. | 1 |  | 0
12 | Compound pressure gauge | NO. | 1 |  | 0
13 | Slide wrench 8” | NO. | 1 |  | 0
14 | Slide wrench 10” | NO. | 1 |  | 0
15 | Slide wrench 6” | NO. | 1 |  | 0
16 | Box spanner set | SET | 1 |  | 0
17 | Screw driver set | SET | 1 |  | 0
18 | Align key set | SET | 1 |  | 0
19 | MS tool box | NO | 1 |  | 0
20 | One lifting and transfer truck for draw-out circuit breakers | NO. | 1 |  | 0
21 | One portable test set for test purposes and calibration of the circuit breaker over current tripping devices | NO. | 1 |  | 0
22 | One device for slow closing | NO. | 1 |  | 0
23 | One set of templates | NO. | 1 |  | 0
24 | One set of gauges | NO. | 1 |  | 0
25 | One set of special keys for contact adjustment | NO. | 1 |  | 0
TOTAL |  |  |  |  | 0

## APPENDIX-B
APPENDIX-B Commissioning spares
NAME OF PROJECT: |  | 206 MW SHAHPURKANDI HEP
NAME OF PACKAGE: |  | HVAC SYSTEMM
TECHNICAL SPECIFICATION No: |  | PE-TS-406-571-11000-A001
SL NO | DESCRIPTION | UNIT | Qty | Unit Ex-Works Price (INR) | Total Ex-Works Price (INR)
1 | FAN BELTS | SET | 1 |  | 0
2 | PRESSURE GAUGE | NO | 1 |  | 0
3 | TEMPERATURE GAUGE | NO | 1 |  | 0
4 | FILTER | SET | 1 |  | 0
1 | FACTORY BUILT ASSEMBLIES (PCC/MCC/DB)
1.1 | Busbar supports (Horizontal) | 1 set of 3 | 1 |  | 0
1.2 | Primary isolating contacts (Bus side) of each rating | 1 set of 3
1.2.1 | 100A |  | 1 |  | 0
1.2.2 | 250A |  | 1 |  | 0
1.2.3 | 400A |  | 1 |  | 0
1.3 | Primary isolating contacts (Load side) of each rating | 1 set of 3
1.3.1 | 100A |  | 1 |  | 0
1.3.2 | 250A |  | 1 |  | 0
1.3.3 | 400A |  | 1 |  | 0
1.4 | Secondary isolating contacts of each rating | 1 set of 3
1.4.1 | 100A |  | 1 |  | 0
1.4.2 | 250A |  | 1 |  | 0
1.4.3 | 400A |  | 1 |  | 0
1.5 | Gaskets (each size) | Meter | 10 |  | 0
1.6 | Fixed Terminal (1way) | Nos. | 10 |  | 0
1.7 | Shrouds (for outgoing modules) (one for each physical size of module) | Nos.
1.7.1 | 300mm |  | 1 |  | 0
1.7.2 | 500mm |  | 1 |  | 0
1.7.3 | 700mm |  | 1 |  | 0
1.8 | Wire (for secondary wiring)
a. | 2.5 mm2 | Metres | 30 |  | 0
b. | 1.5mm2 | Metres | 30 |  | 0
1.9 | Lugs (for secondary wiring) | Nos. | 12 |  | 0
2 | ISOLATING SWITCH
2.1 | Main contact kit for each rating | 1 set of 3 poles | 1 |  | 0
3 | POWER CONTACTORS
3.1 | Contactor coil of each rating | Nos. | 1 |  | 0
3.2 | Contacts kit (main) for each rating | 1 set of 3 poles | 1 |  | 0
4 | AUXILIARY CONTACTORS
4.1 | Complete unit with 2NO + 2NC contacts | Nos. | 1 no. of each rating/type |  | 0
4.2 | Contactor coils
a. | AC for each rating | Set | 1 |  | 0
b. | DC for each rating | Set | 1 |  | 0
5 | MCCB | Nos. | 1 no. of each rating/type |  | 0
6 | MCB | Nos. | 1 no. of each rating/type |  | 0
7 | PUSH BUTTONS
7.1 | Actuator contacts | Nos. | 5 |  | 0
7.2 | Element | Nos. | 5 |  | 0
8 | INDICATING LAMPS
8.1 | Complete unit | Nos. | 5 |  | 0
8.2 | Lens (assorted) | Nos. | 5 |  | 0
9 | OTHERS
9.1 | Selector & control switch (each type) | Nos. | 1 |  | 0
TOTAL |  |  |  |  | 0
NOTES
1 | ABOVE IS THE MINIMUM LIST. ANY OTHER COMMISSIONING SPARE REQUIRED FOR THE SYSTEM SHALL ALSO BE PROVIDED BY THE VENDOR WITHOUT ANY COST IMPLICATION.
2 | FOR ELECTRICAL ITEMS " SET COMPRISES OF ALL ALPHABETS 100 NOS. EACH AND NUMERALS (0-9) 100 NOS. EACH.

## ANNEXURE-II
ANNEXURE - II LIST OF MANDATORY SPARES
NAME OF PROJECT: |  | 206 MW SHAHPURKANDI HEP
NAME OF PACKAGE: |  | HVAC SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-406-571-11000-A0011
S. No. | Description | UNIT | Powerhouse I | Powerhouse II | Total Ex-Works Price (INR)
A | MECHANICAL
1 | Bearings for each type of fan. | Set | 1 | 1
2 | V-belts / flexible coupling set for each type of fan | Set | 1 | 1
3 | Filter bank type and size used | Set | 2 | 2
4 | Manual Hoists (Chain Pulley Block) (FOR EACH TYPE & CAPACITY)
a | All Bearings | Set | 1 | 1
b | Brake assembly and its liners (as applicable) | Set | 1 | 1
B | ELECTRICAL
A. CABLES & CABLING ITEMS
1 | LV power cable each type | % of installed quantity | 10% of Installed quantity | 12% of Installed quantity
2 | Control cable each type | % of installed quantity | 10% of Installed quantity | 12% of Installed quantity
3 | Communication cable each type | % of installed quantity | 10% of Installed quantity | 12% of Installed quantity
4 | Terminals-MV Outdoor type Indoor type | % of installed quantity | 10% of Installed quantity | 12% of Installed quantity
5 | Lugs of each size | % of installed quantity | 10% of Installed quantity | 12% of Installed quantity
6 | Coaxial cables | % of installed quantity | 10% of Installed quantity | 12% of Installed quantity
7 | Cable glands of each size | % of installed quantity | 15% of Installed quantity | 20% of Installed quantity
8 | Junction boxes of each size | % of installed quantity | 15% of Installed quantity | 20% of Installed quantity
9 | Cable tray of each size | % of installed quantity | 10% of Installed quantity | 12% of Installed quantity
10 | Cable supports, hardware etc | % of installed quantity | 15% of Installed quantity | 20% of Installed quantity
NOTE: Minimum one drum (of standard length) is to be provided for all power and control cable of each type and size as mandatory spare.
B. LV SWITCHGEARS
1 | DC Motors for draw-out circuit breakers of each type | Nos. | 2 nos. | 2 nos.
2 | DC Coils for draw-out circuit breakers of each type | Nos. | 1 nos. | 1 nos.
3 | DC Coils for draw-out circuit breakers of each type | Nos. | 1 nos. | 1 nos.
4 | AC Motor for draw-out circuit breakers | Nos. | 1 nos. | 1 nos.
5 | Main contacts for draw-out circuit breakers | Sets | 2 sets | 2 sets
6 | Secondary contacts for draw-out circuit breakers | Sets | 2 sets | 2 sets
7 | control switch of each type | Nos. | 1 nos. | 1 nos.
8 | Solid -state over current trip devices without ground fault element | Nos. | 1 nos. | 1 nos.
9 | solid-state over current trip devices with ground fault element | Nos. | 1 no. | 1 no.
10 | Bus bars of each capacity for distribution centers | Sets | 2 sets | 2 sets
11 | Spring loaded plug-in connectors for starter modules | Sets | 4 sets | 4 sets
12 | Molded case circuit breakers one of each type | Nos. | 1 no. | 1 no.
C | C&I
1 | For each type of switch offered | No.s | 3 No. | 3 No.
TOTAL |  |  |  |  | 0
Notes:
a) Spares listed in Price Schedule is bare minimum requirement. In case any additional mandatory spares requirement is covered elsewhere in the tender specification apart from specified above, same shall be deemed to have been covered in bidder’s scope of supply.
b) One set corresponds to actual quantity of components and devices as installed for the equipment at Site.
c) All Spares shall be supplied as per the requirement of the specifications. In case any spare indicated in the specification is “not applicable” for particular equipment, then suitable applicable alternate spare has been offered / shall be supplied by the bidder without any financial implication."
d) Any item which is quoted as “not applicable” by the bidder in the above list and is found to be “applicable” at a later date shall be supplied by the bidder without any commercial and delivery implication.
e) Any cell left blank in the unpriced schedule shall be treated as “Quoted” and is included in total price.