## Sheet1
Sl. No. | Description | Confirmation by GT OEM (Yes/No) | Rev
Sec-A
1 | GT OEM's major scope of supply, services for gas turbine and their associated systems shall be as indicated below and conforming to end customer specifications which are part of the enquiry documents (end customer specification "JOB NO. B240" is enclosed) |  | 00
2 | GT OEM to submit DOCUMENT No.B240-910-80-42-SS-5010 Rev. C along with the offer with POINTWISE confirmation for GT OEM scope of supply. |  | 01
3 | Gas Turbine (suitable for NG as indicated in end customer specification) with DLE/DLN combustion system located Outdoor. A write-up with the details of the offered combustion system (with DLE/DLN combustors) shall be submitted with the bid/offer. Refer "GAIL Gandhar NGC GT Input R00"(Annexure-A) for requirements of compressor with respect to power, speed, utility requirement of lube oil from GT lube oil system. Refer DOCUMENT No.B240-910-80-42-DS-1002 Rev. C |  | 01
4 | Lube Oil Requirements for Compressor as mentioned below also to be included in GT lube oil system which is in GT OEM Scope. Flow 285 lpm Heat Losses 113 kW Oil grade ISO VG 32 / ISO VG 46 Pressure required at lube oil header mounted on compressor base plate 2.5 kg/cm2g |  | 00
5 | The Gas Turbine shall be either of heavy-industrial, light-industrial or aero-derivative type and Single/Multiple Shaft design equipped with DLE/DLN combustors and shall conform to API Std. 616, 5th edition together with EIL Standard specification no. 6-43-0041 Rev. 2 and other specifications as listed in the List of Attachments forming part of inquiry document. |  | 00
6 | Base plate/frame for all items/equipments in GT OEM scope of supply including Gas turbine, Off-base skids, Auxiliaries, etc along with all items mounted on it required for normal operation of Gas turbine. |  | 00
7 | All foundation hardware (including embedments & over the surface items) for all items/equipments in GT OEM scope of supply including gas turbine, off-base skids, auxiliaries, etc |  | 00
8 | Sufficient spares required for commissioning as per GT OEM experience/recommendation & furnish a list for the same. If however, any additional spares is consumed over and above the quoted commissioning spares, during commissioning, the same shall be provided free of cost, by the GT OEM. Any leftover spares after commissioning shall be handed over to the owner. |  | 00
9 | Mandatory spare parts as specified in “List of Mandatory Spares” DOCUMENT No. B240-910-80-42-SL-5010 Rev. C as attached in the inquiry document, Clause 9.0 of Document no.B240-910-16-51-SP-5010, DOCUMENT No.B240-910-16-51-SL-5010 shall be included as part of supply for complete scope of GT OEM. |  | 01
10 | List of 2 years O&M spares to be provided along with price as per Form SP-2 of enquiry(1)_20190925_111615 document. Prices of 2 Years O&M spares shall be kept valid upto Guarantee/ warranty period. Owner reserves the right to place the order for such O & M spares. Owner reserves the right to select and order any of the spares out of above list. |  | 00
11 | GT recommended maintenance schedule for 15 years indicating clearly requirement of spares / replacement of parts, schedule of inspections, down time required along with services of manufacturer’s expert personnel at site with duration to be furnished by GT OEM as part of technical offer. No commercial offer required for this requirement. |  | 00
12 | Supervision of Erection and Commissioning of Gas turbine shall be as per Form SP-3 of enquiry(1)_20190925_111615 document. GT OEM shall provide Per DIEM rate for the additional mandays over and above offer. In above supervision, GT OEM to also include for equipments like Vibration & temperature monitoring system etc. |  | 00
13 | Inspection & testing as per Clause 10.0 of DOCUMENT No.B240-910-80-42-SP-5010 Rev. C and other requirements mentioned elsewhere in the enquiry document should be followed for GT. |  | 01
14 | (a) Mechanical run test for the Gas Turbine with main rotor / main Gas generator as per API Std. 616 & EIL Standard Spec. 6-43-0041 at Gas Turbine Manufacturer's works (Rotor or Gas Generator as per offered GT type) (b) Performance Test for Gas Turbine main rotor / main Gas generator as per API Std. 616, ASME Code PTC 1 & 22 and EIL Standard Spec. 6-43-0041 at Gas Turbine Manufacturer's works (Rotor or Gas Generator as per offered GT type) |  | 00
15 | Torsional analysis test to be performed by GT OEM for complete train. Required data of compressor and load gear box shall be funished by BHEL during detail engineering stage. |  | 00
16 | Furnish performance guarantees with gas fuel (i.e., power, heat rate, fuel flow). Exhaust flow, exhaust temperature, exhaust composition, exhaust energy to be submitted for information. Refer DOCUMENT No. B240-910-80-42-LP-5010 Rev. B for guarantees, loading and penalty criteria. GT OEM to fill and submit Annexure-1 of DOCUMENT No.B240-910-80-42-LP-5010 Rev. B |  | 00
17 | GT OEM shall indicate the comparative data/table of the emission limits as per CPCB/GPCB (latest in force and whichever is stringent) and guaranteed emission data of the offered Gas Turbine in his bid/offer. The guaranteed exhaust gas emission datasheet (as in Gas Turbine Datasheet) shall be mandatorily filled-in and submitted with the bid/offer. A categorical confirmation of compliance to the above with back-up documents shall be furnished in the bid/offer of the bidder. |  | 00
18 | GT OEM to submit heat balance diagram for gas turbine indicating the guarantees, rated conditions submitted with the bid to validate the performance guarantees. |  | 00
19 | Correction curves to correct power and heat rate shall be submitted as per Clause 4.2.5 of DOCUMENT No. B240-910-80-42-LP-5010 Rev. B and GT OEM to also furnish correction curves which will affect exhaust flow, exhaust energy, exhaust temperature, exhaust composition. |  | 00
20 | Furnish performance guarantee test procedure and correction curves/data for output, heat rate , exhaust flow, exhaust temperature, exhaust energy and demonstration of emission on gas fuel and sound level.This procedure will be submitted for end customer approval. The PGTR shall be done with the process gas (as per Process datasheets) and at full load for 72 hours duration to establish satisfactory performance (in terms of performance guarantee parameters, pressure and temperature etc. as per inquiry document). Alongwith the guarantee parameters, safe & smooth, reliable operation, mechanical integrity and sound level of the complete package shall also be established during the PGTR at site. Refer DOCUMENT No.B240-910-80-42-SP-5010 Rev. C for Performance test requirements. GT OEM to conduct site performance test for gas turbine (not just supervision) with all necessary instruments. All instrumentation, devices (with necessary calibration) and services required for conductance of PG test should be included in GT OEM scope. And the same to be included in the offer. Also, refer STANDARD No. 7-76-0103 Rev.2 |  | 00
21 | GT OEM should provide provision, instrumentation and procedure for measuring performance guarantee parameters(i.e., power, heat rate, fuel flow) during test at site for its scope as required for proving guarantees and as per end customer specification. |  | 00
22 | Zero tolerances for guaranteed parameters should be considered. Guaranteed parameter figures should be inclusive of all errors in instruments and measurements. Refer DOCUMENT No.B240-910-80-42-LP-5010 Rev. B |  | 00
23 | IDLN/Performance tuning/optimization (along with necessary instrumentation, equipment & services) to meet the requirements of output, heat rate, combustion dynamics, vibration, emission, etc. as applicable to be included in vendor scope. |  | 00
24 | Performance guarantee test at site shall be conducted by GT OEM. GT OEM shall be responsible for the guarantees for GT OEM scope and shall make good incase of any shortfall in the performance without any time/price implication. Otherwise LD/Penalties shall be levied in accordance with BHEL NIT. The cost for the “Performance guarantee test run at site” shall be quoted as part of basic price. Refer Clause 10.2.8 of DOCUMENT No. B240-910-80-42-SP-5010 Rev. C |  | 01
25 | Training as per Form SP-4 of enquiry(1)_20190925_111615 document Refer Clause 15.5 of DOCUMENT No. B240-910-80-42-SS-5010 Rev. C Refer Clause 12.0 of DOCUMENT No. B240-910-80-42-SP-5010 Rev. C |  | 01
26 | Special tools and tackles for erection, assembly, disassembly and maintenance (along with the list) for GT. Refer Clause 13.3 of DOCUMENT No.B240-910-80-42-SP-5010 Rev. C Refer Clause 11.3,11.5 of DOCUMENT No.B240-910-80-42-SS-5010 Rev. C |  | 01
27 | Spreader bar/slings/shackles for lifting of skids supplied by GT OEM, as necessary for transportation/handling at port/erection. Refer Clause 13.3 of DOCUMENT No.B240-910-80-42-SP-5010 Rev. C Refer Clause 11.4 of DOCUMENT No.B240-910-80-42-SS-5010 Rev. C |  | 01
28 | All on-base cabling (Signal, Control & Power) upto the Junction boxes for the respective skids are in GT OEM scope. Field side cables are in end customer scope for which GT OEM should share cable schedule requirements.
29 | Local Gauge Boards (SS316) and Local panels (SS316) for the respective skids are in GT OEM scope Refer Clause 6.10 of DOCUMENT NO.B240-910-16-50-SP-5010, Rev B |  | 01
30 | All necessary electricals & instrumentation shall be provided for GT OEM scope. |  | 00
31 | Instrumentation shall be as per end customer Specification. All instruments shall be suitable to Area classification Zone-1 Gr IIC T3 (minimum requirement for instruments). Refer Document no.B240-910-16-51-SP-5010 GT OEM shall fill and submit Document no.B240-910-16-51-CF-5010 |  | 00
32 | Electricals shall be as per end customer Specification. All electricals shall be suitable to Area classification Zone-2, Temp class T3. Refer DOCUMENT NO.B240-910-16-50-SP-5010, Rev B |  | 01
33 | All electrical equipment for use in hazardous areas shall be certified by CIMFR, PTB,Baseefa, UL, FM or equivalent independent testing agency for the service and the area in which it can be used and shall be approved by PESO/CCOE. Copies of Hazardous area test certificates & PESO/ CCOE approval shall be furnished. As per statutory requirement in India, the approval from PESO/CIMFR must be submitted for equipment to be installed in hazardous area. Necessary certification for equipment, electrical and instrumentation as required by end customer specification shall be in GT vendor scope. |  | 00
34 | All electronic/electrical instruments and equipments shall be suitable for area classification as per IEC codes and shall be tested by any recognised authority like Baseefa, FM, PTB, CMRI etc. and shall be certified by Petroleum And Explosives Safety Organisation (PESO)/ Chief Controller of Explosives (CCE), Nagpur or Director General of Mines Safety (DGMS) in India. Intrinsically safe in general. Solenoid valves shall be flameproof. Refer Document no. B240-910-16-51-SP-5010 for further details |  | 00
35 | All on base & interconnection piping among GT OEM supplied skids, utilities, drain and vent piping upto terminal points as per end customer specification. Utility list must be furnished along with the offer. Refer DOCUMENT No.B240-910-83-41-SP-0002 Rev. D |  | 00
36 | Hazardous Gas detection system and UV detection system shall be part of GT OEM supply as per end customer specification. Also refer Clause 11.5 of Document no. B240-910-16-51-SP-5010 |  | 00
37 | Exhaust system consisting of exhaust collector, exhaust duct, expansion joints 1) All instrumentation and controls required for GT Exhaust as per end customer specification. Refer DOCUMENT No.B240-910-80-42-SP-5010 Rev. C Refer DOCUMENT No. B240-910-80-42-DS-1002 Rev. C |  | 01
38 | On skid water wash nozzles & valves (motorized/pneumatic) along with on line & offline piping in Stainless steel 1) All instruments required for operation of GT Water wash 2) Operation control logics to be configured in GT Control system. |  | 00
39 | Enclosures to be provided for the following vendor packages ۰Turbine compartment ۰ Exhaust compartment ۰ Lube oil compartment (Accessory compartment) ۰ Gas compartment Acoustic enclosures with AC&DC lighting, door limit switches for all the skids supplied by GT OEM. All Enclosures should have facilities for equipment handling like mono-rail,hoist, chain-pulley blocks and accessories etc. Enclosure to be designed for sound attenuation and thermal regulation of the internal components. Enclosure to provide for necessary fire detection and regulation and gas detection. Vendor to ensure the following requirements to be provided as a minimum. ۰ Enclosure structure to be made of columns and beams with bracing. mounted panels suited to thermal, acoustical requirements and removable roof to be provided. ۰ Provision of access control locks on the enclosure doors (one on each side per compartment) with safety override for operation from inside the enclosure. Control system Interlock to report incorrectly closed/open doors during machine operation. Doors to have glass window provision with tight seal covers ۰ Interior lighting (Both AC & Emergency DC) suitable to 415V/50Hz/3φ (AC) and 110V DC. Lighting to be explosive proof and confirming to zone-I. Switches to be externally mounted. ۰ Max noise level limited to 85 dBA at 1 mt distance from equipment. Back draft damper and fire suppression medium dampers shall be provided at the inlet/outlet of the vent openings. ۰ Module to be suitable for seismic load zone-II (IS 1893) and wind loads up to 200 kmph. ۰ Co2 based fire protection system incorporating both thermal and UV detection for release. Supply inclusive of CO2 piping and release nozzles etc. ۰ Foundation hardware supply is part of vendor scope. ۰ Enclosure panels designed to provide ease of access for removal of subassemblies. ۰ Pipe/cable/conduits entry points to be suitably sealed. ۰ All electrical and instrumentation items shall be explosion proof Ex-d with ATEX/PESO/CCOE approvals ۰ Also refer Clause 9.7.9 of DOCUMENT No.B240-910-80-42-SP-5010 Rev. C, Clause 6.11.5, 6.11.6, 6.11.8 of DOCUMENT NO.B240-910-16-50-SP-5010,Rev B |  | 01
40 | Fire fighting system with unit fire protection panel for i. Gas turbine, exhaust ii. Bearing tunnel iii. Lube oil/gas module - Electronically operated, fully automatic CO2 flooding system with alarms & trip interlocks - The fire protection system shall be in accordance with NFPA – 12. - CO2 release mechanism - Stainless steel distribution piping for all the protected areas - Field hardware like explosion proof manual call points, visual & audible alarms,pressure switches and junction boxes - Discharge nozzles in protected areas - Thermal detectors for activation and UV detectors. All detectors shall be listed by FM & UL. - Provision for manual activation from main control room as well as from the field. - Design sizing calculation shall be provided for submission to customer - Approvals from statutory & local authorities like PESO shall be obtained by GT OEM - Explosion proof electricals (Ex-d) suitable to zone-1 hazardous area, suitable to NEC class-I, Div-II, Group C & D or IS/IEC 60079-1 Group IIA & IIB. - Warning signs, alarms for attempted entry into protected areas without CO2 isolation - The control system for the fire protection shall be part of F&G Panel and shall be NFPA compliant & OISD Norms. - Architecture , control philosophy and interface with remote systems shall be finalsied durign detailed engineering - Also refer DOCUMENT NO.B240-910-17-44-SP-01 Rev. A, Clause 11.5 of Document no.B240-910-16-51-SP-5010 |  | 00
41 | 1) Fuel gas system dedicated to GT- Control valves, stop valve, manifold, nozzles etc. suitable for DLE/DLN combustion system. 2) Gas flow meter (FE-1201) along with Flow computer (Refer Piping and Instrumentation Diagram B240-02-42-910-1112 Rev.03). GT OEM to realise signals of Flow computer in the control system supplied by GT OEM. As per the piping symbol, the type of flow meter required is Orifice flow element. 3) GT OEM to refer and confirm that marked up scope (Refer Marked up Piping and Instrumentation Diagram B240-02-42-910-1112 Rev.03) has been included in their scope. |  | 00
42 | Starting means for GT Refer Clause 9.7.4 of DOCUMENT No.B240-910-80-42-SP-5010 Rev. C Refer DOCUMENT No.B240-910-80-42-DS-1002 Rev. C Refer Clause 1.3 in Section-B of DOCUMENT No. B240-910-80-42-SS-5010 Rev. C |  | 01
43 | Lube oil skid, Temperature control valves for Lube Oil & Purge air 1) All electrical & instruments required as per end customer specification. |  | 00
44 | As per GT OEM design, Electric motor driven exhaust frame blowers and #2 bearing cooling fans including piping and check valves, interconnecting piping etc. (if applicable) |  | 00
45 | Turning gear for slow roll with AC, DC & manual barring |  | 00
46 | Accessory gear box for shaft driven pumps as per GT OEM design, if any to be included in GT OEM scope. |  | 00
47 | The lube oil system shall conform to API standard 614, 4th edition and data sheets and other specifications as listed in the List of Attachments forming part of inquiry document. Console type common lube oil system shall be supplied for Compressor, Gear Unit & Gas Turbine Driver. |  | 00
48 | - The LO system shall be complete and include oil reservoir, lube oil pumps (main & auxiliary), Emergency Oil Pump (EOP), hydraulic oil pumps (main & auxiliary oil pumps), an overhead emergency lube oil run-down tank suitably sized so as to ensure supply of lube oil to train for complete coast down time and cool off (separate accumulators shall be provided for pump change over), twin filters and all necessary valves, fittings, gauges etc. as required by purchaser's specifications. - Refer DOCUMENT No.B240-910-80-42-SP-5010 Rev. C & datasheets (Document No.B240-910-80-42-DS-1006 Rev. No. A and Document No.B240-910-80-42-DS-1007 Rev. No. B) 1) All electrical & instruments required as per end customer specification |  | 01
49 | The material of construction of lube oil reservoir, lube oil supply and return piping, valve internals etc. shall be of Series 300 Stainless Steel. Refer DOCUMENT No.B240-910-83-41-SP-0002 Rev. D |  | 00
50 | Supply of First fill of lubricants for the machines is not included in the GT OEM's scope of supply, but the lubricants should be available in India. GT OEM to furnish list of vendors available in India. However, GT OEM, in his proposal, shall indicate the Grade of Oil and the quantities required for flushing oil and for first fill and topup of Lubricant for each machine forming part of the GT package. |  | 00
51 | List of consumables (like water wash detergent etc.) to be furnished by GT OEM should be available in India. GT OEM to furnish list of vendors available in India. |  | 00
52 | Following Driving arrangement is envisaged for LO pumps. Main Lube oil Pump : driven by Electric (AC) Motor/shaft-driven Standby Lube oil Pump : driven by Electric (AC) Motor (Emergency AC feeder) Emergency Oil Pump : driven by Electric (DC) Motor (DC battery bank) |  | 00
53 | Coupling between Gas Turbine & Load Gear box (if required) as per end customer specification shall be in GT OEM scope. Compressor data, Gear box data shall be shared during detail engineering stage. Also refer Clause 9.9 of DOCUMENT No.B240-910-80-42-SP-5010 Rev. C and datasheets |  | 01
54 | Coupling between Gas Turbine & Compressor (if Load Gear box is NOT applicable) as per end customer specification shall be in GT OEM scope. Compressor data shall be shared during detail engineering stage. Gas turbine matching the compressor speed (i.e. without gearbox is preferred). Also refer Clause 9.9 of DOCUMENT No.B240-910-80-42-SP-5010 Rev. C and datasheets |  | 01
55 | Gear Box between GT & Compressor as per end customer specification. All instrumentation including Vibration & temperature monitoring system along with sensors, monitors, cables, connectors etc. for Gear box as per end customer specification. Refer Document No.B240-910-80-42-DS-1003 Rev. C Refer Document No.B240-910-80-42-ERGB-5010 Rev A Refer Clause 2.2 of DOCUMENT No.B240-910-80-42-LP-5010 Rev. B |  | 01
56 | Vibration & temperature monitoring system along with sensors, monitors, cables, connectors etc. shall be supplied for GT as per end customer specification. Refer Document no. B240-910-16-51-SP-5010 |  | 00
57 | Hardware/equipment required for Gas turbine Combustion Dynamics Monitoring/DLN Auto tuning/optimization, On Site Monitoring shall be supplied by GT OEM. Required control hardware and software for these systems should be considered in the Control system common for Gas turbine, Compressor and Balance of Plant Auxiliaries which should be supplied by GT OEM (as per end customer specification) which will be ordered separately by our sister unit BHEL-EDN. Refer Annexure-B document. Optional offer for control system for GT alone shall also be submitted. |  | 00
58 | Common Control system for Gas turbine, Compressor and Balance of Plant Auxiliaries (ordered separately by our sister unit BHEL-EDN and should be a separate line item with separate pricing. The technical requirements should meet end customer requirements and also the requirements shared by BHEL-EDN). Refer Annexure-B document. Optional offer for control system for GT alone shall also be submitted. The following minimum requirements also to be covered: 1) No. of HMIs', interface systems AND Locations shall be as per System architecture Network topology configuration 2)Specific control requirements like, Auto synchronisation, Staggering of Loads during emergency Start, IO Finalisation , Software discussions , commissioning spares , DCS & Remote interface will be finalised during detailed engineering stage. 3) Special cables (FO cable etc) for interface between HMI's , network hardware , Modbus IO List , synchronisation etc will be finalised during detailed engineering stage. 4) FAT & SAT and inspection as per end customer specification 5) Services at site and training as per end customer specification. |  | 00
59 | All signals that can trip or unload the gas turbine shall utilize transmitters. Switches are not allowed. |  | 00
60 | Painting including final coat, preparation for shipment and export quality packaging suitable for long term storage |  | 00
61 | Participation of end customer’s personnel during assembly and other important activities, as specified in the end customer Specification. Refer Clause 11.0 of DOCUMENT No.B240-910-80-42-SP-5010 Rev. C GT OEM shall inform the end customer the scheduled test dates 6 weeks in advance and reconfirm the firm date of testing 1 week in advance. |  | 01
62 | Facilitate EIL/Owner, Owner's and/or Consultant's Inspector to witness testing of any or all items at various stages during manufacture and/or final stage before shipment. |  | 00
63 | The end customer engineers deputed to Gas turbine manufacturer's shop shall participate in the assembly operation and other activities and GT OEM shall maintain record of all the final data like tolerances, clearances etc. GT OEM shall have to provide all such data and records to the end customer engineers and shall have to clarify all such data. GT OEM shall submit along with the bid a list of activities in which such participation shall be useful for future maintenance work, along with the time period of each activities and the schedule when these activities are likely to be performed. |  | 00
64 | The GT OEM shall furnish detailed time schedule of inspection/overhaul of various components. The design life of major components shall also be indicated. This information shall be indicated in the proposal. |  | 00
65 | Documentation specifically for GT package, electrical, instrumentation specifications of end customer Specification |  | 00
66 | Participation by GT OEM in HAZOP study of the project is required as per end customer specification. Any suggestions/modifications raised during HAZOP review shall be implemented by OEM without any cost/time implication to the BHEL/end customer. Refer Clause 5.2 of DOCUMENT No.B240-910-80-42-SP-5010 Rev. C Refer Form SP-5 of enquiry(1)_20190925_111615 document |  | 01
67 | Third party inspection as per Clause 19.0 in the SPECIAL CONDITIONS OF CONTRACT (SCC)-PURCHASE of enquiry(1)_20190925_111615 document. |  | 00
68 | OEM shall also comply requirements referred in STANDARD SPECIFICATION No. 6-43-0041 Rev. 2 of end customer. |  | 00
69 | Order of precedence for documents: Conflicts/ambiguity, if any, between various documents attached in the material requisition/inquiry document shall be highlighted by the GT OEM during pre-bid meeting. In case of any conflict among the documents attached in the inquiry document, the following preferential order shall govern, except as specifically indicated otherwise (in any document forming part of MR). However, end customer decision/clarification shall be FINAL and BINDING in this regard. (a) Process Datasheets/P&IDs. (b) Mechanical Datasheets. (c) Job Specifications (if any). (d) Other Specifications. (e) International Standards/Codes/recommended practices as applicable. In case of any other conflict /ambiguity is brought to end customer notice in the bid/proposal & during post bid submission stage, the same shall also be subject to end customer review/approval and end customer decision shall be FINAL and BINDING in this regard. End customer decision shall be complied by the GT OEM without any cost/ time implications. |  | 00
70 | GT OEM shall note that only those deviations shall be permitted which are technically infeasible to be met, provided suitable justification for the same is furnished. Deviations, which can be complied with extra cost and or time implication, shall not be permitted. No cost addition will be allowed during post bid. Any deviations NOT accepted by the end customer shall be withdrawn by GT OEM without any price implication to BHEL/EIL/GAIL. Also, refer Clause 2.0 of DOCUMENT No.B240-910-80-42-SI-5010 Rev. A |  | 00
71 | GT OEM shall necessarily procure all the material / equipment forming permanent part of the unit from OWNER / EIL approved vendors only. This shall include sub-ordered items / components also. Refer end customer specification for OWNER / EIL approved vendor list for the various items/equipments. Refer DOCUMENT No.B240-910-80-42-VL-5010 Rev.A Refer Clause 8 of DOCUMENT NO.B240-910-16-50-SP-5010,Rev B Refer Document No.B240-910-16-51-MD-5010 Rev. 0 Refer DOCUMENT No.B240-000-83-41-LL-0001 Rev. 1 |  | 01
72 | GT OEM shall refer all EIL standard specifications, job specification, data sheets etc. and other codes and standards referred in end customer specification. |  | 00
73 | GT OEM shall furnish all equipment, drivers, auxiliary systems, instruments and controls and safety devices as per the enquiry document. Anything required over and above what is specified, for safe and satisfactory operation of the equipment package shall be included by the GT OEM in his scope. |  | 00
74 | BHEL’s scope of supply in GT package (For information to GT OEM): The inputs/specification/information to be shared by GT OEM (Refer S.No.12 of Sec-B) 1) Lifting beam, Industrial digital video scope, Alignment tools, Torque Wrenches/Bolt Tensioners etc. 2) Inlet air filtration system 3) Inlet ducting upto inlet plenum 4) Exhaust ducting, silencers and stack 5) Off base compressor water wash skid 6) Staircase, ladders and walkways for enclosures 7) CO2 skid along with its instrumentation, interconnection piping from CO2 skid till GT enclosure 8) Ventilation system 9) Portable Lube oil purifier 10) Lube oil mist eliminator 11) Portable Lube oil drain pump 12) Lube Oil cooler (Air cooled type) with adequate number of fans with 100% spare capacity, complete with interconnecting piping between Lube Oil Cooler and the Oil Console. 13) Battery and Battery Charger 14) GTMCC & DCDB 15) Off base interconnection piping. 16) Off base interconnection signal cables. |  | 00
75 | BHEL will share list of field cable (power, control and signal) as per end customer requirement and specification for GT OEM to finalise the cable entry and termination in their equipment. This will be shared during exceution phase after post award of contract. |  | 00
76 | All outdoor equipment shall be provided with Prefabricated FRP canopy by GT OEM. |  | 00
77 | As per Notes-2 of DOCUMENT No.B240-910-80-42-SS-5010 Rev. C, approximate cable routing distance between skid in field and Unit control panel located in existing Control room shall be considered as 500 meters for all interconnecting cable estimate as part of base quote of the Package. This cable distance shall be noted by GT OEM and offer control system complying this requirement. |  | 01
78 | GT OEM to explicitly confirm its participation in the Unitization of GTC train at BHEL works for the required period which will be witnessed by GAIL/EIL representative. Below is the broad scope of activities which will be involved in the Unitization of GTC train: The compressor, gearbox and the GT shall be unitised on the job base plate, aligned and coupled to make a complete unit. The compressor will then be checked for visual inspection to confirm compliance to the GA drawings, nozzle dimension and facing, elevations, anchor bolts position, direction of rotation etc. |  | 01
79 | GT OEM to review the replies of all the prebid queries, Technical amendment, Commercial amendment issued by GAIL/EIL and shall also comply to these end customer requirements. GT OEM shall also submit a copy of above mentioned documents (replies of prebid queries, Technical amendment, Commercial amendment) duly signed & stamped on each page along with their offer as a token of their acceptance. The above documents shall form a part of Bidding Document. |  | 01
Sec-B | Drawings and other documents:
S.NO. | DETAILS OF DOCUMENTS
1 | GT OEM has to refer vendor data requirements of end customer (Document No. B240-910-80-42-VDR-5010 Rev. A) and submit all the drawings and documents which require end customer review and approval. Refer Document No.B240-910-16-50-VR-5010 Rev. A Refer Document No.B240-910-16-51-VDR-5010 Rev. A Refer Document No.B240-910-83-41-VDR-5010 Rev. A |  | 00
2 | GT OEM shall submit all the queries along with list of deviations and also attend PRE-BID MEETING to discuss and sort out.Evaluation of BIDS shall be done on “ZERO DEVIATION” basis. Hence, GT OEM shall strictly make all possible efforts to comply strictly with the requirements specified in the inquiry document. In case deviations are necessary, GT OEM shall note that only those deviations to codes & standards, which are either equipment specific or are technically infeasible to be complied with, may be considered and discussed during PRE-BID MEETING, provided a suitable justification for the same is furnished. Deviations, which can be complied either with extra cost and/or with time implications, shall not be permitted. Deviations, if any, shall be consolidated in a single Deviation List (Doc. No. B240-910-80-42-BF-5010) as enclosed in the MR to be discussed during pre-bid stage. It is in GT OEM interest to ensure that all technical deviations are sorted out in the pre-bid stage only. GT OEM to categorically note that no new deviations (except as agreed and discussed during pre-bid stage) shall be allowed with the offer or after submission of offer/placement of order.In case, GT OEM is not attending the PRE- BID meeting, it shall be understood that the GT OEM does not have any comments / deviations to MR/RFQ requirements. In case any deviations/ clarifications are furnished in his offer, those deviations shall be deemed to have been withdrawn by the GT OEM. Refer Clause 2.0 of DOCUMENT No.B240-910-80-42-SI-5010 Rev. A |  | 00
3 | GT OEM shall refer Clause A,B,C,D, E,F of Section-II for the Qualification and Evaluation criteria and furnish the drawings & documents/data/information along with the bid. |  | 00
4 | GT OEM shall necessarily furnish the drawings & documents/data/information as per Clause 3.0 of DOCUMENT No.B240-910-80-42-SI-5010 Rev. A along with the bid without which the bid/offer shall be considered incomplete and is likely to be rejected. GT OEM shall first submit the completely filled-in Equipment Data sheets, Performance & Correction Curves, filled in Experience Record Proforma, Equipment Manufacturers Latest catalogues and their General reference lists, vendor list and their qualification, Quality Plans for GT and other rotating equipments, any other documents as specified in end customer specification along with the offer. |  | 00
5 | GT OEM to verify and confirm the Qualification Criteria as per Clause 4.0 and Clause 3.0 (Annexure-A) of DOCUMENT No.B240-910-80-42-SP-5010 Rev. C & Clause 1.4 of STANDARD SPECIFICATION No.6-43-0041 Rev. 2 and submit all the documents required as per end customer specification. Note: All end user certificates shall be in English language mentioning the issue date of the certificate, the name of the Project, capacity / specification of the equipment, commissioning date, name and contract details (telephone number / email) of the end user duly signed and sealed in the official letterhead pad. If the original end user certificate is not in English language, the bidder shall submit a translation of the end user certificate made by official translator and verified by a notary public. |  | 00
6 | GT OEM should submit all the documents as per relevant clauses and formats of end customer specification as applicable to GT OEM scope. |  | 00
7 | GT OEM shall furnish all the documents in English, for EIL/GAIL review and acceptance, as specified in the end customer's specification. |  | 00
8 | Also all the drawings and documents at S.No 11 below shall be submitted by GT OEM within 30 days from placement of PO, incorporating project specific title block which will be shared during detail engineering. |  | 00
9 | The drawing and documents (ex. GA drawing etc) which require further engineering and integration by BHEL shall be furnished in Auto CAD format. |  | 00
10 | It is expected that GT OEM will submit bids based strictly on the terms and conditions and specifications contained in the bidding documents and will not stipulate any deviations. Should it, however, become unavoidable, deviations should be separately and specifically stipulated only in the prescribed DOCUMENT No.B240-910-80-42-BF-5010 Rev. A. OWNER reserves the right to reject as nonresponsive any bid containing major deviation(s). |  | 00
11 | As per Clause 4.2.5 of DOCUMENT No.B240-910-80-42-LP-5010 Rev. B, GT OEM shall also furnish a set of sample hand calculations for conversion of test data to site conditions. |  | 00
12 | GT OEM to furnish all necessary functional and ordering specifications, system requirement documents and interface information for sizing of equipment in BHEL’s scope of supply. |  | 00
13 | Following documents and drawings shall be furnished by GT OEM for information/review/acceptance as per end customer specification, not limiting to: |  | 00
13.1 | Following documents shall be submitted mandatorily along with bid but not limted : a. General Arrangement drawing of GT & its auxilairies in native format (editable version like Auto CAD). GT OEM shall also indicate weights of equipment, maintenance space required, crane capacity (recommended) and crane hook approach from the grade level etc. b. Foundation loading drawings with static and dynamic loads and other relevant data for civil foundation for the equipments which are in GT OEM scope of supply in native editable format. c. Utility consumption list (for Instrument air, Cooling water, Nitrogen, Fuel gas, Power etc.) d. Electrical load list including AC (HT, LT) Loads, DC loads, UPS loads etc. GT OEM shall furnish number and rating of UPS feeders (110V AC) required along with offer. e. List of panels along with Dimension, weight, recommended location, clearance around equipment, heat load f. Single Line diagram for GT MCC g. Gas fuel specification and supply requirements at GT inlet h. Lube oil supply, cooling water, preservation and storage, water wash, water purity requirements i. All other filled in Data sheets as per end customer specification j. Sub-vendor's list for all the equipment as per end customer specification k. Functional write up for normal operation l. Gas turbine Thermal performance data consisting of power, heat rate, exhaust flow, exhaust temperature, exhaust composition, emissions etc. m. Aux power along with list of auxiliaries n. Device list and P&ID's o. For complete GT package (typical documents for reference): 1) GA drawing 2) Shipping weights and dimensions 3) Foundation drawing 4) Utility list 5) Electrical load list 6) Cable schedule 7) List of special tools, startup and commissioning spares 8) Vendor list |  | 00
13.2 | Gas turbine Thermal performance data as requested by BHEL within 10 days of placement of PO but not limited to : a. GT power b. Heat rate c. Exhaust flow d. Exhaust temperature e. Exhaust composition f. Emissions data g. Fuel flow & temperature data etc. |  | 00
13.3 | All documents required for qualification of equipment supplied as per end customer specification along with the bid. |  | 00
13.4 | General arrangement of GT & it's auxiliaries in native editable format within 15 days of placement of PO. GT OEM shall also indicate weights of equipment, maintenance space required, crane capacity (recommended) and crane hook approach from the grade level etc. |  | 00
13.5 | Gas Turbine schematics and piping symbols within 30 days of PO. |  | 00
13.6 | Foundation loading drawings with static and dynamic loads and other relevant data for civil foundation for the equipments which are in GT OEM scope of supply in native editable format within 15 days of placement of PO. |  | 00
13.7 | Utility consumption list (for Instrument air, Cooling water, Nitrogen, Fuel gas, Power etc.) within 30 days of placement of PO. |  | 00
13.8 | Electrical load list including AC (HT, LT) Loads, DC loads, UPS loads etc. within 30 days of placement of PO. |  | 00
13.9 | List of panels along with Dimension, weight, recommended location, clearance around equipment, heat load within 30 days of placement of PO. |  | 00
13.10 | Single Line diagram for GT MCC within 30 days of placement of PO. |  | 00
13.11 | GT battery and charger sizing calculation within 30 days of placement of PO. |  | 00
13.12 | Vendor drawings and documents for GTMCC AND DCDB within 90 days of placement of PO. |  | 00
13.13 | Vendor drawings and documents for Battery within 90 days of placement of PO. |  | 00
13.14 | Electrical connection diagram of Junction Boxes and panels within 30 days of placement of PO. |  | 00
13.15 | IO termination details (IO report) for GT Controls, Fire protection, UV detection , Vibration & temperature Monitoring, Haz Gas leakage monitoring system,Starting means etc. within 60 days of placement of PO. |  | 00
13.16 | Earthing / grounding layout Drawing within 90 days of placement of PO. |  | 00
13.17 | Interconnection piping and package connection details, piping specifications within 45 days of placement of PO. |  | 00
13.18 | Gas fuel specification and supply requirements at GT inlet within 30 days of placement of PO. |  | 00
13.19 | Lube oil supply, cooling water, preservation and storage, water wash, water purity requirements within 30 days of placement of PO. |  | 00
13.20 | Device Summary/Device List within 30 days of placement of PO. |  | 00
13.21 | Overall sequence of operation of start-up/shutdown/normal operation within 90 days of placement of PO. |  | 00
13.22 | Electrical outline drawing showing Junction Boxes / panel locations within 60 days of placement of PO. |  | 00
13.23 | All other filled in Data sheets as per end customer specification within 90 days of placement of PO. |  | 00
13.24 | Sub-vendors’ list for all the equipment as per end customer specification within 30 days of placement of PO. |  | 00
13.25 | Functional write up for normal operation within 90 days of placement of PO. |  | 00
13.26 | PG test procedure and correction curves along with data points within 120 days of PO |  | 00
13.27 | All erection documents required for erection at site to make estimates (for eg.Packing List and Weights etc.) for GT OEM scope of supplies |  | 00
13.28 | GT OEM shall provide a bar-chart type schedule for the execution of the WORK for its scope and shall show the main activities with duration, their sequences, and the milestone events specified. |  | 00
13.29 | 6 sets of hard copies & 2 sets of soft copies - Drawings, datasheets, check lists, procedures and other necessary documents required for erection and commissioning of Gas turbine and auxiliaries supplied by GT OEM. |  | 00
13.30 | 6 sets of hard copies & 2 sets of soft copies (or no. of copies as agreed with end customer) - All customer documentation, Drawings, datasheets, check lists, procedures, etc. and other necessary documents required for O&M of Gas turbine and auxiliaries supplied by GT OEM. |  | 00
13.31 | Type test reports, material test certificates, final and in process inspection reports, etc. where ever applicable during detail engineering |  | 00
13.32 | BOM of commissioning spares, mandatory spares (as per the requirements of end customer specification for review and approval) |  | 00
Sec - C | Additional terms and conditions: |  | 00
1 | Pertaining to GT OEM's scope of supply, GT OEM shall be responsible for answering to all GAIL/EIL queries and attending any meetings if required until the issues are resolved and closed by end customer and provide all necessary data as required. |  | 00
2 | GT OEM to supply any other equipment which is not explicitly mentioned as in GT OEM’s scope of supply but mentioned in the end customer specification and is required for smooth and satisfactory operation of the Gas turbine package. |  | 00
3 | GT OEM shall provide detailed breakdown BOM for complete scope of supply. |  | 00
4 | GT OEM shall facilitate GAIL/EIL/BHEL to witness testing of equipments as per the list agreed and finalized with GAIL/EIL/BHEL. |  | 00
5 | GT OEM shall be responsible for compliance with complete specification issued by GAIL/EIL including national standards as specified therein, limited to its scope of supply, and where not TECHNICALLY feasible shall get acceptance from the GAIL/EIL. |  | 00
6 | GT OEM to confirm that if specific deviations are not provided separately , it is presumed that the end customer technical requirements are being complied in toto. |  | 00
7 | GT OEM shall be responsible for getting GAIL/EIL acceptance on material selection, components selection/design and general engineering design practices used to design and procure GT OEM supplied equipment, if GAIL/EIL raises any queries on the same. |  | 00
8 | Between BHEL and GT OEM, each party shall be solely and exclusively responsible for its own scope of work. Both parties shall perform their respective scope in an integrated manner as and when required. |  | 00