## Sheet1
| BHARAT HEAVY ELECTRICAL LIMITED |  |  | Enquiry No. :
| UNIT'S ADDRESS: |  |  | Due Date :
| UNIT'S PHONE NOS. |  |  | Supplier Qtn. No.:
| CONTACT PERSON'S NAME/DESIGN./PHONE NO./E-MAIL (FROM PURCHASE DEP'T.) |  |  | Date :
SPECIFICATION CUM COMPLIANCE CERTIFICATE FOR POWER TRANSDUCERS
NOTE:-
1. Inadequate / incomplete, ambiguous, or unsustainable information against any of the clauses of the specifications / requirements shall be treated as non-compliance.
2. The offer and all documents enclosed with offer should be in English language only.
ADDRESS OF THE SUPPLIER : |  |  |  | ADDRESS OF THE INDIAN AGENTS :
TELEPHONE NOS.: |  |  |  | TELEPHONE NOS.:
FAX NOS.: |  |  |  | FAX NOS.:
E-MAIL ADDRESS : |  |  |  | E-MAIL ADDRESS :
SCOPE: SUPPLY & COMMISSIONING OF POWER TRANSDUCERS WITH SPECIFICATION AS BELOW
Sl. NO | DESCRIPTION FOR BHEL REQUIREMENT | SPECIFIED BY | OFFERED | DEVIATIONS | REMARKS
1 | PURPOSE
1.1 | To measure & record electrical Parameters (Voltage, current and active power) of the AC Drives, directly in engineering units by using retransmitted outputs of 3 phase transducers for acquiring data during testing of Planetary gear box and Bowl Mills. | Vendor to Confirm
2 | Technical Specifications.
2.1 | Power range | 0 to 3000 W
2.2 | Maximum operating Input voltage for Transducer | 415±10%V, 3 Phase, 5 Amp, 50 Hz
2.3 | Transducer power supply Voltage | 220V±10%V, AC or Self powered
2.4 | Transducer current (input) | 5 Amps direct, 2 phase
2.5 | Transducer Voltage (input) | 415 AC direct, 3 phase
2.6 | Accuracy Range | 0.5% of span
2.7 | Burden | better than 0.5VA
2.8 | Response time: | better than 500msec to 99% of rated output
2.9 | Output protection | Fully protected against short /open circuit output.
2.1 | Output ripple: | 0.5% of rated output
2.11 | Max output Volts: | 15 Volts DC under open circuited
2.12 | Isolation: | Input/output/supply/case
2.13 | Temperature Range: | Storage: 40°C, Operating: 0 to 60°C
2.14 | Power transducer analogue output: | 4 -20 mA
2.15 | No of retransmission outputs required: | 3 outputs of 4-20mA, galvanically isolated(each respectively for current, voltage & active power)
2.16 | Output type requirement: | Output 1 -Voltage, Output 2 - Current, Output3 - Active power
2.17 | Transducer without damping adjustment would be required. | Vendor to Confirm
2.18 | Connectivity: | 3 Phase 3 wire unbalanced Load OR 3 Phase 4 wire system
3 | Testing
3.1 | The Power Transducers shall be tested in accordance with applicable Standard. | Vendor to specify applicable Standard.
3.2 | Test reports of all the tests to be carried out on the Power Transducers shall be furnished . | Vendor to Confirm
3.3 | All the above tests should be demonstrated to BHEL engineers during Erection & Commissioning at BHEL Works. | Vendor to Confirm
3.4 | All the tests and calibration certificates are to be submitted before dispatch for acceptance by BHEL. | Vendor to Confirm
4 | AMBIENT CONDITIONS & THERMAL STABILITY :
4.1 | Total equipment should work trouble free and efficiently under following operating / Ambient conditions : Temperature = 5 to 55 degree Celsius, Relative Humidity = 95% max. (Vendor should Confirm that the equipment is suitable for above conditions and details of provisions on the equipment for the same should be furnished) | Vendor to Confirm
4.2 | Weather conditions are tropical, Atmosphere may be dust laden during some part of the year. Equipment shall be kept in the normal shop floor condition. Max. temperature variation is 25 deg Celsius in 24 hours. | Vendor to Confirm
4.3 | Thermal Stability of the complete equipment keeping in view specified Ambient Conditions and accuracy requirements of BHEL and trouble free operation of the equipment should be ensured by vendor. | Vendor to Confirm
4.4 | The Power Transducers including accessories should be suitable for 24 hrs. continuous operation to its full capacity for 24 hour a day and 7 days a week throughout. Vendor to ensure and confirm the same. | Vendor to Confirm
4.5 | If any safety / environmental protection enclosure is required it should be built in the system by the vendor. | Vendor to Confirm
5 | SAFETY ARRANGEMENTS:
5.1 | The System / Equipment should have adequate and reliable safety interlocks / devices to avoid damage to the equipment due to the malfunctioning or mistakes. System / Equipment functions should be continuously monitored and warning indications through lights with messages (On display panels) should be available. | Vendor to Confirm
6 | DOCUMENTATION : Five sets of operating and maintenance manuals of the Equipment (Hard copies) in English language should be supplied along with the equipment. | Vendor to Confirm
7 | COMMISSIONING OF THE EQUIPMENT
7.1 | Supplier to take full responsibility for carrying out the commissioning, start up, testing of the equipment and it’s controls etc. Service requirement like power etc. shall be provided by BHEL. | Vendor to Confirm
7.2 | Successful proving of the equipment for BHEL components by the supplier shall be considered as part of commissioning. All tests, as mentioned at clause 8 (Equipment Acceptance ) shall form part of the commissioning activity. | Vendor to Confirm
8 | EQUIPMENT ACCEPTANCE: | Vendor to Confirm
8.1 | Tests/Activities should be carried by the vendor at BHEL works while commissioning the equipment : | As per Cl. No. 3
8.2 | Demonstration of all features of the equipment & accessories to the satisfaction of BHEL for efficient and effective use of the equipment. | Vendor to Confirm
9 | GUARANTEE :
9.1 | Guarantee shall be as per Tender terms and conditions | Vendor to Confirm
10 | REFERENCE LIST / QUALIFYING CONDITIONS :
| The vendor shall be inline of manufacture of similar equipments atleast for the last 5 years. Furnish details of experience in manufacture of similar equipments and reference of customers to whom such items were supplied earlier. However, if such equipment(s) has/ had been supplied to BHEL, then such equipment should be presently working satisfactorily for more than six months after its commissioning and acceptance in BHEL. | Vendor to Confirm and submit
11 | Delivery | Specify