## Sheet1
| BHARAT HEAVY ELECTRICALS LIMITED |  | Enquiry No.: | M209CG8P0207SJ1
Heavy Power Equipment Plant, Ramachandrapuram,
| Hyderabad - 502 032. INDIA. |  | Supplier Qtn. No.: | ___________________
|  |  | Date : | ___________________
TENDER DOCUMENTS TO BE FILLED BY THE SUPPLIER FOR SUPPLY OF SUBMERSIBLE DE-WATERING PUMPS
QUANTITY: 2 NOS.
NOTE
1. The "Offered" Column and where applicable, the "Deviations" & "Remarks" Column of this format shall be filled in by the Vendor and submitted along with the offer. Inadequate / incomplete, ambiguous, or unsustainable information against any of the clause of the specifications/requirements shall be treated as non-compliance.
2. The offer and all documents enclosed with offer should be in English language only.
ADDRESS OF THE SUPPLIER :
TELEPHONE NOS.:
FAX NOS.:
E-MAIL ADDRESS :
Sl. No. | Description for BHEL Requirement | SPECIFIED / TO BE CONFIRMED BY | Offered | Deviations | Remarks
A | ITEM No. 001: Quantity: 3 Nos.
1 | APPLICATION : The pump is to be used for
de-watering the water from -6 meter level
test pit seepage water. The pump is to be kept under water at -9 m level.
2 | TECHNICAL SPECIFICATION :
| 2.1 Liquid of pumping | Water combined with traces of dirty oil
| 2.2 Temperature of liquid | 25 - 60 DegC
| 2.3 Flow | 180 cum/hr
| 2.4 Head | 30 mlc
| 2.5 Speed | Suitable to pump
| 2.6 Motor rating | 3 ph, 415 Volts, 50 Hz, suitable to pump speed.
| 2.7 Starting Method | STAR/DELTA
| 2.8 Motor Insulation Class (IEC-85) | F
| 2.9 Enclosure Class (IEC-34-5) | IP-58
| 2.10 Motor should be shielded properly & grease or liquid lubricated bearings | Vendor
| 2.11 The pump should be fitted with built in non-return valve. | Vendor
3 | MATERIAL OF CONSTRUCTION
| 3.1 Pump casing | Stainless Steel
| 3.2 Impeller | Stainless Steel
| 3.3 Pump shaft | Stainless Steel
3.00 | SCOPE OF SUPPLY :
| 3.01 The motor supplied should be designed to | Vendor
operate continuously under normal condi-
tions at a voltage of 400 volts, 50Hz, with a
variation in voltage of -10% /+10%, measured
at the terminal, with STAR/DELTA starting
facility.
| 3.02 Power cable is to be water proof/oil proof, PVC insulated double sheathed flexible copper conductor with 50 meters length | Vendor
| 3.03 Electrical control panel is to be supplied for STAR/DELTA starting, monitoring & protection of Electrical motor & pump | Vendor
| 3.04 Following measurement & protection shall be provided in the control panel | Vendor
| # Voltage & Current in all phases with selector switch | Vendor
| # Phase sequence & single phasing protection | Vendor
| # Over voltage / under voltage protection | Vendor
| # Over load protection | Vendor
| # Dry Running protection | Vendor
| # Short circuit protection | Vendor
| # Lamp indication for all 3 ph supply | Vendor
| 3.05 All suitable standard accessories shall be supplied by supplier | Vendor
4 | SPARES
| 4.1 Itemised break up of mechanical, electrical & electronic spares used on the machine in sufficient quantity as per recommendation of Vendor for 2 years of trouble free operations on three shifts running basis should be offered by vendor seperately. (Seperate price for each spare items) | Vendor
5 | DRAWING/DOCUMENTS
| 5.1 Detailed drawing / catalogue shall be submitted along with offer for scrutinisation. | Vendor
| 5.2 Operating & Maintenance Manuals of machine - 5 sets. | Vendor
| 5.3 Electrical curcuits shall be given | Vendor
| 5.4 Foundation Drawing | Vendor
| 5.5 One additional set of all the above documents on CD ROM, wherever possible. | Vendor
6 | ERECTION & COMMISSIONING
6.1 Supplier representative shall be present during Erection & Commissioning of equipment for suprvision & guidence for satisfactory operation of the equipment
7 | PROVEOUT OF EQUIPMENT PERFORMANCE
| Prove out of pump performance at BHEL works is responsibility of supplier | Vendor
8 | PACKING
| Rigid packing for all items of complete equipment & accessories etc.to avoid any damage/loss in transit. All loose items shall be suitably packed in boxes. | Vendor
9 | GUARANTEE
| The equipment shall be guaranteed for the satisfactory performance for a period of 18 months from the date of commissioning or 24 months from the date of supply, which ever is earlier. And as per BHEL standard terms and conditions. | Vendor
10 | REFERENCE LIST
| Customers reference list shall be furnished along with the offer for similar or higher rating equipments. Following details shall be furnished | Vendor
# Name & Address of the customer
# Month & Year of commissioning
# Application for which the machine is supplied
# Name & Designation of the contact person of the customer with Phone No, Fax No & e-mail Id.
# Performance Certificate from Customer
B | ITEM No. 002: Quantity: 5 Nos.
1 | APPLICATION : The pump is to be used for
de-watering the water from -6 meter level
test pit seepage water. The pump is to be kept under water at -9 m level.
2 | TECHNICAL SPECIFICATION :
| 2.1 Liquid of pumping | Water combined with traces of dirty oil
| 2.2 Temperature of liquid | 25 - 60 DegC
| 2.3 Flow | 60 cum/Hr
| 2.4 Head | 30 mlc
| 2.5 Speed | Suitable to pump
| 2.6 Motor rating | 3 ph, 415 Volts, 50 Hz, suitable to pump speed.
| 2.7 Starting Method | STAR/DELTA
| 2.8 Motor Insulation Class (IEC-85) | F
| 2.9 Enclosure Class (IEC-34-5) | IP-58
| 2.10 Motor should be shielded properly & grease or liquid lubricated bearings | Vendor
| 2.11 The pump should be fitted with built in non-return valve. | Vendor
3 | MATERIAL OF CONSTRUCTION
| 3.1 Pump casing | Stainless Steel
| 3.2 Impeller | Stainless Steel
| 3.3 Pump shaft | Stainless Steel
3.00 | SCOPE OF SUPPLY :
| 3.01 The motor supplied should be designed to | Vendor
operate continuously under normal condi-
tions at a voltage of 400 volts, 50Hz, with a
variation in voltage of -10% /+10%, measured
at the terminal, with STAR/DELTA starting
facility.
| 3.02 Power cable is to be water proof/oil proof, PVC insulated double sheathed flexible copper conductor with 50 meters length | Vendor
| 3.03 Electrical control panel is to be supplied for STAR/DELTA starting, monitoring & protection of Electrical motor & pump | Vendor
| 3.04 Following measurement & protection shall be provided in the control panel | Vendor
| # Voltage & Current in all phases with selector switch | Vendor
| # Phase sequence & single phasing protection | Vendor
| # Over voltage / under voltage protection | Vendor
| # Over load protection | Vendor
| # Dry Running protection | Vendor
| # Short circuit protection | Vendor
| # Lamp indication for all 3 ph supply | Vendor
| 3.05 All suitable standard accessories shall be supplied by supplier | Vendor
4 | SPARES
| 4.1 Itemised break up of mechanical, electrical & electronic spares used on the machine in sufficient quantity as per recommendation of Vendor for 2 years of trouble free operations on three shifts running basis should be offered by vendor seperately. (Seperate price for each spare items) | Vendor
5 | DRAWING/DOCUMENTS
| 5.1 Detailed drawing / catalogue shall be submitted along with offer for scrutinisation. | Vendor
| 5.2 Operating & Maintenance Manuals of machine - 5 sets. | Vendor
| 5.3 Electrical curcuits shall be given | Vendor
| 5.4 Foundation Drawing | Vendor
| 5.5 One additional set of all the above documents on CD ROM, wherever possible. | Vendor
6 | ERECTION & COMMISSIONING
6.1 Supplier representative shall be present during Erection & Commissioning of equipment for suprvision & guidence for satisfactory operation of the equipment
7 | PROVEOUT OF EQUIPMENT PERFORMANCE
| Prove out of pump performance at BHEL works is responsibility of supplier | Vendor
8 | PACKING
| Rigid packing for all items of complete equipment & accessories etc.to avoid any damage/loss in transit. All loose items shall be suitably packed in boxes. | Vendor
9 | GUARANTEE
| The equipment shall be guaranteed for the satisfactory performance for a period of 18 months from the date of commissioning or 24 months from the date of supply, which ever is earlier. And as per BHEL standard terms and conditions. | Vendor
10 | REFERENCE LIST
| Customers reference list shall be furnished along with the offer for similar or higher rating equipments. Following details shall be furnished | Vendor
# Name & Address of the customer
# Month & Year of commissioning
# Application for which the machine is supplied
# Name & Designation of the contact person of the customer with Phone No, Fax No & e-mail Id.
# Performance Certificate from Customer