## Sheet1
M209CG8P0321BDP Design, Engineering, Supply, Erection,Testing and Commissioning of complete equipment of Cryogenic Vessels for Liquid Oxygen (or Nitrogen) 2 X 20 KL Storage Tanks and accessories .
Sl.No. | Description of Item | Specified & To be confirmed | Offered | Remarks
| PURPOSE | Establishment of 2 X 20 KL Liquid Oxygen (or Nitrogen) Storage facility with accessories- handling system.
1 | Specification
1.1 | This specification covers the design, supply erection, testing and commissioning of Liquid Oxygen (or Nitrogen) storage and handling system required for the BHEL, R.C.Puram internal use. The requirement of Oxygen will be a maximum of 500 m3/hr and storage system is designed for a capacity to store the plant’s requirement of twenty days. | Vendor to specify
1.2 | The work shall conform to the codes/specification detailed herein, and any deviations shall be clearly spelt out by the bidder. Any changes during the execution of works due to unforeseen circumstances shall be informed in writing in advance to the purchaser/consultants and prior approval obtained in writing before erecting such changes | Vendor to specify
1.3 | The specification is for installing 2 Nos. X 20KL Liquid Oxygen storage vessels with connected facilities as detailed in this document. | Vendor to specify
2 | Scope of supply
2.1 | Oxygen Storage Vessels: Supply of 2 nos. X 20 KL Liquid Oxygen storage Tanks confirm ASME, Sec.VIII,Div-1 under third party inspection | Vendor to confirm
| Model | Vendor to specify
| Capacity: 20,000 ltrs | Vendor to confirm
| Configuration : Vertical | Vendor to confirm
| Working Pr.: 10 Kg/cm² | Vendor to confirm
| Loss rate per day : Below 0.5per day | Vendor to confirm
| Max. Consumption /Hour: 500 Cu.Mts/Hr | Vendor to confirm
| DesignCode: The vessel should confirm ASME, section VIII, Div I or equivalentbe | Vendor to confirm
| Approval: CCOE approval for supply,installation and usage of the equipment. Approval fee to be paid by vendor only. | Vendor to confirm
| Standard: Any other standard which is equivalent to the above design code and has the approval from Controller of Explosives can be used. | Vendor to specify
2.2 | Vaporizers for Line pressure:Supply of Atmospheric vaporizers for Line supply at 10 Kg/cm2 Capacity 500 m3/hr – 2 nos | Vendor to confirm
2.3 | Vaporizers for Cylinder filling : Supply of suitable Atmospheric vaporizers at pressure 150 Kg/cm2 for cylinder Filling – 2nos | Vendor to confirm
2.4 | Liquid Oxygen Pumps : Supply of Liquid Oxygen pumps – suitable for Cylinder filling at 150 Kg/cm2 – 2nos | Vendor to confirm
2.5 | Filling Manifold banks:Supply of Cylinder filling manifold Bank 9 cylinders x 2 Nos with all accessories - 2 sets | Vendor to confirm
2.6 | Safety fititings:All safety fittings for the Vessels and pipe work shall be procured from manufacturer approved by CCE and accompanied by test certificates issued by third party. | Vendor to confirm
2.7 | Earthing of Vessels and equipments: The storage Vessels and equipments shall be effectively earthed to prevent build up of static electrically. Vessels shall be earthed with copper strip 25mm X 3mm and connected earth pit as per standard practice. All parts of equipment not intended to be live shall have an effective connection to earth. | Vendor to confirm
2.8 | Gas Flow measurement instrumentation system - 1No. | Vendor to confirm
3 | General requirements
3.1 | The tenderer shall quote for the design, supply of complete technical equipment of Cryogenic Vessels and accessories including instrumentation, valves and fittings and other equipment of Cryogenic pumps, atmospheric evaporators , cylinder filling manifold - erection, testing and commissioning of the system required for the Liquid Oxygen (or Nitrogen) Storage & handling system for BHEL, R.C.Puram – 502 032. All costs involved to got statutory clearances and other agencies if any are to be borne by the tenderer. . | Vendor to specify
3.2 | Reputed indigenous / import make of the components are to be offered by the tenderer. Details of type and make to be indicated in the bid along with Product data and Technical literatures. | Vendor to specify
3.3 | The tenderer shall be responsible for making final adjustments of foundation levels, dressing or foundation surfaces bedding and grouting of anchor bolts and inserts into the constructed civil works, cutting and patching of existing concrete structure as may be required to be done for the erection of the equipment etc. | Vendor to specify
3.4 | Any civil work damaged by he tenderer, during erection work shall have to made good by the tenderer at his own cost to the satisfaction of the purchaser.. | Vendor to specify
3.5 | The tenderer shall be responsible for the delivery of equipment and materials at Stores (at M/s. BHEL. R.C.Puram). The storage facilities shall be offered by purchaser. Depending on the availability of loading and unloading facilities will be offered by the purchaser. | Vendor to specify
3.6 | The tenderer shall make arrangement for all the items including consumables required for the proper installation of the Cryogenic vessels till the final acceptance of the equipment by the purchaser. Detailed specification of all consumables shall be furnished to the purchaser for subsequent procurement. | Vendor to specify
3.7 | Tools and tackles, instruments and other accessories required for the assembly and erection shall be provided by the tenderer. | Vendor to specify
3.8 | The tenderer shall be free to quote for alternate design of the plant and equipment which can efficiently perform the specified requirements. The tenderer, shall however submit alternate proposal on the basis of data considered techno-economically superior | Vendor to specify
3.9 | All interconnecting piping, valves, miscellaneous fittings together with the support shall be supplied within the design limits . | Vendor to specify
3.1 | The party should supply the Tanks from the manufacturer having reference of 10 vessels of Similar or Higher capacity and the vessels must be working for more than 2 years. Full address of customers with the names of contact person to be given. | Vendor to specify
3.11 | The power supply shall be made available at 415 V, 3, 3 wire, 50 Hz, AC with neutral earthed from the outgoing terminals of the purchaser’s substation, circuit breakers / power distribution board switch fuse units. The control shall be 240 V, AC single phase 50 Hz. | Vendor to specify
3.12 | Industrial water for all uses shall be made available at one single point in the Liquid Oxygen Storage area. | Vendor to specify
3.13 | Necessary illumination work shall be done by the purchaser. | Vendor to specify
3.14 | All civil engineering works including foundations for equipments shall be carried out by the purchaser, as detailed in the tenderer’s drawing. Necessary civil drawings should be submitted in two weeks from the date of LOI / Order. | Vendor to specify
3.15 | The tender may visit the purchaser’s site for assessment of the quantum of work involved, before quoting. | Vendor to specify
3.16 | The tender shall indicate details of all input cables of quoted system. Input cabling is under purchase’s scope. | Vendor to specify
3.17 | The tenderer shall furnish item-wise spare parts list with corresponding prices for two years plant normal operation of plant and equipment supplied by the tenderer, including the parts to be imported | Vendor to specify
3.18 | Skilled, unskilled and supervisory personnel shall be provided by the tenderer. | Vendor to specify
4 | Equipment Manufacture:
4.1 | All equipment shall be of reputed make. The make of bought-out items shall be indicated in the tender. | Vendor to specify
4.2 | All equipment supplied by the tenderer shall be painted as per the instructions of the purchaser in accordance with the colour code in practice. | Vendor to specify
4.3 | All moving or rotating parts shall be provided with suitable safety guards | Vendor to specify
4.4 | Adequate safety measures shall be ensured in the design of all equipment for the protection of operators during working of plant and equipment. | Vendor to specify
4.5 | A non-corrodable name plant in English language stating identification number, voltage, full load current frequency, rated capacity, control voltage, speed, etc., which ever is necessary, shall be provided on each equipment | Vendor to specify
4.6 | The plant and equipment included in Cryogenic storage and handling system shall be designed, assembled and tested in accordance with the latest relevant standards in cases where suitable Indian standards are not available, the equipment shall conform to relevant International standards, codes and practices | Vendor to specify
4.7 | All electrical equipment shall conform to the latest Indian Electricity Regulations as regards safety, earthling and other provisions specified therein for installation and operation of electrical equipment. | Vendor to specify
4.8 | All equipment shall conform to the provisions of statutory and other regulations in force, such as Indian Explosives Act., Indian Factories Act, Indian Petroleum Act, C.I.E. Regulations – Government of India and Government of A.P. | Vendor to specify
4.9 | All equipment accessories, spares and other components of the plant shall be manufactured with first class materials of approved quality and under best workmanship. | Vendor to specify
4.1 | All the drawings, documents, manuals, etc. shall be in English language, and all dimensions shall be marked in metric system. The instruments shall be calibrated in metric units. | Vendor to specify
4.11 | All surfaces shall be cleaned by wire brushing before painting. Painting shall not be done on exposed work in wet weather. | Vendor to specify
4.12 | All equipment supplied shall be shop tested according to the relevant standards and the test certificate shall be furnished by the tenderer. Purchaser will witness all the major tests as agreed between the tenderer and purchaser at manufacturer’s place. Detailed quality plan shall be submitted by the tenderer indicating the data such as items/material specification & make /type of tests/witnessed by. | Vendor to specify
4.13 | Sample specimens of materials and fabrication shall be furnished, if required, by the purchaser, free or cost. | Vendor to specify
4.14 | All items of work welded at site shall be subjected to inspection by the purchaser. | Vendor to specify
4.15 | In case of weld defects, prior approval of the purchaser’s inspector shall be obtained before repairs. The repaired joints shall be completed to the satisfaction of the purchaser’s inspector. | Vendor to specify
4.16 | Any material declared defective by the purchaser, during fabrication/erection/testing shall be replaced or repaired without delay and at not additional cost. | Vendor to specify
4.17 | Delivery period: 6 months from LOI | Vendor to confirm
5 | Data to be furnished with the tender
5.1 | The tenderer shall submit the following drawings and information along with the tender without which the tender may not be considered. | Vendor to specify
5.2 | Preliminary general arrangement drawing of the Liquid Oxygen storage and handling system, indicating the design limit. | Vendor to specify
5.3 | Broad specifications of the equipments offered indicating the technical features, material of construction, etc. | Vendor to specify
5.4 | Schematic flow and instrumentation diagram of the system | Vendor to specify
5.5 | Preliminary single line diagram of electrical. | Vendor to specify
5.6 | Preliminary schedule of drives indicating rating | Vendor to specify
5.7 | Connected electrical load for 30 minutes of maximum demand | Vendor to specify
5.8 | Service requirements such as water, compressed air, etc. shall be indicated. | Vendor to specify
5.9 | Catalogue, brochures, pamphlets, etc. | Vendor to specify
5.1 | The tenderer shall indicate in a bar chart from the schedule for design, manufacture, delivery, erection, testing and commissioning of the plant and equipment to be supplied for BHEL. | Vendor to specify
6 | Documentation
6.1 | The successful tenderer shall supply six sets of the contract drawings. | Vendor to specify
6.2 | General layout drawings with cross-section showing the overall dimensions of equipment, foundation details, pipe work, valves and electrical cable layout and required clearance, etc. | Vendor to specify
6.3 | Dimension drawing showing front, rear, and sectional views and position of power and control entries and any service connecting lines. | Vendor to specify
6.4 | Electrical circuit control diagram. | Vendor to specify
6.5 | External connection diagram. | Vendor to specify
6.6 | Single line wiring diagram. | Vendor to specify
6.7 | Bill of material with cable schedule. | Vendor to specify
6.8 | Detailed drawings and specifications of al wearing parts and the parts subjects to breakages. | Vendor to specify
6.9 | The above drawings shall be supplied with in a period of two weeks from the date of placement of order | Vendor to specify
6.1 | The tender shall supply six sets of all erection drawings for assembly of vessels and accessories. The erection drawings shall, however, be submitted as early as possible but not later than one month before the dispatch of the respective equipment from the supplier works. | Vendor to specify
6.11 | All the revised design and drawings, pertaining to any modification/alternation to the plant from the date of submission of first drawing till completion of erection, shall be furnished. | Vendor to specify
6.12 | Instruction manuals for operation and maintenance of equipment and controls including lubrication charts shall be supplied with the delivery of equipment. | Vendor to specify
6.13 | Relevant manufacturer’s Technical literature shall be supplied with the delivery of equipment. | Vendor to specify
6.14 | On completion of work, the tenderer shall supply six sets of prints and one set of tracings as built. | Vendor to specify
6.15 | The tenderer shall submit the following data/technical information within 2 weeks from the date of the placement of order. | Vendor to specify
6.16 | Complete load data of equipment including dynamic loading to enable the purchaser to prepare all civil engineering work, the outline of foundations of all equipment under the scope of the supply indicating location of anchor bolts, conduits and other parts to be built in the foundation walls, tunnel and other relevant items. | Vendor to specify
6.17 | Requirement of special materials for civil works. | Vendor to specify
6.18 | Routes, sizes and levels of underground cable tunnels and other openings in the concrete. | Vendor to specify
6.19 | Electrical load data, service consumption data power, cooling water, etc. indicting the maximum, minimum and average consumption. | Vendor to specify
6.2 | The tenderer shall give detailed technical specifications of the equipment offered together with general arrangement drawings and other documentation as mentioned above for approval of the purchaser/consultant before the commencement of manufacture and erection. Such approval when accorded shall, however, not relieve the tenderer of his responsibilities so far as the satisfactory performance of the system is concerned. | Vendor to specify
6.21 | The purchaser (BHEL) reserves the right to order the system on any tenderer either fully or part of the system irrespective of the bid ranking. | Vendor to specify
6.22 | No import licence will be provided by BHEL . However the delivery of imported items should match over all project schedule. | Vendor to specify
7 | Major Exclusion
7.1 | All civil work, Boundary wall or fencing, input cabling. | Vendor to specify
8 | Erection
8.1 | All equipments/ parts shall be assembled and erected by the tenderer. All equipment shall be placed on its respective foundations, properly leveled and aligned with precision level measuring instruments, checked for proper clearance between moving and stationary parts whenever applicable and grouted on the foundation. | Vendor to specify
8.2 | The tenderer shall take note of the working conditions, practices and agreements prevailing in the area. The tenderer shall carry out the erection work in such a manner that it shall not affect the operation / construction of the other units. | Vendor to specify
8.3 | After erection all temporary structures, super-structures, storage sheds, etc. constructed by the tenderer shall be removed and the place shall be kept clean. | Vendor to specify
9 | Commissioning & Acceptance Tests.
9.1 | After erection at site, the tenderer shall conduct, for individual equipment, all tests required to ensure that the equipment supplied conforms to the specified requirements and complies with the requirements or applicable codes. | Vendor to specify
9.2 | Details of such tests shall be mutually agreed upon by the tenderer and the purchaser at least one month before such tests are carried out. | Vendor to specify
9.3 | The tender shall give at least seven days notice for readiness of the plants for acceptance tests to be carried out. Tests shall be carried out in the presence of purchaser’s representative. Purchaser shall make available all services required for tests like power, water, etc subject to adequate notice of the requirements by the tenderer. The purchaser will issue preliminary acceptance certificate after the acceptance of the following. | Vendor to specify
9.4 | The equipment is erected conform to the approved drawings | Vendor to specify
9.5 | The equipment is pressure tested in accordance with the accepted norms. | Vendor to specify
9.6 | The correctness of installation of all equipment.Commissioning shall be deemed completed upon satisfactory completion of the guarantee tests and issue of final acceptance certificate. The acceptance certificate shall be governed by the General Conditions of the Contract of M/s Bharat Heavy Electricals Limited, R.C.Puram,Hyd-32 | Vendor to specify
10 | Guarantee
| The tenderer shall stand guarantee for a period of 24 MONTHS after final commissioning of the plant for materials, equipments, workmanship and steady & safe operation of the Liquid Oxygen storage and handling system with their auxiliaries, as a whole giving the specified output as per the technical specifications or as finalized at the time of placement of order. Any defects arising during the guarantee period shall be made good by the contractor at his own cost to the satisfaction of the purchaser and it necessary, the performance test shall be repeated after the replacement of defective parts or any other modification / rectification carried out by the contractor. | Vendor to specify
Important Note:
Before quoting for above, vendor can visit our unit to understand the requirement of the facility and quote accordingly.