## Spec.of 2 X 20MT LPG Yard
M209CG8P0325BDP Design, Engineering, Supply, Erection, Testing and Commissioning of 2 X 20 MT Above Ground LPG Storage Yard with necessary LPG accessories and distribution of LPG Header pipe line system.
Sl.No. | Description of Item | Specified & To be confirmed | Offered | Remarks
| PURPOSE | Establishment of 2 X 20 MT LPG Yard and distribution of Header and pipelines to all the blocks for Furnaces, Heating and cutting application as per Tender Sepcs.
1.0 | Specification
1.1 | Design (Basic and detailed Engineering), supply of all materials, equipments items and components with attendant peripherals required with in the Plant battery limits as per sample SITE plan & P&I drawings No.HY/M&S/GS/LPG/01 & HY/M&S/GS/LPG LAYOUT)/ plans approved by the Chief Controller of Explosives, Nagpur under the Satatutory requirements of Static and Mobile Pressure Vessel Rule 1981 and other complying standards, IS:6044 Part II, Including erection, testing and commissioning of LPG Bulk Storage System, Capacity 2X20MT, suitable for Above Ground Storage . | Vendor to confirm
1.2 | Supply and installation of 2X20 MT LPG Storage tank, unloading system, vapourisers, safety fittings, valves, pressure regulating system, instrumentation, electrical system,fire safety system etc. as detailed below. | Vendor to confirm
1.3 | Supply and laying of pipeline from storage yard to different shop as per Drawing No. HY/M&S/GS/LPG HEADER PIPE LINE/ 01( Supply total materials required for laying pipeline except running length of pipelines.Required pipes shall be supplied by BHEL free of cost in standard length. Paint in the scope of vendor). | Vendor to confirm
1.4 | Complete civil work with in the baterry limit is in vendor scope as per CCOE approved layout. | Vendor to confirm
Scope of supply
2.0 | LPG storage tank:
2.1.1 | Quantity | 2 nos.
2.1.2 | Tank capacity | 20 MT
2.1.3 | Water capacity | 46,200 Litrs Water Capacity
2.1.4 | Design code | IS: 2825 - 1969, Class A
2.1.5 | Design Pressure | 14.5 Kg/ sq.cm + Static Head
2.1.6 | Design temperature | 55 deg.C Max / -6 degree C Min.
2.1.7 | Working temperature | Ambient
2.1.8 | Hydro test pressure | 21.75 Kg/sq.cm min./ As per Code of Construction
2.1.9 | Installation configuration | Above Ground
2.1.10 | Corrision Allowance | 1.5 mm
2.1.11 | Radiography | 100%
2.1.12 | Heat treatment | As per Code requirement
2.1.13 | Third party inspection certificate for tank and system | CCOE approved
2.1.14 | Material of Construction | SA 516 Gr. 70 or SA 537 Class- I or equivalent Boiler and Pressure Vessel Quality Steel
2.1.15 | Flanges | SA 105 / SA 516 Gr.70 /SA 515 Gr.70
2,1,16 | Couplings | SA 105
2.1.17 | Studs | SA 193 Gr.7
2.1.18 | Nuts | SA 194 Gr.2H
2.1.19 | Size of Manway | 20" NB X 1 No. for A/G
2.1.20 | Estimated Tank Weight | Vendor to give( WITH OUT PRODUCT)
2.1.21 | Surface Protection | Total Dry Film Thickness 140 microns min. With primer & finished paint on outside.
3 | Safety fitting for the Propane/LPG Tanks. Each tank shall have the following safety fittings
3.1.1 | 2"X 3" angle body safety relife valve complete with isolation valves, safety vents and rain hoods etc. | 3 nos or as required vendor to specify
3.1.2 | 1/4" NPT fixed level gauge | 1 No or as required vendor to specify
3.1.3 | 1" NPT Slip Tube Gauge or equiv. | 1 No or as required vendor to specify
3.1.4 | Pressure Gauge Rego-948 or equivalent 6" dial | 1 No or as required vendor to specify
3.1.5 | 0-300 Psig, complete with bank up Excess Flow Check Valve 3/4" NPT Female Presure Gauga Range 0-500 Psig. | 1 No or as required vendor to specify
3.1.6 | 3/4" NPT Thermodial -20 Deg. C to + 100 Deg.C | 1 No or as required vendor to specify
3.1.7 | 2" MGM make or equivalent make but CCOE approved Excess Flow Check (EEFC) Valve for liquid and vapour lines vapour recovery.(Wafer/ sandwhich type) | 5 Nos as required vendor to specify
3.1.8 | High pressure switch interlock for compressor c/w transmitter and alarm | 1 No or as required vendor to specify
3.1.9 | High level switch interlock for unloading pump c/w transmitter and alarm | 1 No or as required vendor to specify
3.1.10 | Special sealless Magnetic level Gauge of Rochester, Belgium for continous reading of Tank's liquid content | 1 No of 8" Dial withTransmitter for Remote Read Out at Control Panel - vendor to specify and confirm
4.0 | LPG Unloading Pump:( Skid mounted unit)
4.1 | Quantity | 1 no.
4.2 | Function | Liquid transfer from mobile tanker to storage tank
4.3 | Type | Sliding Vane Positive displacement type with built in Relief valve, complete with Flame proof Motor base plate guard etc. As per as per Drawing No. HY/M&S/GS/LPG UP/ 03. 300 LPM @ 2 Kg/Cm2
4.4 | Capacity | 300 LPM
4.5 | Make and model 521/LGL2DE (Croken / Blackmer , USA or Reputed make approved by CCOE) | Vendor to specify
4.6 | Inlet and outlet connection / size | To suit the pipe connection as per design
4.7 | Motor duly coupled:Power rating | Flame Proof suitable for group IIA & IIB Gases: 5HP
4.8 | Starter | DOL Flame proof
4.9 | Drive | V- Belt
4.10 | Duty | Intermittent
4.11 | Special Features | Tested on Propane/LPG
4.12 | Unloading Pump | < 2 Hrs. from 18 MT Tanker
4.13 | Extended Performance Gurantee of 36 months from the date of commissioning or 42 months from FOB date, whichever period is expires earlier as pre-requisite | Vendor to specify
5.0 | Unloading Vapour recovery compressor:
5.1 | Quantity | 1 no.
5.2 | Make and model Croken/Blackmer, USA make approved by CCOE | 291-107/LB161LU c/w instrumentation as per tender GA Drawing No. HY/M&S/GS/LPG/COMP/ 04, Croken Blackmer USA make
5.3 | Type of Compressor | Reciprocating Air Cooled Non - Lubricated type special desined for LPG/Propane service
5.4 | Bore | 76.2 mm
5.5 | Stroke | 63.5 mm
5.6 | piston Displacement | 28 MCH at 825 RPM
5.6 | Max working pressure | 350 Psia
5.7 | Motor type and Rating | 7.5 HP at 825 RPM in Flame Proof with local Flame Proof Push button
5.8 | Max Compression Ratio Continous Duty | 5
5.9 | Max Compression Ratio Intermittent Duty | 9
5.1 | Protection agaist dry run | Vendor to confirm
5.11 | Provision of liquid sensor at inlet | Vendor to confirm
5.12 | Total Time to evacuate 40CuM LPG Tank lory | 4.5 hrs
5.13 | Total Time to evacuate 25CuM LPG Tank lory | Appx.3 Hrs
5.14 | Furnish Compressor Performance Table | Vendor to confirm
5.15 | Extended Performance Gurantee of 36 months from the date of commissioning or 42 months from FOB date, whichever period is expires earlier as pre-requisite | Vendor to specify
6.0 | LPG Vaporiser:
6.1 | Quantity | 4 nos.
6.2 | Capacity | 300 kg/hr in modular design.
6.3 | Make and model (Reputed make approved by CCOE) | Vendor to specify
6.4 | Design/Type | Electrically heated, hot water bath type, to deliver dry saturated LPG vapour.Design of CCOE approved make and As per GA Drawings No. HY/M&S/GS/LPG/05
6.5 | Inlet and outlet connection / size | To suit the pipe connection as per design
6.6 | Design Pressure | Vendor to specify
6.7 | Test Pressure | Vendor to specify
6.8 | Solenoid valve at liquid inlet | Vendor to confirm
6.9 | Pressure switches | One safety pressure switch each on the vapouriser before the regulator and one pr.switch on the outlet after the regulator to control the solenoid valve.
6.10 | Pressure relief valve | Vendor to confirm
6.11 | Mounting arrangement | Vendor to specify
6.12 | Dimension details | Vendor to specify
6.13 | Shell/ Coil- Design/MOC | ASME/TEMA R; C S / SS 316
6.14 | Power | Vendor to specify
6.15 | Controls : Inlet Safety Solenoid Valve - Hugh Level Float / Hi. Pr. Switch - RTD's for temp controls - Digital Temp. Indicator Controller | Vendor to confirm
6.16 | Electrical | 415 V /3PH/50 Hz/required capacity CCOE Nagpur approved
7.0 | Valves & Fittings for the Pipeline per tender drawing No.HY/M&S/GS/LPGYARD/01
7.1 | Fire Safe & Antistatic design Full Bore Ball Valves | Vendor to calculate as per P&ID
7.2 | Pop action valve, NRV's,Instruments,controls etc. (Required quantity and size as per design) | Vendor to confirm
7.3 | Pipe fittings for the valves / pipelines (required quantity and size as per design.) | Vendor to specify
7.4 | Make and material of the valves, gauges, fittings | Vendor to specify
8.0 | Piping system inside yard for LPG liquid and Vapour line as per tender drawing No.HY/M&S/GS/LPGYARD/01/
8.1 | Seamless sch. 80 heavy duty pipelines - Liquid inlet / outlet, vapour balance / outlet,, drain line. (required size and quantity over and above the existing piping as per desig,) | Vendor to confirm
9.0 | Structural steel:
9.1 | Steel required for approach platforms ( chequered plates / floor grills ) on the tank, piping supports and other requirements as per design | Vendor to confirm
10.0 | Accessories for LPG Piping System. With in yard:-
10.1 | Strainers for Vaporizers (Qty. & size as per design) | Vendor to confirm
10.2 | Strainer for LPG Pump (quantity and size as per design) | Vendor to confirm
10.3 | Non - return valve for LPG Pump (quantity and size as per design) | Vendor to confirm
10.4 | Make, material, test pressure of the above Items | Vendor to confirm
11.0 | Pressure Regulating Station: | Vendor to confirm
11.1 | Pressure Regulators (required quantity and size as per design) | Vendor to confirm
11.2 | Type : Director Actuating Type with auto change over Range of Inlet : 14.5 KG/Cm2 (Max) 3.5 Kg/Cm2 ( Min) Capacity : 900 Kg/ hr. max./ 300 Kg/Hr. min. on continous basis Out let Pressure : 1.5 - 2.0 KCSG adjustable) with +/_ 0.5 KCSG Model/Make : Fischer/Elster/RMG/COPRIM/NIRMAL/ Equ. Approved by CCOE | Vendor to specify and confirm
11.3 | Filters for pressure requlator ( Required quantity and size as per design) | Vendor to confirm
11.4 | Slam shut - off for pressure regulator (Required quantity and size as per design) | Vendor to confirm
11.5 | Make and end connections | Vendor to confirm
12.0 | Decanting Hoses:
12.1 | Double ply wire braided neoprene hose for liquid and vapour (Required quantity and size as per design) | Vendor to confirm
12.2 | Make and pressure rating of the hoses | Vendor to confirm
13.0 | Fire Fighting System ( As per SMPV Rules, OISD 169 & TAC )
13.1 | Fire Extinguishers of DCP type. ( required quantity and capacity as per design) | Vendor to confirm
13.2 | Sand buckets with top cover (required quantity) | Vendor to confirm
13.3 | 2 nosFire hydrant system as per OISD 169 norms, fire hydrants Nozzles, fire hydrant hoses, fire hose boxes of required specifiaction and quantity | Vendor to confirm
13.4 | Ring main pipe for fire hydrant and sprinkler system, nozzles on tank, unloading area, pump, compressor shed. | Vendor to confirm
13.5 | Total piping from storage water tank to yard and all necessary pumps,piping etc. | Vendor to confirm
13.6 | Make of the fire fighting system components | Vendor to confirm
13.7 | Fire water manually operated main control valve - 1 No | Vendor to confirm
OPTIONAL
13.8 | Construcytion of 320CuM Storage water tank as required by CCOE Nagapury | Vendor to confirm
14.0 | Instrumentation:
14.1 | Remote opearted valves (Required quantity and size as per design) | Vendor to confirm
14.1.1 | Mode of operation of Remote Operated Valve (ROV) | Vendor to specify
14.1.2 | Make, model,material of the valves | Vendor to specify
14.1.3 | Air pressure required for operation | Vendor to specify
14.2 | Pressure gauges (Required quantity and size as per design) | Vendor to confirm
14.3 | Level switches (flame proof) for high LPG level alarm | Vendor to confirm
14.3.1 | Make, model, accuracy | Vendor to specify
14.4 | Level switches (flame proof) for low LPG level alarm | Vendor to confirm
14.4.1 | Make, model, accuracy | Vendor to specify
14.5 | Emergency shut - down switches | Vendor to confirm
14.6 | Gas Flow meter with Flow Computer | Vendor to confirm
14.6.1 | Model DN 80 - G 100 Turbine Meter with Mechanical Register Mounted with Electronic Volume Concverter (EVC) OR Intelligent Turbine Gas Meter Model DN 80- G100 complete with Gas inlet filter, upstream & down stream stragtness and by-pass line with isolation valve | Vendor to confirm
14.6.2 | The flow meter shall register both the line flow as also complete flow in SCMH . SCMH shall be used to manually calculate the mass of propane flowing thro' the meter | Vendor to confirm
14.7 | Crash Post:- 3 Nos X 4" NB class C Protection Crash Post to Protect the unloading area from accidental damage by tank lorry a per NEPA 58 | Vendor to confirm
14.8 | Bluck Head: Structural steel fabricated bulk head of adequate strength to withstand rigidity and pull away force of the LPG Tank Lorry and with out pulling away the valves, piping, pump and tank down stream of the unloading hose as per NFPA 58 | Vendor to confirm
15.0 | MCC / Instrumentation control panel:( For Safe Area and in NON- Flame Proof design).
15.1 | Non - flame proof, free standing, dust and vermin proof, compartmentalized, made out of CRCA sheet steel. | Vender to specify and confirm
15.2 | Panel to comprise of all switchgears, indicationg lamps, instruments, push buttons, wiring, MCB, Terminal blocks, busbars, painting etc., | Vendor to confirm
15.3 | Electrical power and control cabling with cable trays, terminations as required | Vendor to confirm
15.4 | The Apparatus and circuits in the Panels shall be so arranged as to facilitate operation and maintenance and at the same time to ensure the necessary degree of safety. | Vendor to confirm
15.5 | Provision shall be made in the panel for terminating the incoming cables as required as single line diagram. | Vendor to confirm
15.6 | Provision shall be made for permanently earthing the frames and other metal parts by two independent connection. | Vendor to confirm
15.7 | Incoming Feeder: 1 No. TP MCCB for Incomer. One set of 96 mm square Ammeter(Amps) complete with selector switch and CT's.One set of 96 MM square voltmeter ( 0-500) Complete with control fuses and selector switch. One set of phse indicating lights with control fuses . | Vendor to confirm
15.8 | Out going Feeder: Separate outgoing feeder shall be provide for the following equipments. Compressor 7.5 HP - 1 No Unloading Pump Motor 5 HP - 1 No. Spare Feeder - 1 No Vaporizer 36 Kw each - 4 No's TP MCCB, S P Preventer shall be provided. Contaractor for DOL starting , start and stop push buttons, Auxillary contactors for interlocking/ sequence of operation, contol terminals complete in all respect with interconnections. Control wiring for sequence of operation shall be inculed to complete the system/ safety shall be incorporated by providing for triping and or alrm annuncian. The wiring shall be PVC insulated aluminium conductor cable of 650/1100 volts grade confirming to IS: 1554 as required. All enclosurees , terminals, cnnection shall be explosive proof. Provision will be made for remote/ local control of all equipments. | Vendor to specify
16.0 | Earthing:
16.1 | As per IS 3043 from to independent earthing pits | Vendor to confirm
16.2 | Earth strips of required size for tank, unloading pump, compressors, vapourisers, MCC and other electrical items | Vendor to confirm
16.3 | Copper jumpers for all LPG pipeline flanges | Vendor to confirm
17.0 | Hardware items: | Vendor to confirm
17.1 | Flanges, bends, tees, reducers, gaskets, nuts, bolts etc., required in LPG and water piping system | Vendor to confirm
18.0 | Painting | Vendor to confirm
18.1 | Anti corrosive primer painting of tanks as per code, pipelines, unloading pump, compressor, Vaporizer, Regulating Station, Valves and finish paint in different colours as per colour code for vapour and liquid lines. | Vendor to confirm
19.0 | Installation of LPG distribution pipeline outside yard:HY/M&S/GS/LPG HEADER PIPE LINE/ 01
19.1 | Installation of LPG distribution pipeline on existing trestle, size 4"(100 mm) NB x sch.40 with necessary clamps, welding and painting with one coat of red oxide paint and two coats of synthetic enamel paint. This line to be laid from LPG storage yard upto all Production blocks. Required pipes shall be supplied by BHEL free of cost in standard length. All the remaining required materials are in the scope of vendor. | 1800 RM for main Distributor Header
19.2 | Installation of LPG distribution pipeline on existing trestle, size 2 1/2 "(62.5 mm) NB x sch. 40 with necessary clamps, welding and painting with one coat of red oxide paint and two coats of synthetic enamel paint. This line to be laid from LPG storage header at sr.no.19.1 above and upto various Production blocks. Required pipes shall be supplied by BHEL free of cost in standard length. All the remaining required materials are in the scope of vendor. | 850 RM for 02 block, for Block 04 and for Block 06
19.3 | Installation of LPG distribution pipeline on existing trestle and structure inside block 04 & 05 with necessay support, size 2"(50 mm) NB x Sch.40 with necessary clamps, welding and painting with one coat of red oxide paint and two coats of synthetic enamel paint. This line to be laid as sub distrubution line in each product block. Required pipes shall be supplied by BHEL free of cost in standard length.All the remaining required materials are in the scope of vendor. | 2500 RM for 02 Block, for Block 04 & 360 RM for Block 05
19.4 | Installation of LPG distribution pipeline on the trestle and steel columns inside block 08, line size 1.5" NB x sch. 40 with necessary clamps, welding and painting with one coat of red oxide paint and two coats of synthetic enamel paint. Required pipes shall be supplied by BHEL free of cost in standard length. All the remaining required materials are in the scope of vendor. | 225 RM for Block 08
19.5 | Installation of LPG Distribution pipe on existing trestles and steel columns inside various blocks, 1" NB x Sch.40 with necessary supports and clamps, welding and painting with one coat of red oxide paint and two coats of synthetic enamel paint. Required pipes shall be supplied by BHEL free of cost in standard length. All the remaining required materials are in the scope of vendor. | 5750 RM Please see attached pipeline schedule.
19.6 | Supply and installation of required Valves( 4" valves 4 nos, 2" valves 15 nos, 1/1/2 valves 2nos and 1" valves 5 nos),bends,elbows, flanges, metallic gaskets of various sizes as required for for the installation of the above pipelines. | Pls see Tender SLD and pipeline schedule
19.7 | Installation of 125 nos. Downcomers of 1" pipe and 6 mts drop length with 1" ball valve with each downcomer on existing trestles and steel columns inside various blocks, 1" NB x Sch.40 with necessary supports and clamps, welding and painting with one coat of red oxide paint and two coats of synthetic enamel paint. Required pipes shall be supplied by BHEL free of cost in standard length. All the remaining required materials are in the scope of vendor. | Vendor to confirm
19.8 | Erection and painting of Pre-fabricated trestles that support the LPG pipelines( from LPG Yard to exisiting producer gas plant approximaately 100mts ). The trestles will be of 7.5m in height and fabricated out of M.S. pipes. The foundation for the trestle including the bolts and fabrication of trestle are in the scope of BHEL. The trestles to be painted with one coat of red oxide paint and two coats of synthetic enamel paint. Paint in the scope of vendor. | Vendor to confirm
20.0 | Control elements, Instruments and gauges:
20.1 | Supply and installation of safety control / isolation valves, flange type non return valves in the distribution header lines for safety and maintenance purpose as per safety norms. Details and quantity as per design to be furnished in the offer. | Vendor to confirm
20.2 | Minimum the following materials to be supplied by vender for Header ppe line . 1). 4" NB Ball Valve - 5 Nos 2). 2.1/2" NB Ball Valve - 6 Nos 3). 2" NB Ball Valve - 12 Nos 4). 1 1/2" NB Ball Valve - 5 Nos 5). 1" NB Ball Valve -200 Nos( Including down comer requirement) 6). Flame Arrestor 4" NB - 2 Nos 7). 4" NB Back pressure Check valve - 2 Nos 8). 4" NB Liquid Trap with Gas Desludger -4 Nos 9). 2 1/2" NB Liquid Trap with Gas Desludger -2 Nos 10). 2" NB Liquid Trap with Gas Desludger -4 Nos | Vendor to confirm and specify
20.3 | Supply and installation of Pressure gauges with isolation valves and end fittings at suitable locations in the pipeline. Specification and make to be furnished in the offer. | Vendor to specify
20.4 | Supply of Structural Support (per Kg) With necessary flanges, bends and elbows tees, pipeline brackets, U clamps, nuts, bolts and gaskets , safety fitting and traps as required any other which are not mentioned which are required laying of pipeline on existing support structure | Vendor to specify
21 | Design, Erection and commissioning:
21.1 | Approval and licence from CCOE, Nagpur (Liason services) | Vendor to confirm
21.2 | Preparation of layout drawings for storage yard showing the location of various items / P.I. diagram / civil design and drawings | Vendor to confirm
21.3 | Preparation of calibration chart on the basis of tank capacity for liquid level measurement | Vendor to confirm
21.4 | Drawing for vapouriser, Compressor and pump sheds | Vendor to confirm
21.5 | Plan of surrounding facilities as per SMPV (U) Rules | Vendor to confirm
21.6 | Design calculation for all equipments | Vendor to confirm
21.7 | Design of safety / control elements in the LPG distribution system meeting the safety norms. | Vendor to confirm
21.8 | Third party inspection certificate for LPG tanks, Safety Fittings | Vendor to confirm
21.9 | Erection of complete system comprising LPG Tanks, vaporisers, pump, compressor, Piping & Valves, Instrumentation / Electrical systems and all other Items included in completion of system within yard. | Vendor to confirm
21.10 | The vendor should arrange necessary equipments, tools to carry out the erection and commisssioning. If necessary welding machine and cutogen torch to carry out welding and cutting operation. | Vendor to confirm
21.11 | Conducting leak test in the LPG disdtribution system pipelines in accordance with the provisions made in IS: 6044 part II. | Vendor to confirm
21.12 | Complete civil works with in the yard and Fire Water Storage Tank , fencut drg. as approved layout. | Vendor to confirm
21.13 | Construction of Sheds for vapouriser, pumps,compressor and MCC room. | Vendor to confirm
21.14 | Flood lighting of the fenced area. | Vendor to confirm
21.15 | Required crane facility with lifting tackles. | Vender to inform
21.16 | Statutory fees payable to Explosives authorities towards drawing approval and final licencing fees on behaf of BHEL. | Vendor to confirm
21.17 | Obtaining NOC from the local Govt. / administration on behaf of BHEL | Vendor to confirm
21.18 | Inspection by competent person and issuance of safety certificate | Vendor to confirm
21.19 | Commissioning service and handing over | Vendor to confirm
21.2 | Training of personnel on operation and maintenance | Vendor to confirm
21.21 | Design and Construction of over head tank of 320 CuM required for fire fighting system as requred by CCOE. | Vendor to inform details
21.22 | Vendors are requested to visit the site before quoting for supply, installation & commissioning of the LPG gas installation. | Vendor
22.0 | BHEL Scope:
22.1 | Supply Input power to power distribution board ( non flameproof) | Vendor to note
22.2 | Free electricity and water for erection purpose. | Vendor to note
22.3 | Required quantity of Water supply for testing | Vendor to note
23.0 | Qualifying conditions:
23.1 | The Vendor should be approved as ALDS Installer by the Department of Explosives, Government of India or an experience & established Installer of Bulk LPG Systems lincenced by CCOE. | Vendor to confirm and furnish details.
23.2 | The bidder/vendor shall have a minimum of FIVE Years of continuous experience in the field of Design, supply, erection, testing and commissioning of the complete LPG gas installation of capacity of 2X 20 Tons or 40 Tons above LPG Installation (on the date of opening of tender) and such installation is presently working satisfactorily for more than one year after commissioning (on the date of opening tender), should quote | Vendor to confirm
23.3 | Performance certificate from the customers regarding satisfactory performance of installation supplied to them in attached format to be enclosed along with technical offer. | Vendor to confirm
23.4 | BHEL reserves the right to verify the information provided by Bidder/vendor. Incase the information provided by Bidder/Vendor is found to be false / incorrect the offer shall be rejected. | Vendor to confirm
23.5 | The Bidder/Vendor to furnish reference list of customer, with full address, details of contract person, where similar system or Higher rating has been supplied in the past. | Vendor to confirm
23.6 | The LPG installation shall be of Above Ground Storage type. | Vendor to confirm
23.7 | The vendors are requested to quote their offer for Design, supply, erection, testing & commissioning of the complete LPG gas installation duly certified by CCOE, Nagpur on turn key basis. | Vendor to confirm
24 | The make of the items wherever not specified shall correspond as follows: - a) LPG Storage Tank (Above Ground) : IS-2825 with 2 MH, each 500 mm b) Cathodic Protection System for A/G : Raychem/ CCOE approved / UG Storage Tanks Manufacturer c) Safety Fittings : CCOE approved manufacturer d) Decanting Pump LPG : Blackmer, USA/ Corken, USA e) Compressor Bulk Plant LPG : Blackmer, USA/ Corken, USA f) Vaporizer LPG : CCOE approved Makes only g) Pipe/Pipe Fitting : Tata/ Jindal / MSL/P.K.Forging/ Priya Engg./Equivalaent h) Valves : Flowchem/Audco/BDK/Equivalaent i) Rochester Gauges : Rochester, Belgium/USA j) High Level Switch : Bliss Anand/ Pune Techtral/Equivalaent k) High Pr. Switch : Switzer l) ROV : Flow Chem/ BDK/ Audco/Equivalaent m) Pressure Regulators 1st Stage suitable for : Elster Jeavons/ Fisher/Elster GmbH/ Min. 21 KCSG Pr. Comap/ Nirmal n) Decanting Hoses : Senior Flexonics/ Equivalent o) Liquid & Gas Flow Indicators : OGPE Design/ Process Equipment make Chemical Ind. Engrs./Equivalaent p) DCP Extinguisher /Bucket : Minimax/Equivalent q) MCC : Vidut Control/ Pryaas/Milstone /Equivalaent r) Power & Control Cables : Skytone/Gem/Grandlay/Gouster./Lap cable s) Demister/ Filtaire : Established design/ Proprietary t) Pressure / Temp. Gauges : Waree/ H.Guru/Equivalaent u) Electric Motors : Siemens/Bharat Bijee/Crompton |  | Vendor to specify
| Note. Before quoting for above, vendor can visit our unit to understand the requirement of the facility and quote accordingly. Vendor's responsibility is to give total Detailed Project Report (DPR) witch is required for replacement of Producer Gas system with LPG system. | Vendor to specify